## Pointmap
|  |  | Modbus Register | [5 empty] | Bacnet Object
|  |  | Integer |  |  |  | Float
| Description | # | Start (MSW) | End (LSW) | Scale | Type | MSW | LSW | Object Type | Instance # | R/W | NV | Units | Range | Notes
Meter Information
| Serial Number |  | 1 | 2 |  | UINT32 |  |  |  |  | R | NV
| Bootloader Version |  | 3 |  |  | UINT16 |  |  |  |  | R | NV
| Firmware Version |  | 4 |  |  | UINT16 |  |  |  |  | R | NV
| Device ID |  | 5 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 15172, 22000 | 15172 = Schneider Pointmap, 22000 = Incusense Pointmap (This Document)
| Power Up Counter |  | 6 |  |  | UINT16 |  |  |  |  | R | NV
| Uptime |  | 7 | 8 |  | UINT32 |  |  |  |  | R | NV | Seconds
| Device Health |  | 9 | [7 empty] | R | NV
| Smart Port ID #1 |  | 10 |  |  | UINT16 |  |  |  |  | R | NV |  |  | 0 = Nothing Connected, 1 = MCM CT Card, 2 = 21 CT Strip + 3 Aux (V1), 3 = 18 CT Strip + 3 Aux (V1), 4 = Floating CT Strip, 5 = 23 CT Strip + 1 Aux, 6 = 24 CT Strip, 7 = Schneider Adapter Board, 8 = 21 CT Strip + 3 Aux (V2), 9 = 18 CT Strip + 3 Aux (V2), 10 = Digital Input Card
| Smart Port ID #2 |  | 11 |  |  | UINT16 |  |  |  |  | R | NV
| Smart Port ID #3 |  | 12 |  |  | UINT16 |  |  |  |  | R | NV
| Smart Port ID #4 |  | 13 |  |  | UINT16 |  |  |  |  | R | NV
| Smart Port #1 Serial Number |  | 14 | 15 |  | UINT32 |  |  |  |  | R | NV
| Smart Port #2 Serial Number |  | 16 | 17 |  | UINT32 |  |  |  |  | R | NV
| Smart Port #3 Serial Number |  | 18 | 19 |  | UINT32 |  |  |  |  | R | NV
| Smart Port #4 Serial Number |  | 20 | 21 |  | UINT32 |  |  |  |  | R | NV
| Smart Port #1 Firmware Version |  | 22 | [7 empty] | R | NV
| Smart Port #2 Firmware Version |  | 23 | [7 empty] | R | NV
| Smart Port #3 Firmware Version |  | 24 | [7 empty] | R | NV
| Smart Port #4 Firmware Version |  | 25 | [7 empty] | R | NV
| MAC Address (Bit 33-48) |  | 26 | [7 empty] | R | NV
| MAC Address (Bit 17-32) |  | 27 | [7 empty] | R | NV
| MAC Address (Bit 1-16) |  | 28 | [7 empty] | R | NV
| Brand Name (16 Registers) |  | 29 | 44 | [6 empty] | R | NV |  |  | Brand Name, Model Name and Device Name supports up to 32 characters (16 registers)
| Model Name (16 Register) |  | 45 | 60 | [6 empty] | R | NV
| Device Name (16 Registers) |  | 61 | 76 | [6 empty] | R/W | NV
Meter Configuration
| Demand # of Sub-Intervals |  | 100 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 1 - 6
| Demand Sub-Interval Length |  | 101 |  |  | UINT16 |  |  |  |  | R/W | NV | Seconds | 0, 10 - 32767 | 0 = Sync to Comms
| Demand Time Stamp (Year) |  | 102 | [7 empty] | R |  | Year |  | Years since 1900 (118 = 2018)
| Demand Time Stamp (Month) |  | 103 | [7 empty] | R |  | Month | 0 - 11 | Month (0 = January)
| Demand Time Stamp (Day) |  | 104 | [7 empty] | R |  | Day | 1 - 31 | Day of the Month
| Demand Time Stamp (Weekday) |  | 105 | [7 empty] | R |  | Weekday | 0 - 6 | Weekday (1 = Monday)
| Demand Time Stamp (Hour) |  | 106 | [7 empty] | R |  | Hour | 0 - 23 | Hour (13 = 1PM)
| Demand Time Stamp (Minute) |  | 107 | [7 empty] | R |  | Minute | 0 - 59 | Minute
| Demand Time Stamp (Second) |  | 108 | [7 empty] | R |  | Seconds | 0 - 59 | Second
| Real Time Clock (Year) |  | 109 |  |  | UINT16 |  |  |  |  | R/W |  | Year |  | Years since 1900 (118 = 2018)
| Real Time Clock (Month) |  | 110 |  |  | UINT16 |  |  |  |  | R/W |  | Month | 0 - 11 | Month (0 = January)
| Real Time Clock (Day) |  | 111 |  |  | UINT16 |  |  |  |  | R/W |  | Day | 1 - 31 | Day of the Month
| Real Time Clock (Weekday) |  | 112 |  |  | UINT16 |  |  |  |  | R/W |  | Weekday | 0 - 6 | Weekday (1 = Monday)
| Real Time Clock (Hour) |  | 113 |  |  | UINT16 |  |  |  |  | R/W |  | Hour | 0 - 23 | Hour (13 = 1PM)
| Real Time Clock (Min) |  | 114 |  |  | UINT16 |  |  |  |  | R/W |  | Minute | 0 - 59 | Minute
| Real Time Clock (Second) |  | 115 |  |  | UINT16 |  |  |  |  | R/W |  | Seconds | 0 - 59 | Second
| Digital Output #1 |  | 116 | [7 empty] | R/W |  |  | 0, 1
| Digital Output #2 |  | 117 | [7 empty] | R/W |  |  | 0, 1
| Digital Input #1 State |  | 118 | [7 empty] | R |  |  | 0, 1
| Digital Input #2 State |  | 119 | [7 empty] | R |  |  | 0, 1
| Digital Input #1 Counter |  | 120 | 121 |  | UINT32 |  |  |  |  | R/W | NV
| Digital Input #1 Counter |  | 122 | 123 |  | UINT32 |  |  |  |  | R/W | NV
| Modbus Slave Address |  | 124 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 1 - 254
| Modbus TCP Port |  | 125 |  |  | UINT16 |  |  |  |  | R | NV |  | 502
| IP Address |  | 126 | 127 | [6 empty] | R/W | NV |  |  | Meter must be rebooted for new network settings to affect. Device can be rebooted remotely using Global Reset/Command (Register 192)
| Gateway |  | 128 | 129 | [6 empty] | R/W | NV
| Mask |  | 130 | 131 | [6 empty] | R/W | NV
| NTP |  | 132 | 133 | [6 empty] | R/W | NV |  |  | Write to NTP register over Modbus will clear the NTP string in webserver
| DNS |  | 134 | 135 | [6 empty] | R/W | NV
| DNS 2 |  | 136 | 137 | [6 empty] | R | NV
| SMTP |  | 138 | 139 | [6 empty] | R | NV
| Baudrate |  | 140 | 141 |  | UINT32 |  |  |  |  | R/W | NV | Baud | 0 - 4 | 0 = 9600, 1 = 19200, 2 = 38400, 3 = 57600, 4 = 76800 (Value can be written to MSW or LSW)
| Parity |  | 142 | [7 empty] | R | NV
| Stop Bits |  | 143 | [7 empty] | R | NV
| Dip Switch Enabled |  | 144 | [7 empty] | R/W | NV |  | 0, 1 | Bit0 - Enables Dipswitch for setting Modbus slave address
| Dips Switch Value |  | 145 |  |  | UINT16 |  |  |  |  | R |  |  |  | When Dip Switch is enabled, this value is used for Modbus Slave Address
| RS485 Gateway Passthrough Enabled |  | 146 | [7 empty] | R | NV
| Panel 1 (Smart Port 1&2) Configuration |  | 147 | [7 empty] | R/W | NV |  | 0 - 4 | 0 = Top Feed, 1 = Bottom Feed, 2 = Single Row Sequential, 3 = Single Row Odd/Even, 4 = Sequential
| Panel 2 (Smart Port 3&4) Configuration |  | 148 | [7 empty] | R/W | NV |  | 0 - 4
| CT Compensation Enabled |  | 149 | [7 empty] | R/W | NV |  | 0 - 3 | Bit0 - Enable CT Compensation for 1/3V CTs Bit1 - Legacy CT Compensation (Only used for Schneider Addapter Board)
Circuit Configuration
Global
| Global CT Size |  | 190 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 32000 | Writing this register will set all branches to same CT size
| Global Breaker Size |  | 191 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 32000 | Writing this register will set all branches to same breaker size
| Global Reset/Command |  | 192 | [7 empty] | R/W | NV |  | See Notes | 12345 = Reboot Device, 20097 = Reset Max Demand, 24658 = Clear True Meter Assignment 24659 = Reset True Meter to Default, 26012 = New Demand SubInterval 26013 = Reset Demand, 29877 = Reset Max kW and Current, 31010 = Clear All Latching Alarms, 32123 = Start Waveform Capture (All Circuits)
| Global CT Type/Compensation |  | 193 | [7 empty] | R/W | NV |  |  | Writing to this register will set all branches to the correseponding CT type
| CT Size |  | 200 | 295 |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 1 | 1 | 200 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 2 | 2 | 201 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 3 | 3 | 202 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 4 | 4 | 203 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 5 | 5 | 204 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 6 | 6 | 205 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 7 | 7 | 206 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 8 | 8 | 207 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 9 | 9 | 208 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 10 | 10 | 209 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 11 | 11 | 210 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 12 | 12 | 211 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 13 | 13 | 212 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 14 | 14 | 213 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 15 | 15 | 214 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 16 | 16 | 215 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 17 | 17 | 216 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 18 | 18 | 217 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 19 | 19 | 218 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 20 | 20 | 219 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 21 | 21 | 220 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 22 | 22 | 221 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 23 | 23 | 222 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 24 | 24 | 223 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 25 | 25 | 224 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 26 | 26 | 225 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 27 | 27 | 226 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 28 | 28 | 227 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 29 | 29 | 228 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 30 | 30 | 229 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 31 | 31 | 230 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 32 | 32 | 231 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 33 | 33 | 232 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 34 | 34 | 233 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 35 | 35 | 234 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 36 | 36 | 235 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 37 | 37 | 236 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 38 | 38 | 237 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 39 | 39 | 238 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 40 | 40 | 239 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 41 | 41 | 240 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 42 | 42 | 241 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 43 | 43 | 242 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 44 | 44 | 243 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 45 | 45 | 244 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 46 | 46 | 245 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 47 | 47 | 246 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 48 | 48 | 247 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 49 | 49 | 248 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 50 | 50 | 249 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 51 | 51 | 250 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 52 | 52 | 251 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 53 | 53 | 252 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 54 | 54 | 253 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 55 | 55 | 254 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 56 | 56 | 255 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 57 | 57 | 256 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 58 | 58 | 257 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 59 | 59 | 258 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 60 | 60 | 259 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 61 | 61 | 260 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 62 | 62 | 261 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 63 | 63 | 262 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 64 | 64 | 263 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 65 | 65 | 264 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 66 | 66 | 265 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 67 | 67 | 266 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 68 | 68 | 267 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 69 | 69 | 268 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 70 | 70 | 269 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 71 | 71 | 270 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 72 | 72 | 271 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 73 | 73 | 272 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 74 | 74 | 273 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 75 | 75 | 274 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 76 | 76 | 275 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 77 | 77 | 276 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 78 | 78 | 277 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 79 | 79 | 278 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 80 | 80 | 279 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 81 | 81 | 280 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 82 | 82 | 281 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 83 | 83 | 282 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 84 | 84 | 283 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 85 | 85 | 284 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 86 | 86 | 285 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 87 | 87 | 286 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 88 | 88 | 287 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 89 | 89 | 288 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 90 | 90 | 289 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 91 | 91 | 290 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 92 | 92 | 291 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 93 | 93 | 292 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 94 | 94 | 293 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 95 | 95 | 294 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 96 | 96 | 295 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size |  | 296 | 391 |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 1 | 1 | 296 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 2 | 2 | 297 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 3 | 3 | 298 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 4 | 4 | 299 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 5 | 5 | 300 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 6 | 6 | 301 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 7 | 7 | 302 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 8 | 8 | 303 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 9 | 9 | 304 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 10 | 10 | 305 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 11 | 11 | 306 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 12 | 12 | 307 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 13 | 13 | 308 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 14 | 14 | 309 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 15 | 15 | 310 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 16 | 16 | 311 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 17 | 17 | 312 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 18 | 18 | 313 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 19 | 19 | 314 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 20 | 20 | 315 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 21 | 21 | 316 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 22 | 22 | 317 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 23 | 23 | 318 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 24 | 24 | 319 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 25 | 25 | 320 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 26 | 26 | 321 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 27 | 27 | 322 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 28 | 28 | 323 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 29 | 29 | 324 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 30 | 30 | 325 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 31 | 31 | 326 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 32 | 32 | 327 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 33 | 33 | 328 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 34 | 34 | 329 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 35 | 35 | 330 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 36 | 36 | 331 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 37 | 37 | 332 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 38 | 38 | 333 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 39 | 39 | 334 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 40 | 40 | 335 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 41 | 41 | 336 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 42 | 42 | 337 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 43 | 43 | 338 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 44 | 44 | 339 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 45 | 45 | 340 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 46 | 46 | 341 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 47 | 47 | 342 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 48 | 48 | 343 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 49 | 49 | 344 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 50 | 50 | 345 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 51 | 51 | 346 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 52 | 52 | 347 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 53 | 53 | 348 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 54 | 54 | 349 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 55 | 55 | 350 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 56 | 56 | 351 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 57 | 57 | 352 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 58 | 58 | 353 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 59 | 59 | 354 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 60 | 60 | 355 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 61 | 61 | 356 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 62 | 62 | 357 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 63 | 63 | 358 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 64 | 64 | 359 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 65 | 65 | 360 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 66 | 66 | 361 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 67 | 67 | 362 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 68 | 68 | 363 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 69 | 69 | 364 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 70 | 70 | 365 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 71 | 71 | 366 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 72 | 72 | 367 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 73 | 73 | 368 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 74 | 74 | 369 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 75 | 75 | 370 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 76 | 76 | 371 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 77 | 77 | 372 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 78 | 78 | 373 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 79 | 79 | 374 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 80 | 80 | 375 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 81 | 81 | 376 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 82 | 82 | 377 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 83 | 83 | 378 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 84 | 84 | 379 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 85 | 85 | 380 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 86 | 86 | 381 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 87 | 87 | 382 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 88 | 88 | 383 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 89 | 89 | 384 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 90 | 90 | 385 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 91 | 91 | 386 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 92 | 92 | 387 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 93 | 93 | 388 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 94 | 94 | 389 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 95 | 95 | 390 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 96 | 96 | 391 |  |  | UINT16 |  |  |  |  | R/W | NV | Amps | 0 - 32000
| Voltage Phase |  | 392 | 487 |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 1 | 1 | 392 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 2 | 2 | 393 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 3 | 3 | 394 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 4 | 4 | 395 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 5 | 5 | 396 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 6 | 6 | 397 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 7 | 7 | 398 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 8 | 8 | 399 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 9 | 9 | 400 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 10 | 10 | 401 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 11 | 11 | 402 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 12 | 12 | 403 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 13 | 13 | 404 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 14 | 14 | 405 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 15 | 15 | 406 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 16 | 16 | 407 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 17 | 17 | 408 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 18 | 18 | 409 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 19 | 19 | 410 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 20 | 20 | 411 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 21 | 21 | 412 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 22 | 22 | 413 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 23 | 23 | 414 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 24 | 24 | 415 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 25 | 25 | 416 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 26 | 26 | 417 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 27 | 27 | 418 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 28 | 28 | 419 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 29 | 29 | 420 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 30 | 30 | 421 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 31 | 31 | 422 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 32 | 32 | 423 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 33 | 33 | 424 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 34 | 34 | 425 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 35 | 35 | 426 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 36 | 36 | 427 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 37 | 37 | 428 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 38 | 38 | 429 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 39 | 39 | 430 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 40 | 40 | 431 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 41 | 41 | 432 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 42 | 42 | 433 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 43 | 43 | 434 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 44 | 44 | 435 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 45 | 45 | 436 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 46 | 46 | 437 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 47 | 47 | 438 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 48 | 48 | 439 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 49 | 49 | 440 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 50 | 50 | 441 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 51 | 51 | 442 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 52 | 52 | 443 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 53 | 53 | 444 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 54 | 54 | 445 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 55 | 55 | 446 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 56 | 56 | 447 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 57 | 57 | 448 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 58 | 58 | 449 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 59 | 59 | 450 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 60 | 60 | 451 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 61 | 61 | 452 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 62 | 62 | 453 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 63 | 63 | 454 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 64 | 64 | 455 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 65 | 65 | 456 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 66 | 66 | 457 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 67 | 67 | 458 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 68 | 68 | 459 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 69 | 69 | 460 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 70 | 70 | 461 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 71 | 71 | 462 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 72 | 72 | 463 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 73 | 73 | 464 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 74 | 74 | 465 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 75 | 75 | 466 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 76 | 76 | 467 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 77 | 77 | 468 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 78 | 78 | 469 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 79 | 79 | 470 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 80 | 80 | 471 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 81 | 81 | 472 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 82 | 82 | 473 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 83 | 83 | 474 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 84 | 84 | 475 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 85 | 85 | 476 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 86 | 86 | 477 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 87 | 87 | 478 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 88 | 88 | 479 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 89 | 89 | 480 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 90 | 90 | 481 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 91 | 91 | 482 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 92 | 92 | 483 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 93 | 93 | 484 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 94 | 94 | 485 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 95 | 95 | 486 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 96 | 96 | 487 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| True Circuit Assignment |  | 488 | 583 |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96 | True Meter Assignment (Starting at register 15000), 0 = Disabled
| True Circuit Assingment - Circuit 1 | 1 | 488 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 2 | 2 | 489 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 3 | 3 | 490 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 4 | 4 | 491 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 5 | 5 | 492 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 6 | 6 | 493 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 7 | 7 | 494 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 8 | 8 | 495 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 9 | 9 | 496 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 10 | 10 | 497 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 11 | 11 | 498 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 12 | 12 | 499 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 13 | 13 | 500 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 14 | 14 | 501 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 15 | 15 | 502 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 16 | 16 | 503 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 17 | 17 | 504 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 18 | 18 | 505 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 19 | 19 | 506 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 20 | 20 | 507 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 21 | 21 | 508 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 22 | 22 | 509 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 23 | 23 | 510 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 24 | 24 | 511 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 25 | 25 | 512 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 26 | 26 | 513 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 27 | 27 | 514 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 28 | 28 | 515 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 29 | 29 | 516 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 30 | 30 | 517 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 31 | 31 | 518 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 32 | 32 | 519 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 33 | 33 | 520 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 34 | 34 | 521 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 35 | 35 | 522 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 36 | 36 | 523 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 37 | 37 | 524 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 38 | 38 | 525 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 39 | 39 | 526 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 40 | 40 | 527 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 41 | 41 | 528 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 42 | 42 | 529 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 43 | 43 | 530 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 44 | 44 | 531 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 45 | 45 | 532 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 46 | 46 | 533 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 47 | 47 | 534 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 48 | 48 | 535 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 49 | 49 | 536 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 50 | 50 | 537 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 51 | 51 | 538 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 52 | 52 | 539 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 53 | 53 | 540 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 54 | 54 | 541 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 55 | 55 | 542 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 56 | 56 | 543 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 57 | 57 | 544 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 58 | 58 | 545 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 59 | 59 | 546 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 60 | 60 | 547 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 61 | 61 | 548 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 62 | 62 | 549 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 63 | 63 | 550 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 64 | 64 | 551 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 65 | 65 | 552 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 66 | 66 | 553 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 67 | 67 | 554 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 68 | 68 | 555 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 69 | 69 | 556 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 70 | 70 | 557 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 71 | 71 | 558 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 72 | 72 | 559 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 73 | 73 | 560 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 74 | 74 | 561 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 75 | 75 | 562 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 76 | 76 | 563 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 77 | 77 | 564 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 78 | 78 | 565 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 79 | 79 | 566 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 80 | 80 | 567 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 81 | 81 | 568 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 82 | 82 | 569 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 83 | 83 | 570 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 84 | 84 | 571 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 85 | 85 | 572 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 86 | 86 | 573 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 87 | 87 | 574 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 88 | 88 | 575 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 89 | 89 | 576 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 90 | 90 | 577 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 91 | 91 | 578 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 92 | 92 | 579 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 93 | 93 | 580 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 94 | 94 | 581 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 95 | 95 | 582 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| True Circuit Assingment - Circuit 96 | 96 | 583 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 0 - 96
| Reset/Command |  | 584 | 679 | [10 empty] | 29877 = Reset Max kW and Current, 32123 = Waveform Capture (Only Selected Circuit)
| Reset/Command - Circuit 1 | 1 | 584 | [7 empty] | R/W | NV
| Reset/Command - Circuit 2 | 2 | 585 | [7 empty] | R/W | NV
| Reset/Command - Circuit 3 | 3 | 586 | [7 empty] | R/W | NV
| Reset/Command - Circuit 4 | 4 | 587 | [7 empty] | R/W | NV
| Reset/Command - Circuit 5 | 5 | 588 | [7 empty] | R/W | NV
| Reset/Command - Circuit 6 | 6 | 589 | [7 empty] | R/W | NV
| Reset/Command - Circuit 7 | 7 | 590 | [7 empty] | R/W | NV
| Reset/Command - Circuit 8 | 8 | 591 | [7 empty] | R/W | NV
| Reset/Command - Circuit 9 | 9 | 592 | [7 empty] | R/W | NV
| Reset/Command - Circuit 10 | 10 | 593 | [7 empty] | R/W | NV
| Reset/Command - Circuit 11 | 11 | 594 | [7 empty] | R/W | NV
| Reset/Command - Circuit 12 | 12 | 595 | [7 empty] | R/W | NV
| Reset/Command - Circuit 13 | 13 | 596 | [7 empty] | R/W | NV
| Reset/Command - Circuit 14 | 14 | 597 | [7 empty] | R/W | NV
| Reset/Command - Circuit 15 | 15 | 598 | [7 empty] | R/W | NV
| Reset/Command - Circuit 16 | 16 | 599 | [7 empty] | R/W | NV
| Reset/Command - Circuit 17 | 17 | 600 | [7 empty] | R/W | NV
| Reset/Command - Circuit 18 | 18 | 601 | [7 empty] | R/W | NV
| Reset/Command - Circuit 19 | 19 | 602 | [7 empty] | R/W | NV
| Reset/Command - Circuit 20 | 20 | 603 | [7 empty] | R/W | NV
| Reset/Command - Circuit 21 | 21 | 604 | [7 empty] | R/W | NV
| Reset/Command - Circuit 22 | 22 | 605 | [7 empty] | R/W | NV
| Reset/Command - Circuit 23 | 23 | 606 | [7 empty] | R/W | NV
| Reset/Command - Circuit 24 | 24 | 607 | [7 empty] | R/W | NV
| Reset/Command - Circuit 25 | 25 | 608 | [7 empty] | R/W | NV
| Reset/Command - Circuit 26 | 26 | 609 | [7 empty] | R/W | NV
| Reset/Command - Circuit 27 | 27 | 610 | [7 empty] | R/W | NV
| Reset/Command - Circuit 28 | 28 | 611 | [7 empty] | R/W | NV
| Reset/Command - Circuit 29 | 29 | 612 | [7 empty] | R/W | NV
| Reset/Command - Circuit 30 | 30 | 613 | [7 empty] | R/W | NV
| Reset/Command - Circuit 31 | 31 | 614 | [7 empty] | R/W | NV
| Reset/Command - Circuit 32 | 32 | 615 | [7 empty] | R/W | NV
| Reset/Command - Circuit 33 | 33 | 616 | [7 empty] | R/W | NV
| Reset/Command - Circuit 34 | 34 | 617 | [7 empty] | R/W | NV
| Reset/Command - Circuit 35 | 35 | 618 | [7 empty] | R/W | NV
| Reset/Command - Circuit 36 | 36 | 619 | [7 empty] | R/W | NV
| Reset/Command - Circuit 37 | 37 | 620 | [7 empty] | R/W | NV
| Reset/Command - Circuit 38 | 38 | 621 | [7 empty] | R/W | NV
| Reset/Command - Circuit 39 | 39 | 622 | [7 empty] | R/W | NV
| Reset/Command - Circuit 40 | 40 | 623 | [7 empty] | R/W | NV
| Reset/Command - Circuit 41 | 41 | 624 | [7 empty] | R/W | NV
| Reset/Command - Circuit 42 | 42 | 625 | [7 empty] | R/W | NV
| Reset/Command - Circuit 43 | 43 | 626 | [7 empty] | R/W | NV
| Reset/Command - Circuit 44 | 44 | 627 | [7 empty] | R/W | NV
| Reset/Command - Circuit 45 | 45 | 628 | [7 empty] | R/W | NV
| Reset/Command - Circuit 46 | 46 | 629 | [7 empty] | R/W | NV
| Reset/Command - Circuit 47 | 47 | 630 | [7 empty] | R/W | NV
| Reset/Command - Circuit 48 | 48 | 631 | [7 empty] | R/W | NV
| Reset/Command - Circuit 49 | 49 | 632 | [7 empty] | R/W | NV
| Reset/Command - Circuit 50 | 50 | 633 | [7 empty] | R/W | NV
| Reset/Command - Circuit 51 | 51 | 634 | [7 empty] | R/W | NV
| Reset/Command - Circuit 52 | 52 | 635 | [7 empty] | R/W | NV
| Reset/Command - Circuit 53 | 53 | 636 | [7 empty] | R/W | NV
| Reset/Command - Circuit 54 | 54 | 637 | [7 empty] | R/W | NV
| Reset/Command - Circuit 55 | 55 | 638 | [7 empty] | R/W | NV
| Reset/Command - Circuit 56 | 56 | 639 | [7 empty] | R/W | NV
| Reset/Command - Circuit 57 | 57 | 640 | [7 empty] | R/W | NV
| Reset/Command - Circuit 58 | 58 | 641 | [7 empty] | R/W | NV
| Reset/Command - Circuit 59 | 59 | 642 | [7 empty] | R/W | NV
| Reset/Command - Circuit 60 | 60 | 643 | [7 empty] | R/W | NV
| Reset/Command - Circuit 61 | 61 | 644 | [7 empty] | R/W | NV
| Reset/Command - Circuit 62 | 62 | 645 | [7 empty] | R/W | NV
| Reset/Command - Circuit 63 | 63 | 646 | [7 empty] | R/W | NV
| Reset/Command - Circuit 64 | 64 | 647 | [7 empty] | R/W | NV
| Reset/Command - Circuit 65 | 65 | 648 | [7 empty] | R/W | NV
| Reset/Command - Circuit 66 | 66 | 649 | [7 empty] | R/W | NV
| Reset/Command - Circuit 67 | 67 | 650 | [7 empty] | R/W | NV
| Reset/Command - Circuit 68 | 68 | 651 | [7 empty] | R/W | NV
| Reset/Command - Circuit 69 | 69 | 652 | [7 empty] | R/W | NV
| Reset/Command - Circuit 70 | 70 | 653 | [7 empty] | R/W | NV
| Reset/Command - Circuit 71 | 71 | 654 | [7 empty] | R/W | NV
| Reset/Command - Circuit 72 | 72 | 655 | [7 empty] | R/W | NV
| Reset/Command - Circuit 73 | 73 | 656 | [7 empty] | R/W | NV
| Reset/Command - Circuit 74 | 74 | 657 | [7 empty] | R/W | NV
| Reset/Command - Circuit 75 | 75 | 658 | [7 empty] | R/W | NV
| Reset/Command - Circuit 76 | 76 | 659 | [7 empty] | R/W | NV
| Reset/Command - Circuit 77 | 77 | 660 | [7 empty] | R/W | NV
| Reset/Command - Circuit 78 | 78 | 661 | [7 empty] | R/W | NV
| Reset/Command - Circuit 79 | 79 | 662 | [7 empty] | R/W | NV
| Reset/Command - Circuit 80 | 80 | 663 | [7 empty] | R/W | NV
| Reset/Command - Circuit 81 | 81 | 664 | [7 empty] | R/W | NV
| Reset/Command - Circuit 82 | 82 | 665 | [7 empty] | R/W | NV
| Reset/Command - Circuit 83 | 83 | 666 | [7 empty] | R/W | NV
| Reset/Command - Circuit 84 | 84 | 667 | [7 empty] | R/W | NV
| Reset/Command - Circuit 85 | 85 | 668 | [7 empty] | R/W | NV
| Reset/Command - Circuit 86 | 86 | 669 | [7 empty] | R/W | NV
| Reset/Command - Circuit 87 | 87 | 670 | [7 empty] | R/W | NV
| Reset/Command - Circuit 88 | 88 | 671 | [7 empty] | R/W | NV
| Reset/Command - Circuit 89 | 89 | 672 | [7 empty] | R/W | NV
| Reset/Command - Circuit 90 | 90 | 673 | [7 empty] | R/W | NV
| Reset/Command - Circuit 91 | 91 | 674 | [7 empty] | R/W | NV
| Reset/Command - Circuit 92 | 92 | 675 | [7 empty] | R/W | NV
| Reset/Command - Circuit 93 | 93 | 676 | [7 empty] | R/W | NV
| Reset/Command - Circuit 94 | 94 | 677 | [7 empty] | R/W | NV
| Reset/Command - Circuit 95 | 95 | 678 | [7 empty] | R/W | NV
| Reset/Command - Circuit 96 | 96 | 679 | [7 empty] | R/W | NV
| CT Type/Compensation |  | 680 | 775
| CT Type/Compensation - Circuit 1 | 1 | 680 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 2 | 2 | 681 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 3 | 3 | 682 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 4 | 4 | 683 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 5 | 5 | 684 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 6 | 6 | 685 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 7 | 7 | 686 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 8 | 8 | 687 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 9 | 9 | 688 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 10 | 10 | 689 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 11 | 11 | 690 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 12 | 12 | 691 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 13 | 13 | 692 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 14 | 14 | 693 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 15 | 15 | 694 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 16 | 16 | 695 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 17 | 17 | 696 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 18 | 18 | 697 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 19 | 19 | 698 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 20 | 20 | 699 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 21 | 21 | 700 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 22 | 22 | 701 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 23 | 23 | 702 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 24 | 24 | 703 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 25 | 25 | 704 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 26 | 26 | 705 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 27 | 27 | 706 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 28 | 28 | 707 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 29 | 29 | 708 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 30 | 30 | 709 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 31 | 31 | 710 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 32 | 32 | 711 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 33 | 33 | 712 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 34 | 34 | 713 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 35 | 35 | 714 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 36 | 36 | 715 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 37 | 37 | 716 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 38 | 38 | 717 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 39 | 39 | 718 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 40 | 40 | 719 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 41 | 41 | 720 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 42 | 42 | 721 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 43 | 43 | 722 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 44 | 44 | 723 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 45 | 45 | 724 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 46 | 46 | 725 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 47 | 47 | 726 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 48 | 48 | 727 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 49 | 49 | 728 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 50 | 50 | 729 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 51 | 51 | 730 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 52 | 52 | 731 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 53 | 53 | 732 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 54 | 54 | 733 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 55 | 55 | 734 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 56 | 56 | 735 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 57 | 57 | 736 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 58 | 58 | 737 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 59 | 59 | 738 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 60 | 60 | 739 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 61 | 61 | 740 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 62 | 62 | 741 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 63 | 63 | 742 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 64 | 64 | 743 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 65 | 65 | 744 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 66 | 66 | 745 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 67 | 67 | 746 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 68 | 68 | 747 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 69 | 69 | 748 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 70 | 70 | 749 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 71 | 71 | 750 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 72 | 72 | 751 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 73 | 73 | 752 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 74 | 74 | 753 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 75 | 75 | 754 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 76 | 76 | 755 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 77 | 77 | 756 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 78 | 78 | 757 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 79 | 79 | 758 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 80 | 80 | 759 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 81 | 81 | 760 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 82 | 82 | 761 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 83 | 83 | 762 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 84 | 84 | 763 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 85 | 85 | 764 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 86 | 86 | 765 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 87 | 87 | 766 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 88 | 88 | 767 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 89 | 89 | 768 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 90 | 90 | 769 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 91 | 91 | 770 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 92 | 92 | 771 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 93 | 93 | 772 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 94 | 94 | 773 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 95 | 95 | 774 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 96 | 96 | 775 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment |  | 776 | 871
| Smart Port to Circuit Assignment - SP1, CH1 | SP1, CH1 | 776 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH2 | SP1, CH2 | 777 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH3 | SP1, CH3 | 778 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH4 | SP1, CH4 | 779 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH5 | SP1, CH5 | 780 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH6 | SP1, CH6 | 781 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH7 | SP1, CH7 | 782 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH8 | SP1, CH8 | 783 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH9 | SP1, CH9 | 784 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH10 | SP1, CH10 | 785 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH11 | SP1, CH11 | 786 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH12 | SP1, CH12 | 787 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH13 | SP1, CH13 | 788 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH14 | SP1, CH14 | 789 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH15 | SP1, CH15 | 790 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH16 | SP1, CH16 | 791 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH17 | SP1, CH17 | 792 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH18 | SP1, CH18 | 793 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH19 | SP1, CH19 | 794 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH20 | SP1, CH20 | 795 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH21 | SP1, CH21 | 796 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH22 | SP1, CH22 | 797 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH23 | SP1, CH23 | 798 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH24 | SP1, CH24 | 799 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH1 | SP2, CH1 | 800 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH2 | SP2, CH2 | 801 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH3 | SP2, CH3 | 802 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH4 | SP2, CH4 | 803 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH5 | SP2, CH5 | 804 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH6 | SP2, CH6 | 805 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH7 | SP2, CH7 | 806 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH8 | SP2, CH8 | 807 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH9 | SP2, CH9 | 808 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH10 | SP2, CH10 | 809 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH11 | SP2, CH11 | 810 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH12 | SP2, CH12 | 811 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH13 | SP2, CH13 | 812 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH14 | SP2, CH14 | 813 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH15 | SP2, CH15 | 814 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH16 | SP2, CH16 | 815 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH17 | SP2, CH17 | 816 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH18 | SP2, CH18 | 817 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH19 | SP2, CH19 | 818 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH20 | SP2, CH20 | 819 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH21 | SP2, CH21 | 820 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH22 | SP2, CH22 | 821 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH23 | SP2, CH23 | 822 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH24 | SP2, CH24 | 823 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH1 | SP3, CH1 | 824 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH2 | SP3, CH2 | 825 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH3 | SP3, CH3 | 826 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH4 | SP3, CH4 | 827 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH5 | SP3, CH5 | 828 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH6 | SP3, CH6 | 829 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH7 | SP3, CH7 | 830 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH8 | SP3, CH8 | 831 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH9 | SP3, CH9 | 832 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH10 | SP3, CH10 | 833 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH11 | SP3, CH11 | 834 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH12 | SP3, CH12 | 835 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH13 | SP3, CH13 | 836 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH14 | SP3, CH14 | 837 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH15 | SP3, CH15 | 838 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH16 | SP3, CH16 | 839 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH17 | SP3, CH17 | 840 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH18 | SP3, CH18 | 841 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH19 | SP3, CH19 | 842 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH20 | SP3, CH20 | 843 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH21 | SP3, CH21 | 844 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH22 | SP3, CH22 | 845 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH23 | SP3, CH23 | 846 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH24 | SP3, CH24 | 847 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH1 | SP4, CH1 | 848 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH2 | SP4, CH2 | 849 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH3 | SP4, CH3 | 850 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH4 | SP4, CH4 | 851 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH5 | SP4, CH5 | 852 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH6 | SP4, CH6 | 853 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH7 | SP4, CH7 | 854 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH8 | SP4, CH8 | 855 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH9 | SP4, CH9 | 856 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH10 | SP4, CH10 | 857 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH11 | SP4, CH11 | 858 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH12 | SP4, CH12 | 859 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH13 | SP4, CH13 | 860 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH14 | SP4, CH14 | 861 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH15 | SP4, CH15 | 862 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH16 | SP4, CH16 | 863 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH17 | SP4, CH17 | 864 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH18 | SP4, CH18 | 865 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH19 | SP4, CH19 | 866 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH20 | SP4, CH20 | 867 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH21 | SP4, CH21 | 868 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH22 | SP4, CH22 | 869 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH23 | SP4, CH23 | 870 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH24 | SP4, CH24 | 871 | [7 empty] | R/W | NV
Alarm/Event Configuration
Voltage Alarm Configuration |  |  | 1000 | 1006
| Overvoltage Alarm Time Delay |  | 1000 |  |  | UINT16 |  |  |  |  | R/W | NV | Seconds | 0 - 32767
| Undervoltage Alarm Time Delay |  | 1001 |  |  | UINT16 |  |  |  |  | R/W | NV | Seconds | 0 - 32767
| Overvoltage Latching Alarm Threshold |  | 1002 |  |  | UINT16 |  |  |  |  | R/W | NV | Volts | 0 - 32767 | Volts Line to Line
| Undervotage Latching Alarm Threshold |  | 1003 |  |  | UINT16 |  |  |  |  | R/W | NV | Volts | 0 - 32767 | Volts Line to Line
| Overvoltage Non-Latching Alarm Threshold |  | 1004 |  |  | UINT16 |  |  |  |  | R/W | NV | Volts | 0 - 32767
| Undervoltage Non-Latching Alarm Threshold |  | 1005 |  |  | UINT16 |  |  |  |  | R/W | NV | Volts | 0 - 32767
| Voltage Alarm Hysteresis |  | 1006 |  |  | UINT16 |  |  |  |  | R/W | NV | Percent | 0 - 32767
Branch Alarm Configuration |  |  | 1007 | 1021
| High-High Latching Alarm Time Delay |  | 1007 |  |  | UINT16 |  |  |  |  | R/W | NV | Seconds
| High Latching Alarm Time Delay |  | 1008 |  |  | UINT16 |  |  |  |  | R/W | NV | Seconds | 0 - 32767
| Low Latching Alarm Time Delay |  | 1009 |  |  | UINT16 |  |  |  |  | R/W | NV | Seconds | 0 - 32767
| Low-Low Latching Alarm Time Delay |  | 1010 |  |  | UINT16 |  |  |  |  | R/W | NV | Seconds | 0 - 32767
| Latching Alarm On Time |  | 1011 |  |  | UINT16 |  |  |  |  | R/W | NV | Seconds | 0 - 32767
| Latching Alarm Off Time |  | 1012 |  |  | UINT16 |  |  |  |  | R/W | NV | Seconds | 0 - 32767
| High-High Latching Alarm Threshold |  | 1013 |  |  | UINT16 |  |  |  |  | R/W | NV | Percent | 0 - 1000
| High Latching Alarm Thresold |  | 1014 |  | -1 | UINT16 |  |  |  |  | R/W | NV | Percent | 0 - 1000 | Percent of Breaker Size (700 = 70%)
| Low Latching Alarm Threshold |  | 1015 |  | -1 | UINT16 |  |  |  |  | R/W | NV | Percent | 0 - 1000 | Percent of Breaker Size (100 = 10%)
| Low-Low Latchng Alarm Threhold |  | 1016 |  |  | UINT16 |  |  |  |  | R/W | NV | Percent | 0 - 1000
| Non-Latching High High Threshold |  | 1017 |  |  | UINT16 |  |  |  |  | R/W | NV | Percent | 0 - 1000
| Non-Latching High Alarm Threshold |  | 1018 |  |  | UINT16 |  |  |  |  | R/W | NV | Percent | 0 - 1000
| Non-Latching Low Alarm Threshold |  | 1019 |  |  | UINT16 |  |  |  |  | R/W | NV | Percent | 0 - 1000
| Non-Latching Low Low Threshold |  | 1020 |  |  | UINT16 |  |  |  |  | R/W | NV | Percent | 0 - 1000
| Non-Latching Hysteresis |  | 1021 |  |  | UINT16 |  |  |  |  | R/W | NV | Percent | 0 - 1000
Waveform Capture Configuration |  |  | 1100 | 1103
| Voltage Capture High RMS Threshold |  | 1100 |  |  | UINT16 |  |  |  |  | R/W | NV | Volts | 0 - 32767 | Volts LL (All line voltages will be captured on event)
| Voltage Capture Low RNS Threshold |  | 1101 |  |  | UINT16 |  |  |  |  | R/W | NV | Volts | 0 - 32767
| Current Capture High RMS Threshold |  | 1102 |  | -1 | UINT16 |  |  |  |  | R/W | NV | Percent | 0 - 1000 | Percent of Breaker Size (800 = 80%)
| Current Capture Low RMS Threshold |  | 1103 |  |  | UINT16 |  |  |  |  | R/W | NV | Percent | 0 - 1000
Alarms and Status
Global Alarm |  |  | 1200 | 1207
| Global Latching Alarm Status |  | 1200 | [11 empty] | Summary of all 96 Channels
| Global Non-Latching Alarm Status |  | 1201
| Global Most Recent Latching Alarm Channel |  | 1202
| Global Most Recent Non-Latching Alarm Channel |  | 1203
| Total Number of Latching Channels In Alarm |  | 1204
| Total Number of Non-Latching Channels In Alarm |  | 1205
| Number of Waveform Capture Events |  | 1206
| Most Recent Waveform Capture Channel |  | 1207
Voltage Status
| Alarm Status |  | 1208 | 1210
| Voltage Alarm Status L1 |  | 1208
| Voltage Alarm Status L2 |  | 1209
| Voltage Alarm Status L3 |  | 1210
Branch Status
| Alarm Status |  | 1211 | 1306 | [10 empty] | Bit1 = High Latching Alarm, Bit2 = Low Latching Alarm, Bit11 = Waveform Capture Triggered, Bit12 = Zero Current Detected, Bit13 = Presence of Voltage (All Other Bits are Currently Unused)
| Branch Alarm Status - Circuit 1 | 1 | 1211 | [7 empty] | R
| Branch Alarm Status - Circuit 2 | 2 | 1212 | [7 empty] | R
| Branch Alarm Status - Circuit 3 | 3 | 1213 | [7 empty] | R
| Branch Alarm Status - Circuit 4 | 4 | 1214 | [7 empty] | R
| Branch Alarm Status - Circuit 5 | 5 | 1215 | [7 empty] | R
| Branch Alarm Status - Circuit 6 | 6 | 1216 | [7 empty] | R
| Branch Alarm Status - Circuit 7 | 7 | 1217 | [7 empty] | R
| Branch Alarm Status - Circuit 8 | 8 | 1218 | [7 empty] | R
| Branch Alarm Status - Circuit 9 | 9 | 1219 | [7 empty] | R
| Branch Alarm Status - Circuit 10 | 10 | 1220 | [7 empty] | R
| Branch Alarm Status - Circuit 11 | 11 | 1221 | [7 empty] | R
| Branch Alarm Status - Circuit 12 | 12 | 1222 | [7 empty] | R
| Branch Alarm Status - Circuit 13 | 13 | 1223 | [7 empty] | R
| Branch Alarm Status - Circuit 14 | 14 | 1224 | [7 empty] | R
| Branch Alarm Status - Circuit 15 | 15 | 1225 | [7 empty] | R
| Branch Alarm Status - Circuit 16 | 16 | 1226 | [7 empty] | R
| Branch Alarm Status - Circuit 17 | 17 | 1227 | [7 empty] | R
| Branch Alarm Status - Circuit 18 | 18 | 1228 | [7 empty] | R
| Branch Alarm Status - Circuit 19 | 19 | 1229 | [7 empty] | R
| Branch Alarm Status - Circuit 20 | 20 | 1230 | [7 empty] | R
| Branch Alarm Status - Circuit 21 | 21 | 1231 | [7 empty] | R
| Branch Alarm Status - Circuit 22 | 22 | 1232 | [7 empty] | R
| Branch Alarm Status - Circuit 23 | 23 | 1233 | [7 empty] | R
| Branch Alarm Status - Circuit 24 | 24 | 1234 | [7 empty] | R
| Branch Alarm Status - Circuit 25 | 25 | 1235 | [7 empty] | R
| Branch Alarm Status - Circuit 26 | 26 | 1236 | [7 empty] | R
| Branch Alarm Status - Circuit 27 | 27 | 1237 | [7 empty] | R
| Branch Alarm Status - Circuit 28 | 28 | 1238 | [7 empty] | R
| Branch Alarm Status - Circuit 29 | 29 | 1239 | [7 empty] | R
| Branch Alarm Status - Circuit 30 | 30 | 1240 | [7 empty] | R
| Branch Alarm Status - Circuit 31 | 31 | 1241 | [7 empty] | R
| Branch Alarm Status - Circuit 32 | 32 | 1242 | [7 empty] | R
| Branch Alarm Status - Circuit 33 | 33 | 1243 | [7 empty] | R
| Branch Alarm Status - Circuit 34 | 34 | 1244 | [7 empty] | R
| Branch Alarm Status - Circuit 35 | 35 | 1245 | [7 empty] | R
| Branch Alarm Status - Circuit 36 | 36 | 1246 | [7 empty] | R
| Branch Alarm Status - Circuit 37 | 37 | 1247 | [7 empty] | R
| Branch Alarm Status - Circuit 38 | 38 | 1248 | [7 empty] | R
| Branch Alarm Status - Circuit 39 | 39 | 1249 | [7 empty] | R
| Branch Alarm Status - Circuit 40 | 40 | 1250 | [7 empty] | R
| Branch Alarm Status - Circuit 41 | 41 | 1251 | [7 empty] | R
| Branch Alarm Status - Circuit 42 | 42 | 1252 | [7 empty] | R
| Branch Alarm Status - Circuit 43 | 43 | 1253 | [7 empty] | R
| Branch Alarm Status - Circuit 44 | 44 | 1254 | [7 empty] | R
| Branch Alarm Status - Circuit 45 | 45 | 1255 | [7 empty] | R
| Branch Alarm Status - Circuit 46 | 46 | 1256 | [7 empty] | R
| Branch Alarm Status - Circuit 47 | 47 | 1257 | [7 empty] | R
| Branch Alarm Status - Circuit 48 | 48 | 1258 | [7 empty] | R
| Branch Alarm Status - Circuit 49 | 49 | 1259 | [7 empty] | R
| Branch Alarm Status - Circuit 50 | 50 | 1260 | [7 empty] | R
| Branch Alarm Status - Circuit 51 | 51 | 1261 | [7 empty] | R
| Branch Alarm Status - Circuit 52 | 52 | 1262 | [7 empty] | R
| Branch Alarm Status - Circuit 53 | 53 | 1263 | [7 empty] | R
| Branch Alarm Status - Circuit 54 | 54 | 1264 | [7 empty] | R
| Branch Alarm Status - Circuit 55 | 55 | 1265 | [7 empty] | R
| Branch Alarm Status - Circuit 56 | 56 | 1266 | [7 empty] | R
| Branch Alarm Status - Circuit 57 | 57 | 1267 | [7 empty] | R
| Branch Alarm Status - Circuit 58 | 58 | 1268 | [7 empty] | R
| Branch Alarm Status - Circuit 59 | 59 | 1269 | [7 empty] | R
| Branch Alarm Status - Circuit 60 | 60 | 1270 | [7 empty] | R
| Branch Alarm Status - Circuit 61 | 61 | 1271 | [7 empty] | R
| Branch Alarm Status - Circuit 62 | 62 | 1272 | [7 empty] | R
| Branch Alarm Status - Circuit 63 | 63 | 1273 | [7 empty] | R
| Branch Alarm Status - Circuit 64 | 64 | 1274 | [7 empty] | R
| Branch Alarm Status - Circuit 65 | 65 | 1275 | [7 empty] | R
| Branch Alarm Status - Circuit 66 | 66 | 1276 | [7 empty] | R
| Branch Alarm Status - Circuit 67 | 67 | 1277 | [7 empty] | R
| Branch Alarm Status - Circuit 68 | 68 | 1278 | [7 empty] | R
| Branch Alarm Status - Circuit 69 | 69 | 1279 | [7 empty] | R
| Branch Alarm Status - Circuit 70 | 70 | 1280 | [7 empty] | R
| Branch Alarm Status - Circuit 71 | 71 | 1281 | [7 empty] | R
| Branch Alarm Status - Circuit 72 | 72 | 1282 | [7 empty] | R
| Branch Alarm Status - Circuit 73 | 73 | 1283 | [7 empty] | R
| Branch Alarm Status - Circuit 74 | 74 | 1284 | [7 empty] | R
| Branch Alarm Status - Circuit 75 | 75 | 1285 | [7 empty] | R
| Branch Alarm Status - Circuit 76 | 76 | 1286 | [7 empty] | R
| Branch Alarm Status - Circuit 77 | 77 | 1287 | [7 empty] | R
| Branch Alarm Status - Circuit 78 | 78 | 1288 | [7 empty] | R
| Branch Alarm Status - Circuit 79 | 79 | 1289 | [7 empty] | R
| Branch Alarm Status - Circuit 80 | 80 | 1290 | [7 empty] | R
| Branch Alarm Status - Circuit 81 | 81 | 1291 | [7 empty] | R
| Branch Alarm Status - Circuit 82 | 82 | 1292 | [7 empty] | R
| Branch Alarm Status - Circuit 83 | 83 | 1293 | [7 empty] | R
| Branch Alarm Status - Circuit 84 | 84 | 1294 | [7 empty] | R
| Branch Alarm Status - Circuit 85 | 85 | 1295 | [7 empty] | R
| Branch Alarm Status - Circuit 86 | 86 | 1296 | [7 empty] | R
| Branch Alarm Status - Circuit 87 | 87 | 1297 | [7 empty] | R
| Branch Alarm Status - Circuit 88 | 88 | 1298 | [7 empty] | R
| Branch Alarm Status - Circuit 89 | 89 | 1299 | [7 empty] | R
| Branch Alarm Status - Circuit 90 | 90 | 1300 | [7 empty] | R
| Branch Alarm Status - Circuit 91 | 91 | 1301 | [7 empty] | R
| Branch Alarm Status - Circuit 92 | 92 | 1302 | [7 empty] | R
| Branch Alarm Status - Circuit 93 | 93 | 1303 | [7 empty] | R
| Branch Alarm Status - Circuit 94 | 94 | 1304 | [7 empty] | R
| Branch Alarm Status - Circuit 95 | 95 | 1305 | [7 empty] | R
| Branch Alarm Status - Circuit 96 | 96 | 1306 | [7 empty] | R
| Alarm Summary Bit0 (6 Registers) |  | 1307 | 1312
| High Latching Alarm Summary (6 Registers) |  | 1313 | 1318
| Low Latching Alarm Summary (6 Registers) |  | 1319 | 1324
| Alarm Summary Bit3 (6 Registers) |  | 1325 | 1330
| Alarm Summary Bit4 (6 Registers) |  | 1331 | 1336
| Alarm Summary Bit5 (6 Registers) |  | 1337 | 1342
| Alarm Summary Bit6 (6 Registers) |  | 1343 | 1348
| Alarm Summary Bit7 (6 Registers) |  | 1349 | 1354
| Alarm Summary Bit8 (6 Registers) |  | 1355 | 1360
| Alarm Summary Bit9 (6 Registers) |  | 1361 | 1366
| Alarm Summary Bit10 (6 Registers) |  | 1367 | 1372
| Alarm Summary Bit11 (6 Registers) |  | 1373 | 1378
| Zero Current Summary (6 Registers) |  | 1379 | 1384
| Voltage Presence Summary (6 Registers) |  | 1385 | 1390
| Alarm Summary Bit14 (6 Registers) |  | 1391 | 1396
| Alarm Summary Bit15 (6 Registers) |  | 1397 | 1402
| Zero Current State |  | 1403 | 1498 |  | UINT16 | [8 empty] | Zero Current State registers will be updated when current drops to 0A
| Branch Zero Current State - Circuit 1 | 1 | 1403 | [7 empty] | R
| Branch Zero Current State - Circuit 2 | 2 | 1404 | [7 empty] | R
| Branch Zero Current State - Circuit 3 | 3 | 1405 | [7 empty] | R
| Branch Zero Current State - Circuit 4 | 4 | 1406 | [7 empty] | R
| Branch Zero Current State - Circuit 5 | 5 | 1407 | [7 empty] | R
| Branch Zero Current State - Circuit 6 | 6 | 1408 | [7 empty] | R
| Branch Zero Current State - Circuit 7 | 7 | 1409 | [7 empty] | R
| Branch Zero Current State - Circuit 8 | 8 | 1410 | [7 empty] | R
| Branch Zero Current State - Circuit 9 | 9 | 1411 | [7 empty] | R
| Branch Zero Current State - Circuit 10 | 10 | 1412 | [7 empty] | R
| Branch Zero Current State - Circuit 11 | 11 | 1413 | [7 empty] | R
| Branch Zero Current State - Circuit 12 | 12 | 1414 | [7 empty] | R
| Branch Zero Current State - Circuit 13 | 13 | 1415 | [7 empty] | R
| Branch Zero Current State - Circuit 14 | 14 | 1416 | [7 empty] | R
| Branch Zero Current State - Circuit 15 | 15 | 1417 | [7 empty] | R
| Branch Zero Current State - Circuit 16 | 16 | 1418 | [7 empty] | R
| Branch Zero Current State - Circuit 17 | 17 | 1419 | [7 empty] | R
| Branch Zero Current State - Circuit 18 | 18 | 1420 | [7 empty] | R
| Branch Zero Current State - Circuit 19 | 19 | 1421 | [7 empty] | R
| Branch Zero Current State - Circuit 20 | 20 | 1422 | [7 empty] | R
| Branch Zero Current State - Circuit 21 | 21 | 1423 | [7 empty] | R
| Branch Zero Current State - Circuit 22 | 22 | 1424 | [7 empty] | R
| Branch Zero Current State - Circuit 23 | 23 | 1425 | [7 empty] | R
| Branch Zero Current State - Circuit 24 | 24 | 1426 | [7 empty] | R
| Branch Zero Current State - Circuit 25 | 25 | 1427 | [7 empty] | R
| Branch Zero Current State - Circuit 26 | 26 | 1428 | [7 empty] | R
| Branch Zero Current State - Circuit 27 | 27 | 1429 | [7 empty] | R
| Branch Zero Current State - Circuit 28 | 28 | 1430 | [7 empty] | R
| Branch Zero Current State - Circuit 29 | 29 | 1431 | [7 empty] | R
| Branch Zero Current State - Circuit 30 | 30 | 1432 | [7 empty] | R
| Branch Zero Current State - Circuit 31 | 31 | 1433 | [7 empty] | R
| Branch Zero Current State - Circuit 32 | 32 | 1434 | [7 empty] | R
| Branch Zero Current State - Circuit 33 | 33 | 1435 | [7 empty] | R
| Branch Zero Current State - Circuit 34 | 34 | 1436 | [7 empty] | R
| Branch Zero Current State - Circuit 35 | 35 | 1437 | [7 empty] | R
| Branch Zero Current State - Circuit 36 | 36 | 1438 | [7 empty] | R
| Branch Zero Current State - Circuit 37 | 37 | 1439 | [7 empty] | R
| Branch Zero Current State - Circuit 38 | 38 | 1440 | [7 empty] | R
| Branch Zero Current State - Circuit 39 | 39 | 1441 | [7 empty] | R
| Branch Zero Current State - Circuit 40 | 40 | 1442 | [7 empty] | R
| Branch Zero Current State - Circuit 41 | 41 | 1443 | [7 empty] | R
| Branch Zero Current State - Circuit 42 | 42 | 1444 | [7 empty] | R
| Branch Zero Current State - Circuit 43 | 43 | 1445 | [7 empty] | R
| Branch Zero Current State - Circuit 44 | 44 | 1446 | [7 empty] | R
| Branch Zero Current State - Circuit 45 | 45 | 1447 | [7 empty] | R
| Branch Zero Current State - Circuit 46 | 46 | 1448 | [7 empty] | R
| Branch Zero Current State - Circuit 47 | 47 | 1449 | [7 empty] | R
| Branch Zero Current State - Circuit 48 | 48 | 1450 | [7 empty] | R
| Branch Zero Current State - Circuit 49 | 49 | 1451 | [7 empty] | R
| Branch Zero Current State - Circuit 50 | 50 | 1452 | [7 empty] | R
| Branch Zero Current State - Circuit 51 | 51 | 1453 | [7 empty] | R
| Branch Zero Current State - Circuit 52 | 52 | 1454 | [7 empty] | R
| Branch Zero Current State - Circuit 53 | 53 | 1455 | [7 empty] | R
| Branch Zero Current State - Circuit 54 | 54 | 1456 | [7 empty] | R
| Branch Zero Current State - Circuit 55 | 55 | 1457 | [7 empty] | R
| Branch Zero Current State - Circuit 56 | 56 | 1458 | [7 empty] | R
| Branch Zero Current State - Circuit 57 | 57 | 1459 | [7 empty] | R
| Branch Zero Current State - Circuit 58 | 58 | 1460 | [7 empty] | R
| Branch Zero Current State - Circuit 59 | 59 | 1461 | [7 empty] | R
| Branch Zero Current State - Circuit 60 | 60 | 1462 | [7 empty] | R
| Branch Zero Current State - Circuit 61 | 61 | 1463 | [7 empty] | R
| Branch Zero Current State - Circuit 62 | 62 | 1464 | [7 empty] | R
| Branch Zero Current State - Circuit 63 | 63 | 1465 | [7 empty] | R
| Branch Zero Current State - Circuit 64 | 64 | 1466 | [7 empty] | R
| Branch Zero Current State - Circuit 65 | 65 | 1467 | [7 empty] | R
| Branch Zero Current State - Circuit 66 | 66 | 1468 | [7 empty] | R
| Branch Zero Current State - Circuit 67 | 67 | 1469 | [7 empty] | R
| Branch Zero Current State - Circuit 68 | 68 | 1470 | [7 empty] | R
| Branch Zero Current State - Circuit 69 | 69 | 1471 | [7 empty] | R
| Branch Zero Current State - Circuit 70 | 70 | 1472 | [7 empty] | R
| Branch Zero Current State - Circuit 71 | 71 | 1473 | [7 empty] | R
| Branch Zero Current State - Circuit 72 | 72 | 1474 | [7 empty] | R
| Branch Zero Current State - Circuit 73 | 73 | 1475 | [7 empty] | R
| Branch Zero Current State - Circuit 74 | 74 | 1476 | [7 empty] | R
| Branch Zero Current State - Circuit 75 | 75 | 1477 | [7 empty] | R
| Branch Zero Current State - Circuit 76 | 76 | 1478 | [7 empty] | R
| Branch Zero Current State - Circuit 77 | 77 | 1479 | [7 empty] | R
| Branch Zero Current State - Circuit 78 | 78 | 1480 | [7 empty] | R
| Branch Zero Current State - Circuit 79 | 79 | 1481 | [7 empty] | R
| Branch Zero Current State - Circuit 80 | 80 | 1482 | [7 empty] | R
| Branch Zero Current State - Circuit 81 | 81 | 1483 | [7 empty] | R
| Branch Zero Current State - Circuit 82 | 82 | 1484 | [7 empty] | R
| Branch Zero Current State - Circuit 83 | 83 | 1485 | [7 empty] | R
| Branch Zero Current State - Circuit 84 | 84 | 1486 | [7 empty] | R
| Branch Zero Current State - Circuit 85 | 85 | 1487 | [7 empty] | R
| Branch Zero Current State - Circuit 86 | 86 | 1488 | [7 empty] | R
| Branch Zero Current State - Circuit 87 | 87 | 1489 | [7 empty] | R
| Branch Zero Current State - Circuit 88 | 88 | 1490 | [7 empty] | R
| Branch Zero Current State - Circuit 89 | 89 | 1491 | [7 empty] | R
| Branch Zero Current State - Circuit 90 | 90 | 1492 | [7 empty] | R
| Branch Zero Current State - Circuit 91 | 91 | 1493 | [7 empty] | R
| Branch Zero Current State - Circuit 92 | 92 | 1494 | [7 empty] | R
| Branch Zero Current State - Circuit 93 | 93 | 1495 | [7 empty] | R
| Branch Zero Current State - Circuit 94 | 94 | 1496 | [7 empty] | R
| Branch Zero Current State - Circuit 95 | 95 | 1497 | [7 empty] | R
| Branch Zero Current State - Circuit 96 | 96 | 1498 | [7 empty] | R
Smart Port/Panel Configuration
| Smart Port 1/2 (Panel 1) Circuit Configuration |  | 1800 | [11 empty] | 0 = Top Feed, 1 = Bottom Feed, 2 = Single Row Sequential, 3 = Single Row Odd/Even, 4 = Sequential
| Smart Port 3/4 (Panel 2) Circuit Configuration |  | 1801
| Panel 1 Location (64 Registers) |  | 1802 | 1865 | [10 empty] | Location string for Panel 1 and Panel 2, Each string supports up to 128 characters (64 characters)
| Panel 2 Location (64 Registers) |  | 1866 | 1929
| Smart Port 1 Configuration |  | 1930
| Smart Port 2 Configuration |  | 1931
| Smart Port 3 Configuration |  | 1932
| Smart Port 4 Configuration |  | 1933
| Smart Port 1 ID String (16 Registers) |  | 1934 | 1949
| Smart Port 2 ID String (16 Registers) |  | 1950 | 1965
| Smart Port 3 ID String (16 Registers) |  | 1966 | 1981
| Smart Port 4 ID String (16 Registers) |  | 1982 | 1997
Dynamic Smart Port | See Pointmap Based on Attached Card |  | 3000 | 3999
| Smart Port #1 (Dynamic Maps) |  | 3000 | 3249
| Smart Port #2 (Dynamic Maps) |  | 3250 | 3499
| Smart Port #3 (Dynamic Maps) |  | 3500 | 3749
| Smart Port #4 (Dynamic Maps) |  | 3750 | 3999
Reserved for AUX |  |  | 4000 | 4799
Voltage Readings
| Voltage Scale |  | 4800 |  |  | INT16 |  |  |  |  | R
| Frequency |  | 4801 |  | -2 | UINT16 | 4900 | 4901 | AI | 1 | R |  | Hz |  | Derived from L1
| Voltage LN Average |  | 4802 |  | 4800 | UINT16 | 4902 | 4903 | AI | 2 | R |  | Volts
| Voltage LL Average |  | 4803 |  | 4800 | UINT16 | 4904 | 4905 | AI | 3 | R |  | Volts
| Voltage LN |  | 4804 | 4806 | 4800 | UINT16 | 4906 | 4911 |  |  | R |  | Volts
| Voltage L1 |  | 4804 |  | 4800 | UINT16 | 4906 | 4907 | AI | 4 | R |  | Volts
| Voltage L2 |  | 4805 |  | 4800 | UINT16 | 4908 | 4909 | AI | 5 | R |  | Volts
| Voltage L3 |  | 4806 |  | 4800 | UINT16 | 4910 | 4911 | AI | 6 | R |  | Volts
| Voltage LL |  | 4807 | 4809 | 4800 | UINT16 | 4912 | 4917 |  |  | R |  | Volts
| Voltage L1 - L2 |  | 4807 |  | 4800 | UINT16 | 4912 | 4913 | AI | 7 | R |  | Volts
| Voltage L2 - L3 |  | 4808 |  | 4800 | UINT16 | 4914 | 4915 | AI | 8 | R |  | Volts
| Voltage L3 - L1 |  | 4809 |  | 4800 | UINT16 | 4916 | 4917 | AI | 9 | R |  | Volts
| Percent THD |  | 4810 | 4813 | -1 | UINT16 | 4918 | 4925 |  |  | R |  | Percent
| Percent THD Average (L1, L2 & L3) |  | 4810 |  | -1 | UINT16 | 4918 | 4919 | AI | 10 | R |  | Percent
| Percent THD - L1 |  | 4811 |  | -1 | UINT16 | 4920 | 4921 | AI | 11 | R |  | Percent
| Percent THD - L2 |  | 4812 |  | -1 | UINT16 | 4922 | 4923 | AI | 12 | R |  | Percent
| Percent THD - L3 |  | 4813 |  | -1 | UINT16 | 4924 | 4925 | AI | 13 | R |  | Percent
| Voltage Angle |  | 4814 | 4816 | -1 | INT16 | 4926 | 4931 |  |  | R |  | Degrees
| L1 Angle |  | 4814 |  | -1 | INT16 | 4926 | 4927 | AI | 14 | R |  | Degrees |  | Always Reads 0
| L2 Angle |  | 4815 |  | -1 | INT16 | 4928 | 4929 | AI | 15 | R |  | Degrees
| L3 Angle |  | 4816 |  | -1 | INT16 | 4930 | 4931 | AI | 16 | R |  | Degrees
Single Phase Reading by Type
| Energy Scale |  | 5000 | 5095 |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 1 | 1 | 5000 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 2 | 2 | 5001 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 3 | 3 | 5002 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 4 | 4 | 5003 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 5 | 5 | 5004 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 6 | 6 | 5005 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 7 | 7 | 5006 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 8 | 8 | 5007 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 9 | 9 | 5008 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 10 | 10 | 5009 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 11 | 11 | 5010 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 12 | 12 | 5011 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 13 | 13 | 5012 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 14 | 14 | 5013 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 15 | 15 | 5014 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 16 | 16 | 5015 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 17 | 17 | 5016 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 18 | 18 | 5017 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 19 | 19 | 5018 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 20 | 20 | 5019 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 21 | 21 | 5020 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 22 | 22 | 5021 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 23 | 23 | 5022 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 24 | 24 | 5023 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 25 | 25 | 5024 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 26 | 26 | 5025 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 27 | 27 | 5026 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 28 | 28 | 5027 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 29 | 29 | 5028 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 30 | 30 | 5029 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 31 | 31 | 5030 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 32 | 32 | 5031 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 33 | 33 | 5032 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 34 | 34 | 5033 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 35 | 35 | 5034 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 36 | 36 | 5035 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 37 | 37 | 5036 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 38 | 38 | 5037 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 39 | 39 | 5038 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 40 | 40 | 5039 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 41 | 41 | 5040 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 42 | 42 | 5041 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 43 | 43 | 5042 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 44 | 44 | 5043 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 45 | 45 | 5044 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 46 | 46 | 5045 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 47 | 47 | 5046 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 48 | 48 | 5047 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 49 | 49 | 5048 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 50 | 50 | 5049 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 51 | 51 | 5050 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 52 | 52 | 5051 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 53 | 53 | 5052 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 54 | 54 | 5053 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 55 | 55 | 5054 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 56 | 56 | 5055 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 57 | 57 | 5056 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 58 | 58 | 5057 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 59 | 59 | 5058 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 60 | 60 | 5059 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 61 | 61 | 5060 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 62 | 62 | 5061 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 63 | 63 | 5062 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 64 | 64 | 5063 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 65 | 65 | 5064 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 66 | 66 | 5065 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 67 | 67 | 5066 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 68 | 68 | 5067 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 69 | 69 | 5068 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 70 | 70 | 5069 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 71 | 71 | 5070 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 72 | 72 | 5071 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 73 | 73 | 5072 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 74 | 74 | 5073 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 75 | 75 | 5074 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 76 | 76 | 5075 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 77 | 77 | 5076 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 78 | 78 | 5077 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 79 | 79 | 5078 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 80 | 80 | 5079 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 81 | 81 | 5080 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 82 | 82 | 5081 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 83 | 83 | 5082 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 84 | 84 | 5083 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 85 | 85 | 5084 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 86 | 86 | 5085 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 87 | 87 | 5086 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 88 | 88 | 5087 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 89 | 89 | 5088 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 90 | 90 | 5089 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 91 | 91 | 5090 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 92 | 92 | 5091 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 93 | 93 | 5092 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 94 | 94 | 5093 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 95 | 95 | 5094 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 96 | 96 | 5095 |  |  | INT16 |  |  |  |  | R
| Power Scale |  | 5096 | 5191 |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 1 | 1 | 5096 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 2 | 2 | 5097 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 3 | 3 | 5098 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 4 | 4 | 5099 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 5 | 5 | 5100 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 6 | 6 | 5101 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 7 | 7 | 5102 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 8 | 8 | 5103 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 9 | 9 | 5104 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 10 | 10 | 5105 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 11 | 11 | 5106 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 12 | 12 | 5107 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 13 | 13 | 5108 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 14 | 14 | 5109 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 15 | 15 | 5110 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 16 | 16 | 5111 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 17 | 17 | 5112 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 18 | 18 | 5113 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 19 | 19 | 5114 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 20 | 20 | 5115 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 21 | 21 | 5116 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 22 | 22 | 5117 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 23 | 23 | 5118 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 24 | 24 | 5119 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 25 | 25 | 5120 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 26 | 26 | 5121 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 27 | 27 | 5122 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 28 | 28 | 5123 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 29 | 29 | 5124 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 30 | 30 | 5125 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 31 | 31 | 5126 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 32 | 32 | 5127 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 33 | 33 | 5128 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 34 | 34 | 5129 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 35 | 35 | 5130 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 36 | 36 | 5131 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 37 | 37 | 5132 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 38 | 38 | 5133 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 39 | 39 | 5134 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 40 | 40 | 5135 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 41 | 41 | 5136 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 42 | 42 | 5137 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 43 | 43 | 5138 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 44 | 44 | 5139 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 45 | 45 | 5140 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 46 | 46 | 5141 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 47 | 47 | 5142 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 48 | 48 | 5143 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 49 | 49 | 5144 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 50 | 50 | 5145 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 51 | 51 | 5146 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 52 | 52 | 5147 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 53 | 53 | 5148 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 54 | 54 | 5149 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 55 | 55 | 5150 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 56 | 56 | 5151 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 57 | 57 | 5152 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 58 | 58 | 5153 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 59 | 59 | 5154 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 60 | 60 | 5155 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 61 | 61 | 5156 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 62 | 62 | 5157 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 63 | 63 | 5158 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 64 | 64 | 5159 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 65 | 65 | 5160 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 66 | 66 | 5161 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 67 | 67 | 5162 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 68 | 68 | 5163 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 69 | 69 | 5164 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 70 | 70 | 5165 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 71 | 71 | 5166 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 72 | 72 | 5167 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 73 | 73 | 5168 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 74 | 74 | 5169 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 75 | 75 | 5170 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 76 | 76 | 5171 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 77 | 77 | 5172 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 78 | 78 | 5173 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 79 | 79 | 5174 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 80 | 80 | 5175 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 81 | 81 | 5176 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 82 | 82 | 5177 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 83 | 83 | 5178 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 84 | 84 | 5179 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 85 | 85 | 5180 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 86 | 86 | 5181 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 87 | 87 | 5182 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 88 | 88 | 5183 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 89 | 89 | 5184 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 90 | 90 | 5185 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 91 | 91 | 5186 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 92 | 92 | 5187 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 93 | 93 | 5188 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 94 | 94 | 5189 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 95 | 95 | 5190 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 96 | 96 | 5191 |  |  | INT16 |  |  |  |  | R
| Current Scale |  | 5192 | 5287 |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 1 | 1 | 5192 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 2 | 2 | 5193 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 3 | 3 | 5194 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 4 | 4 | 5195 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 5 | 5 | 5196 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 6 | 6 | 5197 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 7 | 7 | 5198 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 8 | 8 | 5199 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 9 | 9 | 5200 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 10 | 10 | 5201 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 11 | 11 | 5202 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 12 | 12 | 5203 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 13 | 13 | 5204 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 14 | 14 | 5205 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 15 | 15 | 5206 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 16 | 16 | 5207 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 17 | 17 | 5208 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 18 | 18 | 5209 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 19 | 19 | 5210 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 20 | 20 | 5211 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 21 | 21 | 5212 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 22 | 22 | 5213 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 23 | 23 | 5214 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 24 | 24 | 5215 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 25 | 25 | 5216 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 26 | 26 | 5217 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 27 | 27 | 5218 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 28 | 28 | 5219 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 29 | 29 | 5220 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 30 | 30 | 5221 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 31 | 31 | 5222 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 32 | 32 | 5223 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 33 | 33 | 5224 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 34 | 34 | 5225 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 35 | 35 | 5226 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 36 | 36 | 5227 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 37 | 37 | 5228 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 38 | 38 | 5229 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 39 | 39 | 5230 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 40 | 40 | 5231 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 41 | 41 | 5232 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 42 | 42 | 5233 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 43 | 43 | 5234 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 44 | 44 | 5235 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 45 | 45 | 5236 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 46 | 46 | 5237 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 47 | 47 | 5238 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 48 | 48 | 5239 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 49 | 49 | 5240 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 50 | 50 | 5241 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 51 | 51 | 5242 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 52 | 52 | 5243 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 53 | 53 | 5244 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 54 | 54 | 5245 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 55 | 55 | 5246 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 56 | 56 | 5247 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 57 | 57 | 5248 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 58 | 58 | 5249 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 59 | 59 | 5250 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 60 | 60 | 5251 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 61 | 61 | 5252 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 62 | 62 | 5253 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 63 | 63 | 5254 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 64 | 64 | 5255 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 65 | 65 | 5256 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 66 | 66 | 5257 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 67 | 67 | 5258 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 68 | 68 | 5259 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 69 | 69 | 5260 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 70 | 70 | 5261 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 71 | 71 | 5262 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 72 | 72 | 5263 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 73 | 73 | 5264 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 74 | 74 | 5265 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 75 | 75 | 5266 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 76 | 76 | 5267 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 77 | 77 | 5268 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 78 | 78 | 5269 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 79 | 79 | 5270 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 80 | 80 | 5271 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 81 | 81 | 5272 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 82 | 82 | 5273 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 83 | 83 | 5274 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 84 | 84 | 5275 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 85 | 85 | 5276 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 86 | 86 | 5277 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 87 | 87 | 5278 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 88 | 88 | 5279 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 89 | 89 | 5280 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 90 | 90 | 5281 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 91 | 91 | 5282 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 92 | 92 | 5283 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 93 | 93 | 5284 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 94 | 94 | 5285 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 95 | 95 | 5286 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 96 | 96 | 5287 |  |  | INT16 |  |  |  |  | R
| kWh |  | 5288 | 5479 | Energy | UINT32 | 10000 | 10191 | AI |  | R | NV | kWh |  | 32 bit unsigned integer
| kWh - Circuit 1 | 1 | 5288 | 5289 | 5000 | UINT32 | 10000 | 10001 | AI | 17 | R | NV | kWh
| kWh - Circuit 2 | 2 | 5290 | 5291 | 5001 | UINT32 | 10002 | 10003 | AI | 18 | R | NV | kWh
| kWh - Circuit 3 | 3 | 5292 | 5293 | 5002 | UINT32 | 10004 | 10005 | AI | 19 | R | NV | kWh
| kWh - Circuit 4 | 4 | 5294 | 5295 | 5003 | UINT32 | 10006 | 10007 | AI | 20 | R | NV | kWh
| kWh - Circuit 5 | 5 | 5296 | 5297 | 5004 | UINT32 | 10008 | 10009 | AI | 21 | R | NV | kWh
| kWh - Circuit 6 | 6 | 5298 | 5299 | 5005 | UINT32 | 10010 | 10011 | AI | 22 | R | NV | kWh
| kWh - Circuit 7 | 7 | 5300 | 5301 | 5006 | UINT32 | 10012 | 10013 | AI | 23 | R | NV | kWh
| kWh - Circuit 8 | 8 | 5302 | 5303 | 5007 | UINT32 | 10014 | 10015 | AI | 24 | R | NV | kWh
| kWh - Circuit 9 | 9 | 5304 | 5305 | 5008 | UINT32 | 10016 | 10017 | AI | 25 | R | NV | kWh
| kWh - Circuit 10 | 10 | 5306 | 5307 | 5009 | UINT32 | 10018 | 10019 | AI | 26 | R | NV | kWh
| kWh - Circuit 11 | 11 | 5308 | 5309 | 5010 | UINT32 | 10020 | 10021 | AI | 27 | R | NV | kWh
| kWh - Circuit 12 | 12 | 5310 | 5311 | 5011 | UINT32 | 10022 | 10023 | AI | 28 | R | NV | kWh
| kWh - Circuit 13 | 13 | 5312 | 5313 | 5012 | UINT32 | 10024 | 10025 | AI | 29 | R | NV | kWh
| kWh - Circuit 14 | 14 | 5314 | 5315 | 5013 | UINT32 | 10026 | 10027 | AI | 30 | R | NV | kWh
| kWh - Circuit 15 | 15 | 5316 | 5317 | 5014 | UINT32 | 10028 | 10029 | AI | 31 | R | NV | kWh
| kWh - Circuit 16 | 16 | 5318 | 5319 | 5015 | UINT32 | 10030 | 10031 | AI | 32 | R | NV | kWh
| kWh - Circuit 17 | 17 | 5320 | 5321 | 5016 | UINT32 | 10032 | 10033 | AI | 33 | R | NV | kWh
| kWh - Circuit 18 | 18 | 5322 | 5323 | 5017 | UINT32 | 10034 | 10035 | AI | 34 | R | NV | kWh
| kWh - Circuit 19 | 19 | 5324 | 5325 | 5018 | UINT32 | 10036 | 10037 | AI | 35 | R | NV | kWh
| kWh - Circuit 20 | 20 | 5326 | 5327 | 5019 | UINT32 | 10038 | 10039 | AI | 36 | R | NV | kWh
| kWh - Circuit 21 | 21 | 5328 | 5329 | 5020 | UINT32 | 10040 | 10041 | AI | 37 | R | NV | kWh
| kWh - Circuit 22 | 22 | 5330 | 5331 | 5021 | UINT32 | 10042 | 10043 | AI | 38 | R | NV | kWh
| kWh - Circuit 23 | 23 | 5332 | 5333 | 5022 | UINT32 | 10044 | 10045 | AI | 39 | R | NV | kWh
| kWh - Circuit 24 | 24 | 5334 | 5335 | 5023 | UINT32 | 10046 | 10047 | AI | 40 | R | NV | kWh
| kWh - Circuit 25 | 25 | 5336 | 5337 | 5024 | UINT32 | 10048 | 10049 | AI | 41 | R | NV | kWh
| kWh - Circuit 26 | 26 | 5338 | 5339 | 5025 | UINT32 | 10050 | 10051 | AI | 42 | R | NV | kWh
| kWh - Circuit 27 | 27 | 5340 | 5341 | 5026 | UINT32 | 10052 | 10053 | AI | 43 | R | NV | kWh
| kWh - Circuit 28 | 28 | 5342 | 5343 | 5027 | UINT32 | 10054 | 10055 | AI | 44 | R | NV | kWh
| kWh - Circuit 29 | 29 | 5344 | 5345 | 5028 | UINT32 | 10056 | 10057 | AI | 45 | R | NV | kWh
| kWh - Circuit 30 | 30 | 5346 | 5347 | 5029 | UINT32 | 10058 | 10059 | AI | 46 | R | NV | kWh
| kWh - Circuit 31 | 31 | 5348 | 5349 | 5030 | UINT32 | 10060 | 10061 | AI | 47 | R | NV | kWh
| kWh - Circuit 32 | 32 | 5350 | 5351 | 5031 | UINT32 | 10062 | 10063 | AI | 48 | R | NV | kWh
| kWh - Circuit 33 | 33 | 5352 | 5353 | 5032 | UINT32 | 10064 | 10065 | AI | 49 | R | NV | kWh
| kWh - Circuit 34 | 34 | 5354 | 5355 | 5033 | UINT32 | 10066 | 10067 | AI | 50 | R | NV | kWh
| kWh - Circuit 35 | 35 | 5356 | 5357 | 5034 | UINT32 | 10068 | 10069 | AI | 51 | R | NV | kWh
| kWh - Circuit 36 | 36 | 5358 | 5359 | 5035 | UINT32 | 10070 | 10071 | AI | 52 | R | NV | kWh
| kWh - Circuit 37 | 37 | 5360 | 5361 | 5036 | UINT32 | 10072 | 10073 | AI | 53 | R | NV | kWh
| kWh - Circuit 38 | 38 | 5362 | 5363 | 5037 | UINT32 | 10074 | 10075 | AI | 54 | R | NV | kWh
| kWh - Circuit 39 | 39 | 5364 | 5365 | 5038 | UINT32 | 10076 | 10077 | AI | 55 | R | NV | kWh
| kWh - Circuit 40 | 40 | 5366 | 5367 | 5039 | UINT32 | 10078 | 10079 | AI | 56 | R | NV | kWh
| kWh - Circuit 41 | 41 | 5368 | 5369 | 5040 | UINT32 | 10080 | 10081 | AI | 57 | R | NV | kWh
| kWh - Circuit 42 | 42 | 5370 | 5371 | 5041 | UINT32 | 10082 | 10083 | AI | 58 | R | NV | kWh
| kWh - Circuit 43 | 43 | 5372 | 5373 | 5042 | UINT32 | 10084 | 10085 | AI | 59 | R | NV | kWh
| kWh - Circuit 44 | 44 | 5374 | 5375 | 5043 | UINT32 | 10086 | 10087 | AI | 60 | R | NV | kWh
| kWh - Circuit 45 | 45 | 5376 | 5377 | 5044 | UINT32 | 10088 | 10089 | AI | 61 | R | NV | kWh
| kWh - Circuit 46 | 46 | 5378 | 5379 | 5045 | UINT32 | 10090 | 10091 | AI | 62 | R | NV | kWh
| kWh - Circuit 47 | 47 | 5380 | 5381 | 5046 | UINT32 | 10092 | 10093 | AI | 63 | R | NV | kWh
| kWh - Circuit 48 | 48 | 5382 | 5383 | 5047 | UINT32 | 10094 | 10095 | AI | 64 | R | NV | kWh
| kWh - Circuit 49 | 49 | 5384 | 5385 | 5048 | UINT32 | 10096 | 10097 | AI | 65 | R | NV | kWh
| kWh - Circuit 50 | 50 | 5386 | 5387 | 5049 | UINT32 | 10098 | 10099 | AI | 66 | R | NV | kWh
| kWh - Circuit 51 | 51 | 5388 | 5389 | 5050 | UINT32 | 10100 | 10101 | AI | 67 | R | NV | kWh
| kWh - Circuit 52 | 52 | 5390 | 5391 | 5051 | UINT32 | 10102 | 10103 | AI | 68 | R | NV | kWh
| kWh - Circuit 53 | 53 | 5392 | 5393 | 5052 | UINT32 | 10104 | 10105 | AI | 69 | R | NV | kWh
| kWh - Circuit 54 | 54 | 5394 | 5395 | 5053 | UINT32 | 10106 | 10107 | AI | 70 | R | NV | kWh
| kWh - Circuit 55 | 55 | 5396 | 5397 | 5054 | UINT32 | 10108 | 10109 | AI | 71 | R | NV | kWh
| kWh - Circuit 56 | 56 | 5398 | 5399 | 5055 | UINT32 | 10110 | 10111 | AI | 72 | R | NV | kWh
| kWh - Circuit 57 | 57 | 5400 | 5401 | 5056 | UINT32 | 10112 | 10113 | AI | 73 | R | NV | kWh
| kWh - Circuit 58 | 58 | 5402 | 5403 | 5057 | UINT32 | 10114 | 10115 | AI | 74 | R | NV | kWh
| kWh - Circuit 59 | 59 | 5404 | 5405 | 5058 | UINT32 | 10116 | 10117 | AI | 75 | R | NV | kWh
| kWh - Circuit 60 | 60 | 5406 | 5407 | 5059 | UINT32 | 10118 | 10119 | AI | 76 | R | NV | kWh
| kWh - Circuit 61 | 61 | 5408 | 5409 | 5060 | UINT32 | 10120 | 10121 | AI | 77 | R | NV | kWh
| kWh - Circuit 62 | 62 | 5410 | 5411 | 5061 | UINT32 | 10122 | 10123 | AI | 78 | R | NV | kWh
| kWh - Circuit 63 | 63 | 5412 | 5413 | 5062 | UINT32 | 10124 | 10125 | AI | 79 | R | NV | kWh
| kWh - Circuit 64 | 64 | 5414 | 5415 | 5063 | UINT32 | 10126 | 10127 | AI | 80 | R | NV | kWh
| kWh - Circuit 65 | 65 | 5416 | 5417 | 5064 | UINT32 | 10128 | 10129 | AI | 81 | R | NV | kWh
| kWh - Circuit 66 | 66 | 5418 | 5419 | 5065 | UINT32 | 10130 | 10131 | AI | 82 | R | NV | kWh
| kWh - Circuit 67 | 67 | 5420 | 5421 | 5066 | UINT32 | 10132 | 10133 | AI | 83 | R | NV | kWh
| kWh - Circuit 68 | 68 | 5422 | 5423 | 5067 | UINT32 | 10134 | 10135 | AI | 84 | R | NV | kWh
| kWh - Circuit 69 | 69 | 5424 | 5425 | 5068 | UINT32 | 10136 | 10137 | AI | 85 | R | NV | kWh
| kWh - Circuit 70 | 70 | 5426 | 5427 | 5069 | UINT32 | 10138 | 10139 | AI | 86 | R | NV | kWh
| kWh - Circuit 71 | 71 | 5428 | 5429 | 5070 | UINT32 | 10140 | 10141 | AI | 87 | R | NV | kWh
| kWh - Circuit 72 | 72 | 5430 | 5431 | 5071 | UINT32 | 10142 | 10143 | AI | 88 | R | NV | kWh
| kWh - Circuit 73 | 73 | 5432 | 5433 | 5072 | UINT32 | 10144 | 10145 | AI | 89 | R | NV | kWh
| kWh - Circuit 74 | 74 | 5434 | 5435 | 5073 | UINT32 | 10146 | 10147 | AI | 90 | R | NV | kWh
| kWh - Circuit 75 | 75 | 5436 | 5437 | 5074 | UINT32 | 10148 | 10149 | AI | 91 | R | NV | kWh
| kWh - Circuit 76 | 76 | 5438 | 5439 | 5075 | UINT32 | 10150 | 10151 | AI | 92 | R | NV | kWh
| kWh - Circuit 77 | 77 | 5440 | 5441 | 5076 | UINT32 | 10152 | 10153 | AI | 93 | R | NV | kWh
| kWh - Circuit 78 | 78 | 5442 | 5443 | 5077 | UINT32 | 10154 | 10155 | AI | 94 | R | NV | kWh
| kWh - Circuit 79 | 79 | 5444 | 5445 | 5078 | UINT32 | 10156 | 10157 | AI | 95 | R | NV | kWh
| kWh - Circuit 80 | 80 | 5446 | 5447 | 5079 | UINT32 | 10158 | 10159 | AI | 96 | R | NV | kWh
| kWh - Circuit 81 | 81 | 5448 | 5449 | 5080 | UINT32 | 10160 | 10161 | AI | 97 | R | NV | kWh
| kWh - Circuit 82 | 82 | 5450 | 5451 | 5081 | UINT32 | 10162 | 10163 | AI | 98 | R | NV | kWh
| kWh - Circuit 83 | 83 | 5452 | 5453 | 5082 | UINT32 | 10164 | 10165 | AI | 99 | R | NV | kWh
| kWh - Circuit 84 | 84 | 5454 | 5455 | 5083 | UINT32 | 10166 | 10167 | AI | 100 | R | NV | kWh
| kWh - Circuit 85 | 85 | 5456 | 5457 | 5084 | UINT32 | 10168 | 10169 | AI | 101 | R | NV | kWh
| kWh - Circuit 86 | 86 | 5458 | 5459 | 5085 | UINT32 | 10170 | 10171 | AI | 102 | R | NV | kWh
| kWh - Circuit 87 | 87 | 5460 | 5461 | 5086 | UINT32 | 10172 | 10173 | AI | 103 | R | NV | kWh
| kWh - Circuit 88 | 88 | 5462 | 5463 | 5087 | UINT32 | 10174 | 10175 | AI | 104 | R | NV | kWh
| kWh - Circuit 89 | 89 | 5464 | 5465 | 5088 | UINT32 | 10176 | 10177 | AI | 105 | R | NV | kWh
| kWh - Circuit 90 | 90 | 5466 | 5467 | 5089 | UINT32 | 10178 | 10179 | AI | 106 | R | NV | kWh
| kWh - Circuit 91 | 91 | 5468 | 5469 | 5090 | UINT32 | 10180 | 10181 | AI | 107 | R | NV | kWh
| kWh - Circuit 92 | 92 | 5470 | 5471 | 5091 | UINT32 | 10182 | 10183 | AI | 108 | R | NV | kWh
| kWh - Circuit 93 | 93 | 5472 | 5473 | 5092 | UINT32 | 10184 | 10185 | AI | 109 | R | NV | kWh
| kWh - Circuit 94 | 94 | 5474 | 5475 | 5093 | UINT32 | 10186 | 10187 | AI | 110 | R | NV | kWh
| kWh - Circuit 95 | 95 | 5476 | 5477 | 5094 | UINT32 | 10188 | 10189 | AI | 111 | R | NV | kWh
| kWh - Circuit 96 | 96 | 5478 | 5479 | 5095 | UINT32 | 10190 | 10191 | AI | 112 | R | NV | kWh
| kVARh |  | 5480 | 5671 | Energy | UINT32 | 10192 | 10383 | AI |  | R | NV | kVARh |  | 32 bit unsigned integer
| kVARh - Circuit 1 | 1 | 5480 | 5481 | 5000 | UINT32 | 10192 | 10193 | AI | 113 | R | NV | kVARh
| kVARh - Circuit 2 | 2 | 5482 | 5483 | 5001 | UINT32 | 10194 | 10195 | AI | 114 | R | NV | kVARh
| kVARh - Circuit 3 | 3 | 5484 | 5485 | 5002 | UINT32 | 10196 | 10197 | AI | 115 | R | NV | kVARh
| kVARh - Circuit 4 | 4 | 5486 | 5487 | 5003 | UINT32 | 10198 | 10199 | AI | 116 | R | NV | kVARh
| kVARh - Circuit 5 | 5 | 5488 | 5489 | 5004 | UINT32 | 10200 | 10201 | AI | 117 | R | NV | kVARh
| kVARh - Circuit 6 | 6 | 5490 | 5491 | 5005 | UINT32 | 10202 | 10203 | AI | 118 | R | NV | kVARh
| kVARh - Circuit 7 | 7 | 5492 | 5493 | 5006 | UINT32 | 10204 | 10205 | AI | 119 | R | NV | kVARh
| kVARh - Circuit 8 | 8 | 5494 | 5495 | 5007 | UINT32 | 10206 | 10207 | AI | 120 | R | NV | kVARh
| kVARh - Circuit 9 | 9 | 5496 | 5497 | 5008 | UINT32 | 10208 | 10209 | AI | 121 | R | NV | kVARh
| kVARh - Circuit 10 | 10 | 5498 | 5499 | 5009 | UINT32 | 10210 | 10211 | AI | 122 | R | NV | kVARh
| kVARh - Circuit 11 | 11 | 5500 | 5501 | 5010 | UINT32 | 10212 | 10213 | AI | 123 | R | NV | kVARh
| kVARh - Circuit 12 | 12 | 5502 | 5503 | 5011 | UINT32 | 10214 | 10215 | AI | 124 | R | NV | kVARh
| kVARh - Circuit 13 | 13 | 5504 | 5505 | 5012 | UINT32 | 10216 | 10217 | AI | 125 | R | NV | kVARh
| kVARh - Circuit 14 | 14 | 5506 | 5507 | 5013 | UINT32 | 10218 | 10219 | AI | 126 | R | NV | kVARh
| kVARh - Circuit 15 | 15 | 5508 | 5509 | 5014 | UINT32 | 10220 | 10221 | AI | 127 | R | NV | kVARh
| kVARh - Circuit 16 | 16 | 5510 | 5511 | 5015 | UINT32 | 10222 | 10223 | AI | 128 | R | NV | kVARh
| kVARh - Circuit 17 | 17 | 5512 | 5513 | 5016 | UINT32 | 10224 | 10225 | AI | 129 | R | NV | kVARh
| kVARh - Circuit 18 | 18 | 5514 | 5515 | 5017 | UINT32 | 10226 | 10227 | AI | 130 | R | NV | kVARh
| kVARh - Circuit 19 | 19 | 5516 | 5517 | 5018 | UINT32 | 10228 | 10229 | AI | 131 | R | NV | kVARh
| kVARh - Circuit 20 | 20 | 5518 | 5519 | 5019 | UINT32 | 10230 | 10231 | AI | 132 | R | NV | kVARh
| kVARh - Circuit 21 | 21 | 5520 | 5521 | 5020 | UINT32 | 10232 | 10233 | AI | 133 | R | NV | kVARh
| kVARh - Circuit 22 | 22 | 5522 | 5523 | 5021 | UINT32 | 10234 | 10235 | AI | 134 | R | NV | kVARh
| kVARh - Circuit 23 | 23 | 5524 | 5525 | 5022 | UINT32 | 10236 | 10237 | AI | 135 | R | NV | kVARh
| kVARh - Circuit 24 | 24 | 5526 | 5527 | 5023 | UINT32 | 10238 | 10239 | AI | 136 | R | NV | kVARh
| kVARh - Circuit 25 | 25 | 5528 | 5529 | 5024 | UINT32 | 10240 | 10241 | AI | 137 | R | NV | kVARh
| kVARh - Circuit 26 | 26 | 5530 | 5531 | 5025 | UINT32 | 10242 | 10243 | AI | 138 | R | NV | kVARh
| kVARh - Circuit 27 | 27 | 5532 | 5533 | 5026 | UINT32 | 10244 | 10245 | AI | 139 | R | NV | kVARh
| kVARh - Circuit 28 | 28 | 5534 | 5535 | 5027 | UINT32 | 10246 | 10247 | AI | 140 | R | NV | kVARh
| kVARh - Circuit 29 | 29 | 5536 | 5537 | 5028 | UINT32 | 10248 | 10249 | AI | 141 | R | NV | kVARh
| kVARh - Circuit 30 | 30 | 5538 | 5539 | 5029 | UINT32 | 10250 | 10251 | AI | 142 | R | NV | kVARh
| kVARh - Circuit 31 | 31 | 5540 | 5541 | 5030 | UINT32 | 10252 | 10253 | AI | 143 | R | NV | kVARh
| kVARh - Circuit 32 | 32 | 5542 | 5543 | 5031 | UINT32 | 10254 | 10255 | AI | 144 | R | NV | kVARh
| kVARh - Circuit 33 | 33 | 5544 | 5545 | 5032 | UINT32 | 10256 | 10257 | AI | 145 | R | NV | kVARh
| kVARh - Circuit 34 | 34 | 5546 | 5547 | 5033 | UINT32 | 10258 | 10259 | AI | 146 | R | NV | kVARh
| kVARh - Circuit 35 | 35 | 5548 | 5549 | 5034 | UINT32 | 10260 | 10261 | AI | 147 | R | NV | kVARh
| kVARh - Circuit 36 | 36 | 5550 | 5551 | 5035 | UINT32 | 10262 | 10263 | AI | 148 | R | NV | kVARh
| kVARh - Circuit 37 | 37 | 5552 | 5553 | 5036 | UINT32 | 10264 | 10265 | AI | 149 | R | NV | kVARh
| kVARh - Circuit 38 | 38 | 5554 | 5555 | 5037 | UINT32 | 10266 | 10267 | AI | 150 | R | NV | kVARh
| kVARh - Circuit 39 | 39 | 5556 | 5557 | 5038 | UINT32 | 10268 | 10269 | AI | 151 | R | NV | kVARh
| kVARh - Circuit 40 | 40 | 5558 | 5559 | 5039 | UINT32 | 10270 | 10271 | AI | 152 | R | NV | kVARh
| kVARh - Circuit 41 | 41 | 5560 | 5561 | 5040 | UINT32 | 10272 | 10273 | AI | 153 | R | NV | kVARh
| kVARh - Circuit 42 | 42 | 5562 | 5563 | 5041 | UINT32 | 10274 | 10275 | AI | 154 | R | NV | kVARh
| kVARh - Circuit 43 | 43 | 5564 | 5565 | 5042 | UINT32 | 10276 | 10277 | AI | 155 | R | NV | kVARh
| kVARh - Circuit 44 | 44 | 5566 | 5567 | 5043 | UINT32 | 10278 | 10279 | AI | 156 | R | NV | kVARh
| kVARh - Circuit 45 | 45 | 5568 | 5569 | 5044 | UINT32 | 10280 | 10281 | AI | 157 | R | NV | kVARh
| kVARh - Circuit 46 | 46 | 5570 | 5571 | 5045 | UINT32 | 10282 | 10283 | AI | 158 | R | NV | kVARh
| kVARh - Circuit 47 | 47 | 5572 | 5573 | 5046 | UINT32 | 10284 | 10285 | AI | 159 | R | NV | kVARh
| kVARh - Circuit 48 | 48 | 5574 | 5575 | 5047 | UINT32 | 10286 | 10287 | AI | 160 | R | NV | kVARh
| kVARh - Circuit 49 | 49 | 5576 | 5577 | 5048 | UINT32 | 10288 | 10289 | AI | 161 | R | NV | kVARh
| kVARh - Circuit 50 | 50 | 5578 | 5579 | 5049 | UINT32 | 10290 | 10291 | AI | 162 | R | NV | kVARh
| kVARh - Circuit 51 | 51 | 5580 | 5581 | 5050 | UINT32 | 10292 | 10293 | AI | 163 | R | NV | kVARh
| kVARh - Circuit 52 | 52 | 5582 | 5583 | 5051 | UINT32 | 10294 | 10295 | AI | 164 | R | NV | kVARh
| kVARh - Circuit 53 | 53 | 5584 | 5585 | 5052 | UINT32 | 10296 | 10297 | AI | 165 | R | NV | kVARh
| kVARh - Circuit 54 | 54 | 5586 | 5587 | 5053 | UINT32 | 10298 | 10299 | AI | 166 | R | NV | kVARh
| kVARh - Circuit 55 | 55 | 5588 | 5589 | 5054 | UINT32 | 10300 | 10301 | AI | 167 | R | NV | kVARh
| kVARh - Circuit 56 | 56 | 5590 | 5591 | 5055 | UINT32 | 10302 | 10303 | AI | 168 | R | NV | kVARh
| kVARh - Circuit 57 | 57 | 5592 | 5593 | 5056 | UINT32 | 10304 | 10305 | AI | 169 | R | NV | kVARh
| kVARh - Circuit 58 | 58 | 5594 | 5595 | 5057 | UINT32 | 10306 | 10307 | AI | 170 | R | NV | kVARh
| kVARh - Circuit 59 | 59 | 5596 | 5597 | 5058 | UINT32 | 10308 | 10309 | AI | 171 | R | NV | kVARh
| kVARh - Circuit 60 | 60 | 5598 | 5599 | 5059 | UINT32 | 10310 | 10311 | AI | 172 | R | NV | kVARh
| kVARh - Circuit 61 | 61 | 5600 | 5601 | 5060 | UINT32 | 10312 | 10313 | AI | 173 | R | NV | kVARh
| kVARh - Circuit 62 | 62 | 5602 | 5603 | 5061 | UINT32 | 10314 | 10315 | AI | 174 | R | NV | kVARh
| kVARh - Circuit 63 | 63 | 5604 | 5605 | 5062 | UINT32 | 10316 | 10317 | AI | 175 | R | NV | kVARh
| kVARh - Circuit 64 | 64 | 5606 | 5607 | 5063 | UINT32 | 10318 | 10319 | AI | 176 | R | NV | kVARh
| kVARh - Circuit 65 | 65 | 5608 | 5609 | 5064 | UINT32 | 10320 | 10321 | AI | 177 | R | NV | kVARh
| kVARh - Circuit 66 | 66 | 5610 | 5611 | 5065 | UINT32 | 10322 | 10323 | AI | 178 | R | NV | kVARh
| kVARh - Circuit 67 | 67 | 5612 | 5613 | 5066 | UINT32 | 10324 | 10325 | AI | 179 | R | NV | kVARh
| kVARh - Circuit 68 | 68 | 5614 | 5615 | 5067 | UINT32 | 10326 | 10327 | AI | 180 | R | NV | kVARh
| kVARh - Circuit 69 | 69 | 5616 | 5617 | 5068 | UINT32 | 10328 | 10329 | AI | 181 | R | NV | kVARh
| kVARh - Circuit 70 | 70 | 5618 | 5619 | 5069 | UINT32 | 10330 | 10331 | AI | 182 | R | NV | kVARh
| kVARh - Circuit 71 | 71 | 5620 | 5621 | 5070 | UINT32 | 10332 | 10333 | AI | 183 | R | NV | kVARh
| kVARh - Circuit 72 | 72 | 5622 | 5623 | 5071 | UINT32 | 10334 | 10335 | AI | 184 | R | NV | kVARh
| kVARh - Circuit 73 | 73 | 5624 | 5625 | 5072 | UINT32 | 10336 | 10337 | AI | 185 | R | NV | kVARh
| kVARh - Circuit 74 | 74 | 5626 | 5627 | 5073 | UINT32 | 10338 | 10339 | AI | 186 | R | NV | kVARh
| kVARh - Circuit 75 | 75 | 5628 | 5629 | 5074 | UINT32 | 10340 | 10341 | AI | 187 | R | NV | kVARh
| kVARh - Circuit 76 | 76 | 5630 | 5631 | 5075 | UINT32 | 10342 | 10343 | AI | 188 | R | NV | kVARh
| kVARh - Circuit 77 | 77 | 5632 | 5633 | 5076 | UINT32 | 10344 | 10345 | AI | 189 | R | NV | kVARh
| kVARh - Circuit 78 | 78 | 5634 | 5635 | 5077 | UINT32 | 10346 | 10347 | AI | 190 | R | NV | kVARh
| kVARh - Circuit 79 | 79 | 5636 | 5637 | 5078 | UINT32 | 10348 | 10349 | AI | 191 | R | NV | kVARh
| kVARh - Circuit 80 | 80 | 5638 | 5639 | 5079 | UINT32 | 10350 | 10351 | AI | 192 | R | NV | kVARh
| kVARh - Circuit 81 | 81 | 5640 | 5641 | 5080 | UINT32 | 10352 | 10353 | AI | 193 | R | NV | kVARh
| kVARh - Circuit 82 | 82 | 5642 | 5643 | 5081 | UINT32 | 10354 | 10355 | AI | 194 | R | NV | kVARh
| kVARh - Circuit 83 | 83 | 5644 | 5645 | 5082 | UINT32 | 10356 | 10357 | AI | 195 | R | NV | kVARh
| kVARh - Circuit 84 | 84 | 5646 | 5647 | 5083 | UINT32 | 10358 | 10359 | AI | 196 | R | NV | kVARh
| kVARh - Circuit 85 | 85 | 5648 | 5649 | 5084 | UINT32 | 10360 | 10361 | AI | 197 | R | NV | kVARh
| kVARh - Circuit 86 | 86 | 5650 | 5651 | 5085 | UINT32 | 10362 | 10363 | AI | 198 | R | NV | kVARh
| kVARh - Circuit 87 | 87 | 5652 | 5653 | 5086 | UINT32 | 10364 | 10365 | AI | 199 | R | NV | kVARh
| kVARh - Circuit 88 | 88 | 5654 | 5655 | 5087 | UINT32 | 10366 | 10367 | AI | 200 | R | NV | kVARh
| kVARh - Circuit 89 | 89 | 5656 | 5657 | 5088 | UINT32 | 10368 | 10369 | AI | 201 | R | NV | kVARh
| kVARh - Circuit 90 | 90 | 5658 | 5659 | 5089 | UINT32 | 10370 | 10371 | AI | 202 | R | NV | kVARh
| kVARh - Circuit 91 | 91 | 5660 | 5661 | 5090 | UINT32 | 10372 | 10373 | AI | 203 | R | NV | kVARh
| kVARh - Circuit 92 | 92 | 5662 | 5663 | 5091 | UINT32 | 10374 | 10375 | AI | 204 | R | NV | kVARh
| kVARh - Circuit 93 | 93 | 5664 | 5665 | 5092 | UINT32 | 10376 | 10377 | AI | 205 | R | NV | kVARh
| kVARh - Circuit 94 | 94 | 5666 | 5667 | 5093 | UINT32 | 10378 | 10379 | AI | 206 | R | NV | kVARh
| kVARh - Circuit 95 | 95 | 5668 | 5669 | 5094 | UINT32 | 10380 | 10381 | AI | 207 | R | NV | kVARh
| kVARh - Circuit 96 | 96 | 5670 | 5671 | 5095 | UINT32 | 10382 | 10383 | AI | 208 | R | NV | kVARh
| kVAh |  | 5672 | 5863 | Energy | UINT32 | 10384 | 10575 | AI |  | R | NV | kVAh
| kVAh - Circuit 1 | 1 | 5672 | 5673 | 5000 | UINT32 | 10384 | 10385 | AI | 209 | R | NV | kVAh
| kVAh - Circuit 2 | 2 | 5674 | 5675 | 5001 | UINT32 | 10386 | 10387 | AI | 210 | R | NV | kVAh
| kVAh - Circuit 3 | 3 | 5676 | 5677 | 5002 | UINT32 | 10388 | 10389 | AI | 211 | R | NV | kVAh
| kVAh - Circuit 4 | 4 | 5678 | 5679 | 5003 | UINT32 | 10390 | 10391 | AI | 212 | R | NV | kVAh
| kVAh - Circuit 5 | 5 | 5680 | 5681 | 5004 | UINT32 | 10392 | 10393 | AI | 213 | R | NV | kVAh
| kVAh - Circuit 6 | 6 | 5682 | 5683 | 5005 | UINT32 | 10394 | 10395 | AI | 214 | R | NV | kVAh
| kVAh - Circuit 7 | 7 | 5684 | 5685 | 5006 | UINT32 | 10396 | 10397 | AI | 215 | R | NV | kVAh
| kVAh - Circuit 8 | 8 | 5686 | 5687 | 5007 | UINT32 | 10398 | 10399 | AI | 216 | R | NV | kVAh
| kVAh - Circuit 9 | 9 | 5688 | 5689 | 5008 | UINT32 | 10400 | 10401 | AI | 217 | R | NV | kVAh
| kVAh - Circuit 10 | 10 | 5690 | 5691 | 5009 | UINT32 | 10402 | 10403 | AI | 218 | R | NV | kVAh
| kVAh - Circuit 11 | 11 | 5692 | 5693 | 5010 | UINT32 | 10404 | 10405 | AI | 219 | R | NV | kVAh
| kVAh - Circuit 12 | 12 | 5694 | 5695 | 5011 | UINT32 | 10406 | 10407 | AI | 220 | R | NV | kVAh
| kVAh - Circuit 13 | 13 | 5696 | 5697 | 5012 | UINT32 | 10408 | 10409 | AI | 221 | R | NV | kVAh
| kVAh - Circuit 14 | 14 | 5698 | 5699 | 5013 | UINT32 | 10410 | 10411 | AI | 222 | R | NV | kVAh
| kVAh - Circuit 15 | 15 | 5700 | 5701 | 5014 | UINT32 | 10412 | 10413 | AI | 223 | R | NV | kVAh
| kVAh - Circuit 16 | 16 | 5702 | 5703 | 5015 | UINT32 | 10414 | 10415 | AI | 224 | R | NV | kVAh
| kVAh - Circuit 17 | 17 | 5704 | 5705 | 5016 | UINT32 | 10416 | 10417 | AI | 225 | R | NV | kVAh
| kVAh - Circuit 18 | 18 | 5706 | 5707 | 5017 | UINT32 | 10418 | 10419 | AI | 226 | R | NV | kVAh
| kVAh - Circuit 19 | 19 | 5708 | 5709 | 5018 | UINT32 | 10420 | 10421 | AI | 227 | R | NV | kVAh
| kVAh - Circuit 20 | 20 | 5710 | 5711 | 5019 | UINT32 | 10422 | 10423 | AI | 228 | R | NV | kVAh
| kVAh - Circuit 21 | 21 | 5712 | 5713 | 5020 | UINT32 | 10424 | 10425 | AI | 229 | R | NV | kVAh
| kVAh - Circuit 22 | 22 | 5714 | 5715 | 5021 | UINT32 | 10426 | 10427 | AI | 230 | R | NV | kVAh
| kVAh - Circuit 23 | 23 | 5716 | 5717 | 5022 | UINT32 | 10428 | 10429 | AI | 231 | R | NV | kVAh
| kVAh - Circuit 24 | 24 | 5718 | 5719 | 5023 | UINT32 | 10430 | 10431 | AI | 232 | R | NV | kVAh
| kVAh - Circuit 25 | 25 | 5720 | 5721 | 5024 | UINT32 | 10432 | 10433 | AI | 233 | R | NV | kVAh
| kVAh - Circuit 26 | 26 | 5722 | 5723 | 5025 | UINT32 | 10434 | 10435 | AI | 234 | R | NV | kVAh
| kVAh - Circuit 27 | 27 | 5724 | 5725 | 5026 | UINT32 | 10436 | 10437 | AI | 235 | R | NV | kVAh
| kVAh - Circuit 28 | 28 | 5726 | 5727 | 5027 | UINT32 | 10438 | 10439 | AI | 236 | R | NV | kVAh
| kVAh - Circuit 29 | 29 | 5728 | 5729 | 5028 | UINT32 | 10440 | 10441 | AI | 237 | R | NV | kVAh
| kVAh - Circuit 30 | 30 | 5730 | 5731 | 5029 | UINT32 | 10442 | 10443 | AI | 238 | R | NV | kVAh
| kVAh - Circuit 31 | 31 | 5732 | 5733 | 5030 | UINT32 | 10444 | 10445 | AI | 239 | R | NV | kVAh
| kVAh - Circuit 32 | 32 | 5734 | 5735 | 5031 | UINT32 | 10446 | 10447 | AI | 240 | R | NV | kVAh
| kVAh - Circuit 33 | 33 | 5736 | 5737 | 5032 | UINT32 | 10448 | 10449 | AI | 241 | R | NV | kVAh
| kVAh - Circuit 34 | 34 | 5738 | 5739 | 5033 | UINT32 | 10450 | 10451 | AI | 242 | R | NV | kVAh
| kVAh - Circuit 35 | 35 | 5740 | 5741 | 5034 | UINT32 | 10452 | 10453 | AI | 243 | R | NV | kVAh
| kVAh - Circuit 36 | 36 | 5742 | 5743 | 5035 | UINT32 | 10454 | 10455 | AI | 244 | R | NV | kVAh
| kVAh - Circuit 37 | 37 | 5744 | 5745 | 5036 | UINT32 | 10456 | 10457 | AI | 245 | R | NV | kVAh
| kVAh - Circuit 38 | 38 | 5746 | 5747 | 5037 | UINT32 | 10458 | 10459 | AI | 246 | R | NV | kVAh
| kVAh - Circuit 39 | 39 | 5748 | 5749 | 5038 | UINT32 | 10460 | 10461 | AI | 247 | R | NV | kVAh
| kVAh - Circuit 40 | 40 | 5750 | 5751 | 5039 | UINT32 | 10462 | 10463 | AI | 248 | R | NV | kVAh
| kVAh - Circuit 41 | 41 | 5752 | 5753 | 5040 | UINT32 | 10464 | 10465 | AI | 249 | R | NV | kVAh
| kVAh - Circuit 42 | 42 | 5754 | 5755 | 5041 | UINT32 | 10466 | 10467 | AI | 250 | R | NV | kVAh
| kVAh - Circuit 43 | 43 | 5756 | 5757 | 5042 | UINT32 | 10468 | 10469 | AI | 251 | R | NV | kVAh
| kVAh - Circuit 44 | 44 | 5758 | 5759 | 5043 | UINT32 | 10470 | 10471 | AI | 252 | R | NV | kVAh
| kVAh - Circuit 45 | 45 | 5760 | 5761 | 5044 | UINT32 | 10472 | 10473 | AI | 253 | R | NV | kVAh
| kVAh - Circuit 46 | 46 | 5762 | 5763 | 5045 | UINT32 | 10474 | 10475 | AI | 254 | R | NV | kVAh
| kVAh - Circuit 47 | 47 | 5764 | 5765 | 5046 | UINT32 | 10476 | 10477 | AI | 255 | R | NV | kVAh
| kVAh - Circuit 48 | 48 | 5766 | 5767 | 5047 | UINT32 | 10478 | 10479 | AI | 256 | R | NV | kVAh
| kVAh - Circuit 49 | 49 | 5768 | 5769 | 5048 | UINT32 | 10480 | 10481 | AI | 257 | R | NV | kVAh
| kVAh - Circuit 50 | 50 | 5770 | 5771 | 5049 | UINT32 | 10482 | 10483 | AI | 258 | R | NV | kVAh
| kVAh - Circuit 51 | 51 | 5772 | 5773 | 5050 | UINT32 | 10484 | 10485 | AI | 259 | R | NV | kVAh
| kVAh - Circuit 52 | 52 | 5774 | 5775 | 5051 | UINT32 | 10486 | 10487 | AI | 260 | R | NV | kVAh
| kVAh - Circuit 53 | 53 | 5776 | 5777 | 5052 | UINT32 | 10488 | 10489 | AI | 261 | R | NV | kVAh
| kVAh - Circuit 54 | 54 | 5778 | 5779 | 5053 | UINT32 | 10490 | 10491 | AI | 262 | R | NV | kVAh
| kVAh - Circuit 55 | 55 | 5780 | 5781 | 5054 | UINT32 | 10492 | 10493 | AI | 263 | R | NV | kVAh
| kVAh - Circuit 56 | 56 | 5782 | 5783 | 5055 | UINT32 | 10494 | 10495 | AI | 264 | R | NV | kVAh
| kVAh - Circuit 57 | 57 | 5784 | 5785 | 5056 | UINT32 | 10496 | 10497 | AI | 265 | R | NV | kVAh
| kVAh - Circuit 58 | 58 | 5786 | 5787 | 5057 | UINT32 | 10498 | 10499 | AI | 266 | R | NV | kVAh
| kVAh - Circuit 59 | 59 | 5788 | 5789 | 5058 | UINT32 | 10500 | 10501 | AI | 267 | R | NV | kVAh
| kVAh - Circuit 60 | 60 | 5790 | 5791 | 5059 | UINT32 | 10502 | 10503 | AI | 268 | R | NV | kVAh
| kVAh - Circuit 61 | 61 | 5792 | 5793 | 5060 | UINT32 | 10504 | 10505 | AI | 269 | R | NV | kVAh
| kVAh - Circuit 62 | 62 | 5794 | 5795 | 5061 | UINT32 | 10506 | 10507 | AI | 270 | R | NV | kVAh
| kVAh - Circuit 63 | 63 | 5796 | 5797 | 5062 | UINT32 | 10508 | 10509 | AI | 271 | R | NV | kVAh
| kVAh - Circuit 64 | 64 | 5798 | 5799 | 5063 | UINT32 | 10510 | 10511 | AI | 272 | R | NV | kVAh
| kVAh - Circuit 65 | 65 | 5800 | 5801 | 5064 | UINT32 | 10512 | 10513 | AI | 273 | R | NV | kVAh
| kVAh - Circuit 66 | 66 | 5802 | 5803 | 5065 | UINT32 | 10514 | 10515 | AI | 274 | R | NV | kVAh
| kVAh - Circuit 67 | 67 | 5804 | 5805 | 5066 | UINT32 | 10516 | 10517 | AI | 275 | R | NV | kVAh
| kVAh - Circuit 68 | 68 | 5806 | 5807 | 5067 | UINT32 | 10518 | 10519 | AI | 276 | R | NV | kVAh
| kVAh - Circuit 69 | 69 | 5808 | 5809 | 5068 | UINT32 | 10520 | 10521 | AI | 277 | R | NV | kVAh
| kVAh - Circuit 70 | 70 | 5810 | 5811 | 5069 | UINT32 | 10522 | 10523 | AI | 278 | R | NV | kVAh
| kVAh - Circuit 71 | 71 | 5812 | 5813 | 5070 | UINT32 | 10524 | 10525 | AI | 279 | R | NV | kVAh
| kVAh - Circuit 72 | 72 | 5814 | 5815 | 5071 | UINT32 | 10526 | 10527 | AI | 280 | R | NV | kVAh
| kVAh - Circuit 73 | 73 | 5816 | 5817 | 5072 | UINT32 | 10528 | 10529 | AI | 281 | R | NV | kVAh
| kVAh - Circuit 74 | 74 | 5818 | 5819 | 5073 | UINT32 | 10530 | 10531 | AI | 282 | R | NV | kVAh
| kVAh - Circuit 75 | 75 | 5820 | 5821 | 5074 | UINT32 | 10532 | 10533 | AI | 283 | R | NV | kVAh
| kVAh - Circuit 76 | 76 | 5822 | 5823 | 5075 | UINT32 | 10534 | 10535 | AI | 284 | R | NV | kVAh
| kVAh - Circuit 77 | 77 | 5824 | 5825 | 5076 | UINT32 | 10536 | 10537 | AI | 285 | R | NV | kVAh
| kVAh - Circuit 78 | 78 | 5826 | 5827 | 5077 | UINT32 | 10538 | 10539 | AI | 286 | R | NV | kVAh
| kVAh - Circuit 79 | 79 | 5828 | 5829 | 5078 | UINT32 | 10540 | 10541 | AI | 287 | R | NV | kVAh
| kVAh - Circuit 80 | 80 | 5830 | 5831 | 5079 | UINT32 | 10542 | 10543 | AI | 288 | R | NV | kVAh
| kVAh - Circuit 81 | 81 | 5832 | 5833 | 5080 | UINT32 | 10544 | 10545 | AI | 289 | R | NV | kVAh
| kVAh - Circuit 82 | 82 | 5834 | 5835 | 5081 | UINT32 | 10546 | 10547 | AI | 290 | R | NV | kVAh
| kVAh - Circuit 83 | 83 | 5836 | 5837 | 5082 | UINT32 | 10548 | 10549 | AI | 291 | R | NV | kVAh
| kVAh - Circuit 84 | 84 | 5838 | 5839 | 5083 | UINT32 | 10550 | 10551 | AI | 292 | R | NV | kVAh
| kVAh - Circuit 85 | 85 | 5840 | 5841 | 5084 | UINT32 | 10552 | 10553 | AI | 293 | R | NV | kVAh
| kVAh - Circuit 86 | 86 | 5842 | 5843 | 5085 | UINT32 | 10554 | 10555 | AI | 294 | R | NV | kVAh
| kVAh - Circuit 87 | 87 | 5844 | 5845 | 5086 | UINT32 | 10556 | 10557 | AI | 295 | R | NV | kVAh
| kVAh - Circuit 88 | 88 | 5846 | 5847 | 5087 | UINT32 | 10558 | 10559 | AI | 296 | R | NV | kVAh
| kVAh - Circuit 89 | 89 | 5848 | 5849 | 5088 | UINT32 | 10560 | 10561 | AI | 297 | R | NV | kVAh
| kVAh - Circuit 90 | 90 | 5850 | 5851 | 5089 | UINT32 | 10562 | 10563 | AI | 298 | R | NV | kVAh
| kVAh - Circuit 91 | 91 | 5852 | 5853 | 5090 | UINT32 | 10564 | 10565 | AI | 299 | R | NV | kVAh
| kVAh - Circuit 92 | 92 | 5854 | 5855 | 5091 | UINT32 | 10566 | 10567 | AI | 300 | R | NV | kVAh
| kVAh - Circuit 93 | 93 | 5856 | 5857 | 5092 | UINT32 | 10568 | 10569 | AI | 301 | R | NV | kVAh
| kVAh - Circuit 94 | 94 | 5858 | 5859 | 5093 | UINT32 | 10570 | 10571 | AI | 302 | R | NV | kVAh
| kVAh - Circuit 95 | 95 | 5860 | 5861 | 5094 | UINT32 | 10572 | 10573 | AI | 303 | R | NV | kVAh
| kVAh - Circuit 96 | 96 | 5862 | 5863 | 5095 | UINT32 | 10574 | 10575 | AI | 304 | R | NV | kVAh
| kW |  | 5864 | 5959 | Power | UINT16 | 10576 | 10767 | AI |  | R |  | kW
| kW - Circuit 1 | 1 | 5864 |  | 5096 | UINT16 | 10576 | 10577 | AI | 305 | R |  | kW
| kW - Circuit 2 | 2 | 5865 |  | 5097 | UINT16 | 10578 | 10579 | AI | 306 | R |  | kW
| kW - Circuit 3 | 3 | 5866 |  | 5098 | UINT16 | 10580 | 10581 | AI | 307 | R |  | kW
| kW - Circuit 4 | 4 | 5867 |  | 5099 | UINT16 | 10582 | 10583 | AI | 308 | R |  | kW
| kW - Circuit 5 | 5 | 5868 |  | 5100 | UINT16 | 10584 | 10585 | AI | 309 | R |  | kW
| kW - Circuit 6 | 6 | 5869 |  | 5101 | UINT16 | 10586 | 10587 | AI | 310 | R |  | kW
| kW - Circuit 7 | 7 | 5870 |  | 5102 | UINT16 | 10588 | 10589 | AI | 311 | R |  | kW
| kW - Circuit 8 | 8 | 5871 |  | 5103 | UINT16 | 10590 | 10591 | AI | 312 | R |  | kW
| kW - Circuit 9 | 9 | 5872 |  | 5104 | UINT16 | 10592 | 10593 | AI | 313 | R |  | kW
| kW - Circuit 10 | 10 | 5873 |  | 5105 | UINT16 | 10594 | 10595 | AI | 314 | R |  | kW
| kW - Circuit 11 | 11 | 5874 |  | 5106 | UINT16 | 10596 | 10597 | AI | 315 | R |  | kW
| kW - Circuit 12 | 12 | 5875 |  | 5107 | UINT16 | 10598 | 10599 | AI | 316 | R |  | kW
| kW - Circuit 13 | 13 | 5876 |  | 5108 | UINT16 | 10600 | 10601 | AI | 317 | R |  | kW
| kW - Circuit 14 | 14 | 5877 |  | 5109 | UINT16 | 10602 | 10603 | AI | 318 | R |  | kW
| kW - Circuit 15 | 15 | 5878 |  | 5110 | UINT16 | 10604 | 10605 | AI | 319 | R |  | kW
| kW - Circuit 16 | 16 | 5879 |  | 5111 | UINT16 | 10606 | 10607 | AI | 320 | R |  | kW
| kW - Circuit 17 | 17 | 5880 |  | 5112 | UINT16 | 10608 | 10609 | AI | 321 | R |  | kW
| kW - Circuit 18 | 18 | 5881 |  | 5113 | UINT16 | 10610 | 10611 | AI | 322 | R |  | kW
| kW - Circuit 19 | 19 | 5882 |  | 5114 | UINT16 | 10612 | 10613 | AI | 323 | R |  | kW
| kW - Circuit 20 | 20 | 5883 |  | 5115 | UINT16 | 10614 | 10615 | AI | 324 | R |  | kW
| kW - Circuit 21 | 21 | 5884 |  | 5116 | UINT16 | 10616 | 10617 | AI | 325 | R |  | kW
| kW - Circuit 22 | 22 | 5885 |  | 5117 | UINT16 | 10618 | 10619 | AI | 326 | R |  | kW
| kW - Circuit 23 | 23 | 5886 |  | 5118 | UINT16 | 10620 | 10621 | AI | 327 | R |  | kW
| kW - Circuit 24 | 24 | 5887 |  | 5119 | UINT16 | 10622 | 10623 | AI | 328 | R |  | kW
| kW - Circuit 25 | 25 | 5888 |  | 5120 | UINT16 | 10624 | 10625 | AI | 329 | R |  | kW
| kW - Circuit 26 | 26 | 5889 |  | 5121 | UINT16 | 10626 | 10627 | AI | 330 | R |  | kW
| kW - Circuit 27 | 27 | 5890 |  | 5122 | UINT16 | 10628 | 10629 | AI | 331 | R |  | kW
| kW - Circuit 28 | 28 | 5891 |  | 5123 | UINT16 | 10630 | 10631 | AI | 332 | R |  | kW
| kW - Circuit 29 | 29 | 5892 |  | 5124 | UINT16 | 10632 | 10633 | AI | 333 | R |  | kW
| kW - Circuit 30 | 30 | 5893 |  | 5125 | UINT16 | 10634 | 10635 | AI | 334 | R |  | kW
| kW - Circuit 31 | 31 | 5894 |  | 5126 | UINT16 | 10636 | 10637 | AI | 335 | R |  | kW
| kW - Circuit 32 | 32 | 5895 |  | 5127 | UINT16 | 10638 | 10639 | AI | 336 | R |  | kW
| kW - Circuit 33 | 33 | 5896 |  | 5128 | UINT16 | 10640 | 10641 | AI | 337 | R |  | kW
| kW - Circuit 34 | 34 | 5897 |  | 5129 | UINT16 | 10642 | 10643 | AI | 338 | R |  | kW
| kW - Circuit 35 | 35 | 5898 |  | 5130 | UINT16 | 10644 | 10645 | AI | 339 | R |  | kW
| kW - Circuit 36 | 36 | 5899 |  | 5131 | UINT16 | 10646 | 10647 | AI | 340 | R |  | kW
| kW - Circuit 37 | 37 | 5900 |  | 5132 | UINT16 | 10648 | 10649 | AI | 341 | R |  | kW
| kW - Circuit 38 | 38 | 5901 |  | 5133 | UINT16 | 10650 | 10651 | AI | 342 | R |  | kW
| kW - Circuit 39 | 39 | 5902 |  | 5134 | UINT16 | 10652 | 10653 | AI | 343 | R |  | kW
| kW - Circuit 40 | 40 | 5903 |  | 5135 | UINT16 | 10654 | 10655 | AI | 344 | R |  | kW
| kW - Circuit 41 | 41 | 5904 |  | 5136 | UINT16 | 10656 | 10657 | AI | 345 | R |  | kW
| kW - Circuit 42 | 42 | 5905 |  | 5137 | UINT16 | 10658 | 10659 | AI | 346 | R |  | kW
| kW - Circuit 43 | 43 | 5906 |  | 5138 | UINT16 | 10660 | 10661 | AI | 347 | R |  | kW
| kW - Circuit 44 | 44 | 5907 |  | 5139 | UINT16 | 10662 | 10663 | AI | 348 | R |  | kW
| kW - Circuit 45 | 45 | 5908 |  | 5140 | UINT16 | 10664 | 10665 | AI | 349 | R |  | kW
| kW - Circuit 46 | 46 | 5909 |  | 5141 | UINT16 | 10666 | 10667 | AI | 350 | R |  | kW
| kW - Circuit 47 | 47 | 5910 |  | 5142 | UINT16 | 10668 | 10669 | AI | 351 | R |  | kW
| kW - Circuit 48 | 48 | 5911 |  | 5143 | UINT16 | 10670 | 10671 | AI | 352 | R |  | kW
| kW - Circuit 49 | 49 | 5912 |  | 5144 | UINT16 | 10672 | 10673 | AI | 353 | R |  | kW
| kW - Circuit 50 | 50 | 5913 |  | 5145 | UINT16 | 10674 | 10675 | AI | 354 | R |  | kW
| kW - Circuit 51 | 51 | 5914 |  | 5146 | UINT16 | 10676 | 10677 | AI | 355 | R |  | kW
| kW - Circuit 52 | 52 | 5915 |  | 5147 | UINT16 | 10678 | 10679 | AI | 356 | R |  | kW
| kW - Circuit 53 | 53 | 5916 |  | 5148 | UINT16 | 10680 | 10681 | AI | 357 | R |  | kW
| kW - Circuit 54 | 54 | 5917 |  | 5149 | UINT16 | 10682 | 10683 | AI | 358 | R |  | kW
| kW - Circuit 55 | 55 | 5918 |  | 5150 | UINT16 | 10684 | 10685 | AI | 359 | R |  | kW
| kW - Circuit 56 | 56 | 5919 |  | 5151 | UINT16 | 10686 | 10687 | AI | 360 | R |  | kW
| kW - Circuit 57 | 57 | 5920 |  | 5152 | UINT16 | 10688 | 10689 | AI | 361 | R |  | kW
| kW - Circuit 58 | 58 | 5921 |  | 5153 | UINT16 | 10690 | 10691 | AI | 362 | R |  | kW
| kW - Circuit 59 | 59 | 5922 |  | 5154 | UINT16 | 10692 | 10693 | AI | 363 | R |  | kW
| kW - Circuit 60 | 60 | 5923 |  | 5155 | UINT16 | 10694 | 10695 | AI | 364 | R |  | kW
| kW - Circuit 61 | 61 | 5924 |  | 5156 | UINT16 | 10696 | 10697 | AI | 365 | R |  | kW
| kW - Circuit 62 | 62 | 5925 |  | 5157 | UINT16 | 10698 | 10699 | AI | 366 | R |  | kW
| kW - Circuit 63 | 63 | 5926 |  | 5158 | UINT16 | 10700 | 10701 | AI | 367 | R |  | kW
| kW - Circuit 64 | 64 | 5927 |  | 5159 | UINT16 | 10702 | 10703 | AI | 368 | R |  | kW
| kW - Circuit 65 | 65 | 5928 |  | 5160 | UINT16 | 10704 | 10705 | AI | 369 | R |  | kW
| kW - Circuit 66 | 66 | 5929 |  | 5161 | UINT16 | 10706 | 10707 | AI | 370 | R |  | kW
| kW - Circuit 67 | 67 | 5930 |  | 5162 | UINT16 | 10708 | 10709 | AI | 371 | R |  | kW
| kW - Circuit 68 | 68 | 5931 |  | 5163 | UINT16 | 10710 | 10711 | AI | 372 | R |  | kW
| kW - Circuit 69 | 69 | 5932 |  | 5164 | UINT16 | 10712 | 10713 | AI | 373 | R |  | kW
| kW - Circuit 70 | 70 | 5933 |  | 5165 | UINT16 | 10714 | 10715 | AI | 374 | R |  | kW
| kW - Circuit 71 | 71 | 5934 |  | 5166 | UINT16 | 10716 | 10717 | AI | 375 | R |  | kW
| kW - Circuit 72 | 72 | 5935 |  | 5167 | UINT16 | 10718 | 10719 | AI | 376 | R |  | kW
| kW - Circuit 73 | 73 | 5936 |  | 5168 | UINT16 | 10720 | 10721 | AI | 377 | R |  | kW
| kW - Circuit 74 | 74 | 5937 |  | 5169 | UINT16 | 10722 | 10723 | AI | 378 | R |  | kW
| kW - Circuit 75 | 75 | 5938 |  | 5170 | UINT16 | 10724 | 10725 | AI | 379 | R |  | kW
| kW - Circuit 76 | 76 | 5939 |  | 5171 | UINT16 | 10726 | 10727 | AI | 380 | R |  | kW
| kW - Circuit 77 | 77 | 5940 |  | 5172 | UINT16 | 10728 | 10729 | AI | 381 | R |  | kW
| kW - Circuit 78 | 78 | 5941 |  | 5173 | UINT16 | 10730 | 10731 | AI | 382 | R |  | kW
| kW - Circuit 79 | 79 | 5942 |  | 5174 | UINT16 | 10732 | 10733 | AI | 383 | R |  | kW
| kW - Circuit 80 | 80 | 5943 |  | 5175 | UINT16 | 10734 | 10735 | AI | 384 | R |  | kW
| kW - Circuit 81 | 81 | 5944 |  | 5176 | UINT16 | 10736 | 10737 | AI | 385 | R |  | kW
| kW - Circuit 82 | 82 | 5945 |  | 5177 | UINT16 | 10738 | 10739 | AI | 386 | R |  | kW
| kW - Circuit 83 | 83 | 5946 |  | 5178 | UINT16 | 10740 | 10741 | AI | 387 | R |  | kW
| kW - Circuit 84 | 84 | 5947 |  | 5179 | UINT16 | 10742 | 10743 | AI | 388 | R |  | kW
| kW - Circuit 85 | 85 | 5948 |  | 5180 | UINT16 | 10744 | 10745 | AI | 389 | R |  | kW
| kW - Circuit 86 | 86 | 5949 |  | 5181 | UINT16 | 10746 | 10747 | AI | 390 | R |  | kW
| kW - Circuit 87 | 87 | 5950 |  | 5182 | UINT16 | 10748 | 10749 | AI | 391 | R |  | kW
| kW - Circuit 88 | 88 | 5951 |  | 5183 | UINT16 | 10750 | 10751 | AI | 392 | R |  | kW
| kW - Circuit 89 | 89 | 5952 |  | 5184 | UINT16 | 10752 | 10753 | AI | 393 | R |  | kW
| kW - Circuit 90 | 90 | 5953 |  | 5185 | UINT16 | 10754 | 10755 | AI | 394 | R |  | kW
| kW - Circuit 91 | 91 | 5954 |  | 5186 | UINT16 | 10756 | 10757 | AI | 395 | R |  | kW
| kW - Circuit 92 | 92 | 5955 |  | 5187 | UINT16 | 10758 | 10759 | AI | 396 | R |  | kW
| kW - Circuit 93 | 93 | 5956 |  | 5188 | UINT16 | 10760 | 10761 | AI | 397 | R |  | kW
| kW - Circuit 94 | 94 | 5957 |  | 5189 | UINT16 | 10762 | 10763 | AI | 398 | R |  | kW
| kW - Circuit 95 | 95 | 5958 |  | 5190 | UINT16 | 10764 | 10765 | AI | 399 | R |  | kW
| kW - Circuit 96 | 96 | 5959 |  | 5191 | UINT16 | 10766 | 10767 | AI | 400 | R |  | kW
| kVAR |  | 5960 | 6055 | Power | UINT16 | 10768 | 10959 | AI |  | R |  | kVAR
| kVAR - Circuit 1 | 1 | 5960 |  | 5096 | UINT16 | 10768 | 10769 | AI | 401 | R |  | kVAR
| kVAR - Circuit 2 | 2 | 5961 |  | 5097 | UINT16 | 10770 | 10771 | AI | 402 | R |  | kVAR
| kVAR - Circuit 3 | 3 | 5962 |  | 5098 | UINT16 | 10772 | 10773 | AI | 403 | R |  | kVAR
| kVAR - Circuit 4 | 4 | 5963 |  | 5099 | UINT16 | 10774 | 10775 | AI | 404 | R |  | kVAR
| kVAR - Circuit 5 | 5 | 5964 |  | 5100 | UINT16 | 10776 | 10777 | AI | 405 | R |  | kVAR
| kVAR - Circuit 6 | 6 | 5965 |  | 5101 | UINT16 | 10778 | 10779 | AI | 406 | R |  | kVAR
| kVAR - Circuit 7 | 7 | 5966 |  | 5102 | UINT16 | 10780 | 10781 | AI | 407 | R |  | kVAR
| kVAR - Circuit 8 | 8 | 5967 |  | 5103 | UINT16 | 10782 | 10783 | AI | 408 | R |  | kVAR
| kVAR - Circuit 9 | 9 | 5968 |  | 5104 | UINT16 | 10784 | 10785 | AI | 409 | R |  | kVAR
| kVAR - Circuit 10 | 10 | 5969 |  | 5105 | UINT16 | 10786 | 10787 | AI | 410 | R |  | kVAR
| kVAR - Circuit 11 | 11 | 5970 |  | 5106 | UINT16 | 10788 | 10789 | AI | 411 | R |  | kVAR
| kVAR - Circuit 12 | 12 | 5971 |  | 5107 | UINT16 | 10790 | 10791 | AI | 412 | R |  | kVAR
| kVAR - Circuit 13 | 13 | 5972 |  | 5108 | UINT16 | 10792 | 10793 | AI | 413 | R |  | kVAR
| kVAR - Circuit 14 | 14 | 5973 |  | 5109 | UINT16 | 10794 | 10795 | AI | 414 | R |  | kVAR
| kVAR - Circuit 15 | 15 | 5974 |  | 5110 | UINT16 | 10796 | 10797 | AI | 415 | R |  | kVAR
| kVAR - Circuit 16 | 16 | 5975 |  | 5111 | UINT16 | 10798 | 10799 | AI | 416 | R |  | kVAR
| kVAR - Circuit 17 | 17 | 5976 |  | 5112 | UINT16 | 10800 | 10801 | AI | 417 | R |  | kVAR
| kVAR - Circuit 18 | 18 | 5977 |  | 5113 | UINT16 | 10802 | 10803 | AI | 418 | R |  | kVAR
| kVAR - Circuit 19 | 19 | 5978 |  | 5114 | UINT16 | 10804 | 10805 | AI | 419 | R |  | kVAR
| kVAR - Circuit 20 | 20 | 5979 |  | 5115 | UINT16 | 10806 | 10807 | AI | 420 | R |  | kVAR
| kVAR - Circuit 21 | 21 | 5980 |  | 5116 | UINT16 | 10808 | 10809 | AI | 421 | R |  | kVAR
| kVAR - Circuit 22 | 22 | 5981 |  | 5117 | UINT16 | 10810 | 10811 | AI | 422 | R |  | kVAR
| kVAR - Circuit 23 | 23 | 5982 |  | 5118 | UINT16 | 10812 | 10813 | AI | 423 | R |  | kVAR
| kVAR - Circuit 24 | 24 | 5983 |  | 5119 | UINT16 | 10814 | 10815 | AI | 424 | R |  | kVAR
| kVAR - Circuit 25 | 25 | 5984 |  | 5120 | UINT16 | 10816 | 10817 | AI | 425 | R |  | kVAR
| kVAR - Circuit 26 | 26 | 5985 |  | 5121 | UINT16 | 10818 | 10819 | AI | 426 | R |  | kVAR
| kVAR - Circuit 27 | 27 | 5986 |  | 5122 | UINT16 | 10820 | 10821 | AI | 427 | R |  | kVAR
| kVAR - Circuit 28 | 28 | 5987 |  | 5123 | UINT16 | 10822 | 10823 | AI | 428 | R |  | kVAR
| kVAR - Circuit 29 | 29 | 5988 |  | 5124 | UINT16 | 10824 | 10825 | AI | 429 | R |  | kVAR
| kVAR - Circuit 30 | 30 | 5989 |  | 5125 | UINT16 | 10826 | 10827 | AI | 430 | R |  | kVAR
| kVAR - Circuit 31 | 31 | 5990 |  | 5126 | UINT16 | 10828 | 10829 | AI | 431 | R |  | kVAR
| kVAR - Circuit 32 | 32 | 5991 |  | 5127 | UINT16 | 10830 | 10831 | AI | 432 | R |  | kVAR
| kVAR - Circuit 33 | 33 | 5992 |  | 5128 | UINT16 | 10832 | 10833 | AI | 433 | R |  | kVAR
| kVAR - Circuit 34 | 34 | 5993 |  | 5129 | UINT16 | 10834 | 10835 | AI | 434 | R |  | kVAR
| kVAR - Circuit 35 | 35 | 5994 |  | 5130 | UINT16 | 10836 | 10837 | AI | 435 | R |  | kVAR
| kVAR - Circuit 36 | 36 | 5995 |  | 5131 | UINT16 | 10838 | 10839 | AI | 436 | R |  | kVAR
| kVAR - Circuit 37 | 37 | 5996 |  | 5132 | UINT16 | 10840 | 10841 | AI | 437 | R |  | kVAR
| kVAR - Circuit 38 | 38 | 5997 |  | 5133 | UINT16 | 10842 | 10843 | AI | 438 | R |  | kVAR
| kVAR - Circuit 39 | 39 | 5998 |  | 5134 | UINT16 | 10844 | 10845 | AI | 439 | R |  | kVAR
| kVAR - Circuit 40 | 40 | 5999 |  | 5135 | UINT16 | 10846 | 10847 | AI | 440 | R |  | kVAR
| kVAR - Circuit 41 | 41 | 6000 |  | 5136 | UINT16 | 10848 | 10849 | AI | 441 | R |  | kVAR
| kVAR - Circuit 42 | 42 | 6001 |  | 5137 | UINT16 | 10850 | 10851 | AI | 442 | R |  | kVAR
| kVAR - Circuit 43 | 43 | 6002 |  | 5138 | UINT16 | 10852 | 10853 | AI | 443 | R |  | kVAR
| kVAR - Circuit 44 | 44 | 6003 |  | 5139 | UINT16 | 10854 | 10855 | AI | 444 | R |  | kVAR
| kVAR - Circuit 45 | 45 | 6004 |  | 5140 | UINT16 | 10856 | 10857 | AI | 445 | R |  | kVAR
| kVAR - Circuit 46 | 46 | 6005 |  | 5141 | UINT16 | 10858 | 10859 | AI | 446 | R |  | kVAR
| kVAR - Circuit 47 | 47 | 6006 |  | 5142 | UINT16 | 10860 | 10861 | AI | 447 | R |  | kVAR
| kVAR - Circuit 48 | 48 | 6007 |  | 5143 | UINT16 | 10862 | 10863 | AI | 448 | R |  | kVAR
| kVAR - Circuit 49 | 49 | 6008 |  | 5144 | UINT16 | 10864 | 10865 | AI | 449 | R |  | kVAR
| kVAR - Circuit 50 | 50 | 6009 |  | 5145 | UINT16 | 10866 | 10867 | AI | 450 | R |  | kVAR
| kVAR - Circuit 51 | 51 | 6010 |  | 5146 | UINT16 | 10868 | 10869 | AI | 451 | R |  | kVAR
| kVAR - Circuit 52 | 52 | 6011 |  | 5147 | UINT16 | 10870 | 10871 | AI | 452 | R |  | kVAR
| kVAR - Circuit 53 | 53 | 6012 |  | 5148 | UINT16 | 10872 | 10873 | AI | 453 | R |  | kVAR
| kVAR - Circuit 54 | 54 | 6013 |  | 5149 | UINT16 | 10874 | 10875 | AI | 454 | R |  | kVAR
| kVAR - Circuit 55 | 55 | 6014 |  | 5150 | UINT16 | 10876 | 10877 | AI | 455 | R |  | kVAR
| kVAR - Circuit 56 | 56 | 6015 |  | 5151 | UINT16 | 10878 | 10879 | AI | 456 | R |  | kVAR
| kVAR - Circuit 57 | 57 | 6016 |  | 5152 | UINT16 | 10880 | 10881 | AI | 457 | R |  | kVAR
| kVAR - Circuit 58 | 58 | 6017 |  | 5153 | UINT16 | 10882 | 10883 | AI | 458 | R |  | kVAR
| kVAR - Circuit 59 | 59 | 6018 |  | 5154 | UINT16 | 10884 | 10885 | AI | 459 | R |  | kVAR
| kVAR - Circuit 60 | 60 | 6019 |  | 5155 | UINT16 | 10886 | 10887 | AI | 460 | R |  | kVAR
| kVAR - Circuit 61 | 61 | 6020 |  | 5156 | UINT16 | 10888 | 10889 | AI | 461 | R |  | kVAR
| kVAR - Circuit 62 | 62 | 6021 |  | 5157 | UINT16 | 10890 | 10891 | AI | 462 | R |  | kVAR
| kVAR - Circuit 63 | 63 | 6022 |  | 5158 | UINT16 | 10892 | 10893 | AI | 463 | R |  | kVAR
| kVAR - Circuit 64 | 64 | 6023 |  | 5159 | UINT16 | 10894 | 10895 | AI | 464 | R |  | kVAR
| kVAR - Circuit 65 | 65 | 6024 |  | 5160 | UINT16 | 10896 | 10897 | AI | 465 | R |  | kVAR
| kVAR - Circuit 66 | 66 | 6025 |  | 5161 | UINT16 | 10898 | 10899 | AI | 466 | R |  | kVAR
| kVAR - Circuit 67 | 67 | 6026 |  | 5162 | UINT16 | 10900 | 10901 | AI | 467 | R |  | kVAR
| kVAR - Circuit 68 | 68 | 6027 |  | 5163 | UINT16 | 10902 | 10903 | AI | 468 | R |  | kVAR
| kVAR - Circuit 69 | 69 | 6028 |  | 5164 | UINT16 | 10904 | 10905 | AI | 469 | R |  | kVAR
| kVAR - Circuit 70 | 70 | 6029 |  | 5165 | UINT16 | 10906 | 10907 | AI | 470 | R |  | kVAR
| kVAR - Circuit 71 | 71 | 6030 |  | 5166 | UINT16 | 10908 | 10909 | AI | 471 | R |  | kVAR
| kVAR - Circuit 72 | 72 | 6031 |  | 5167 | UINT16 | 10910 | 10911 | AI | 472 | R |  | kVAR
| kVAR - Circuit 73 | 73 | 6032 |  | 5168 | UINT16 | 10912 | 10913 | AI | 473 | R |  | kVAR
| kVAR - Circuit 74 | 74 | 6033 |  | 5169 | UINT16 | 10914 | 10915 | AI | 474 | R |  | kVAR
| kVAR - Circuit 75 | 75 | 6034 |  | 5170 | UINT16 | 10916 | 10917 | AI | 475 | R |  | kVAR
| kVAR - Circuit 76 | 76 | 6035 |  | 5171 | UINT16 | 10918 | 10919 | AI | 476 | R |  | kVAR
| kVAR - Circuit 77 | 77 | 6036 |  | 5172 | UINT16 | 10920 | 10921 | AI | 477 | R |  | kVAR
| kVAR - Circuit 78 | 78 | 6037 |  | 5173 | UINT16 | 10922 | 10923 | AI | 478 | R |  | kVAR
| kVAR - Circuit 79 | 79 | 6038 |  | 5174 | UINT16 | 10924 | 10925 | AI | 479 | R |  | kVAR
| kVAR - Circuit 80 | 80 | 6039 |  | 5175 | UINT16 | 10926 | 10927 | AI | 480 | R |  | kVAR
| kVAR - Circuit 81 | 81 | 6040 |  | 5176 | UINT16 | 10928 | 10929 | AI | 481 | R |  | kVAR
| kVAR - Circuit 82 | 82 | 6041 |  | 5177 | UINT16 | 10930 | 10931 | AI | 482 | R |  | kVAR
| kVAR - Circuit 83 | 83 | 6042 |  | 5178 | UINT16 | 10932 | 10933 | AI | 483 | R |  | kVAR
| kVAR - Circuit 84 | 84 | 6043 |  | 5179 | UINT16 | 10934 | 10935 | AI | 484 | R |  | kVAR
| kVAR - Circuit 85 | 85 | 6044 |  | 5180 | UINT16 | 10936 | 10937 | AI | 485 | R |  | kVAR
| kVAR - Circuit 86 | 86 | 6045 |  | 5181 | UINT16 | 10938 | 10939 | AI | 486 | R |  | kVAR
| kVAR - Circuit 87 | 87 | 6046 |  | 5182 | UINT16 | 10940 | 10941 | AI | 487 | R |  | kVAR
| kVAR - Circuit 88 | 88 | 6047 |  | 5183 | UINT16 | 10942 | 10943 | AI | 488 | R |  | kVAR
| kVAR - Circuit 89 | 89 | 6048 |  | 5184 | UINT16 | 10944 | 10945 | AI | 489 | R |  | kVAR
| kVAR - Circuit 90 | 90 | 6049 |  | 5185 | UINT16 | 10946 | 10947 | AI | 490 | R |  | kVAR
| kVAR - Circuit 91 | 91 | 6050 |  | 5186 | UINT16 | 10948 | 10949 | AI | 491 | R |  | kVAR
| kVAR - Circuit 92 | 92 | 6051 |  | 5187 | UINT16 | 10950 | 10951 | AI | 492 | R |  | kVAR
| kVAR - Circuit 93 | 93 | 6052 |  | 5188 | UINT16 | 10952 | 10953 | AI | 493 | R |  | kVAR
| kVAR - Circuit 94 | 94 | 6053 |  | 5189 | UINT16 | 10954 | 10955 | AI | 494 | R |  | kVAR
| kVAR - Circuit 95 | 95 | 6054 |  | 5190 | UINT16 | 10956 | 10957 | AI | 495 | R |  | kVAR
| kVAR - Circuit 96 | 96 | 6055 |  | 5191 | UINT16 | 10958 | 10959 | AI | 496 | R |  | kVAR
| kVA |  | 6056 | 6151 | Power | UINT16 | 10960 | 11151 | AI |  | R |  | kVA
| kVA - Circuit 1 | 1 | 6056 |  | 5096 | UINT16 | 10960 | 10961 | AI | 497 | R |  | kVA
| kVA - Circuit 2 | 2 | 6057 |  | 5097 | UINT16 | 10962 | 10963 | AI | 498 | R |  | kVA
| kVA - Circuit 3 | 3 | 6058 |  | 5098 | UINT16 | 10964 | 10965 | AI | 499 | R |  | kVA
| kVA - Circuit 4 | 4 | 6059 |  | 5099 | UINT16 | 10966 | 10967 | AI | 500 | R |  | kVA
| kVA - Circuit 5 | 5 | 6060 |  | 5100 | UINT16 | 10968 | 10969 | AI | 501 | R |  | kVA
| kVA - Circuit 6 | 6 | 6061 |  | 5101 | UINT16 | 10970 | 10971 | AI | 502 | R |  | kVA
| kVA - Circuit 7 | 7 | 6062 |  | 5102 | UINT16 | 10972 | 10973 | AI | 503 | R |  | kVA
| kVA - Circuit 8 | 8 | 6063 |  | 5103 | UINT16 | 10974 | 10975 | AI | 504 | R |  | kVA
| kVA - Circuit 9 | 9 | 6064 |  | 5104 | UINT16 | 10976 | 10977 | AI | 505 | R |  | kVA
| kVA - Circuit 10 | 10 | 6065 |  | 5105 | UINT16 | 10978 | 10979 | AI | 506 | R |  | kVA
| kVA - Circuit 11 | 11 | 6066 |  | 5106 | UINT16 | 10980 | 10981 | AI | 507 | R |  | kVA
| kVA - Circuit 12 | 12 | 6067 |  | 5107 | UINT16 | 10982 | 10983 | AI | 508 | R |  | kVA
| kVA - Circuit 13 | 13 | 6068 |  | 5108 | UINT16 | 10984 | 10985 | AI | 509 | R |  | kVA
| kVA - Circuit 14 | 14 | 6069 |  | 5109 | UINT16 | 10986 | 10987 | AI | 510 | R |  | kVA
| kVA - Circuit 15 | 15 | 6070 |  | 5110 | UINT16 | 10988 | 10989 | AI | 511 | R |  | kVA
| kVA - Circuit 16 | 16 | 6071 |  | 5111 | UINT16 | 10990 | 10991 | AI | 512 | R |  | kVA
| kVA - Circuit 17 | 17 | 6072 |  | 5112 | UINT16 | 10992 | 10993 | AI | 513 | R |  | kVA
| kVA - Circuit 18 | 18 | 6073 |  | 5113 | UINT16 | 10994 | 10995 | AI | 514 | R |  | kVA
| kVA - Circuit 19 | 19 | 6074 |  | 5114 | UINT16 | 10996 | 10997 | AI | 515 | R |  | kVA
| kVA - Circuit 20 | 20 | 6075 |  | 5115 | UINT16 | 10998 | 10999 | AI | 516 | R |  | kVA
| kVA - Circuit 21 | 21 | 6076 |  | 5116 | UINT16 | 11000 | 11001 | AI | 517 | R |  | kVA
| kVA - Circuit 22 | 22 | 6077 |  | 5117 | UINT16 | 11002 | 11003 | AI | 518 | R |  | kVA
| kVA - Circuit 23 | 23 | 6078 |  | 5118 | UINT16 | 11004 | 11005 | AI | 519 | R |  | kVA
| kVA - Circuit 24 | 24 | 6079 |  | 5119 | UINT16 | 11006 | 11007 | AI | 520 | R |  | kVA
| kVA - Circuit 25 | 25 | 6080 |  | 5120 | UINT16 | 11008 | 11009 | AI | 521 | R |  | kVA
| kVA - Circuit 26 | 26 | 6081 |  | 5121 | UINT16 | 11010 | 11011 | AI | 522 | R |  | kVA
| kVA - Circuit 27 | 27 | 6082 |  | 5122 | UINT16 | 11012 | 11013 | AI | 523 | R |  | kVA
| kVA - Circuit 28 | 28 | 6083 |  | 5123 | UINT16 | 11014 | 11015 | AI | 524 | R |  | kVA
| kVA - Circuit 29 | 29 | 6084 |  | 5124 | UINT16 | 11016 | 11017 | AI | 525 | R |  | kVA
| kVA - Circuit 30 | 30 | 6085 |  | 5125 | UINT16 | 11018 | 11019 | AI | 526 | R |  | kVA
| kVA - Circuit 31 | 31 | 6086 |  | 5126 | UINT16 | 11020 | 11021 | AI | 527 | R |  | kVA
| kVA - Circuit 32 | 32 | 6087 |  | 5127 | UINT16 | 11022 | 11023 | AI | 528 | R |  | kVA
| kVA - Circuit 33 | 33 | 6088 |  | 5128 | UINT16 | 11024 | 11025 | AI | 529 | R |  | kVA
| kVA - Circuit 34 | 34 | 6089 |  | 5129 | UINT16 | 11026 | 11027 | AI | 530 | R |  | kVA
| kVA - Circuit 35 | 35 | 6090 |  | 5130 | UINT16 | 11028 | 11029 | AI | 531 | R |  | kVA
| kVA - Circuit 36 | 36 | 6091 |  | 5131 | UINT16 | 11030 | 11031 | AI | 532 | R |  | kVA
| kVA - Circuit 37 | 37 | 6092 |  | 5132 | UINT16 | 11032 | 11033 | AI | 533 | R |  | kVA
| kVA - Circuit 38 | 38 | 6093 |  | 5133 | UINT16 | 11034 | 11035 | AI | 534 | R |  | kVA
| kVA - Circuit 39 | 39 | 6094 |  | 5134 | UINT16 | 11036 | 11037 | AI | 535 | R |  | kVA
| kVA - Circuit 40 | 40 | 6095 |  | 5135 | UINT16 | 11038 | 11039 | AI | 536 | R |  | kVA
| kVA - Circuit 41 | 41 | 6096 |  | 5136 | UINT16 | 11040 | 11041 | AI | 537 | R |  | kVA
| kVA - Circuit 42 | 42 | 6097 |  | 5137 | UINT16 | 11042 | 11043 | AI | 538 | R |  | kVA
| kVA - Circuit 43 | 43 | 6098 |  | 5138 | UINT16 | 11044 | 11045 | AI | 539 | R |  | kVA
| kVA - Circuit 44 | 44 | 6099 |  | 5139 | UINT16 | 11046 | 11047 | AI | 540 | R |  | kVA
| kVA - Circuit 45 | 45 | 6100 |  | 5140 | UINT16 | 11048 | 11049 | AI | 541 | R |  | kVA
| kVA - Circuit 46 | 46 | 6101 |  | 5141 | UINT16 | 11050 | 11051 | AI | 542 | R |  | kVA
| kVA - Circuit 47 | 47 | 6102 |  | 5142 | UINT16 | 11052 | 11053 | AI | 543 | R |  | kVA
| kVA - Circuit 48 | 48 | 6103 |  | 5143 | UINT16 | 11054 | 11055 | AI | 544 | R |  | kVA
| kVA - Circuit 49 | 49 | 6104 |  | 5144 | UINT16 | 11056 | 11057 | AI | 545 | R |  | kVA
| kVA - Circuit 50 | 50 | 6105 |  | 5145 | UINT16 | 11058 | 11059 | AI | 546 | R |  | kVA
| kVA - Circuit 51 | 51 | 6106 |  | 5146 | UINT16 | 11060 | 11061 | AI | 547 | R |  | kVA
| kVA - Circuit 52 | 52 | 6107 |  | 5147 | UINT16 | 11062 | 11063 | AI | 548 | R |  | kVA
| kVA - Circuit 53 | 53 | 6108 |  | 5148 | UINT16 | 11064 | 11065 | AI | 549 | R |  | kVA
| kVA - Circuit 54 | 54 | 6109 |  | 5149 | UINT16 | 11066 | 11067 | AI | 550 | R |  | kVA
| kVA - Circuit 55 | 55 | 6110 |  | 5150 | UINT16 | 11068 | 11069 | AI | 551 | R |  | kVA
| kVA - Circuit 56 | 56 | 6111 |  | 5151 | UINT16 | 11070 | 11071 | AI | 552 | R |  | kVA
| kVA - Circuit 57 | 57 | 6112 |  | 5152 | UINT16 | 11072 | 11073 | AI | 553 | R |  | kVA
| kVA - Circuit 58 | 58 | 6113 |  | 5153 | UINT16 | 11074 | 11075 | AI | 554 | R |  | kVA
| kVA - Circuit 59 | 59 | 6114 |  | 5154 | UINT16 | 11076 | 11077 | AI | 555 | R |  | kVA
| kVA - Circuit 60 | 60 | 6115 |  | 5155 | UINT16 | 11078 | 11079 | AI | 556 | R |  | kVA
| kVA - Circuit 61 | 61 | 6116 |  | 5156 | UINT16 | 11080 | 11081 | AI | 557 | R |  | kVA
| kVA - Circuit 62 | 62 | 6117 |  | 5157 | UINT16 | 11082 | 11083 | AI | 558 | R |  | kVA
| kVA - Circuit 63 | 63 | 6118 |  | 5158 | UINT16 | 11084 | 11085 | AI | 559 | R |  | kVA
| kVA - Circuit 64 | 64 | 6119 |  | 5159 | UINT16 | 11086 | 11087 | AI | 560 | R |  | kVA
| kVA - Circuit 65 | 65 | 6120 |  | 5160 | UINT16 | 11088 | 11089 | AI | 561 | R |  | kVA
| kVA - Circuit 66 | 66 | 6121 |  | 5161 | UINT16 | 11090 | 11091 | AI | 562 | R |  | kVA
| kVA - Circuit 67 | 67 | 6122 |  | 5162 | UINT16 | 11092 | 11093 | AI | 563 | R |  | kVA
| kVA - Circuit 68 | 68 | 6123 |  | 5163 | UINT16 | 11094 | 11095 | AI | 564 | R |  | kVA
| kVA - Circuit 69 | 69 | 6124 |  | 5164 | UINT16 | 11096 | 11097 | AI | 565 | R |  | kVA
| kVA - Circuit 70 | 70 | 6125 |  | 5165 | UINT16 | 11098 | 11099 | AI | 566 | R |  | kVA
| kVA - Circuit 71 | 71 | 6126 |  | 5166 | UINT16 | 11100 | 11101 | AI | 567 | R |  | kVA
| kVA - Circuit 72 | 72 | 6127 |  | 5167 | UINT16 | 11102 | 11103 | AI | 568 | R |  | kVA
| kVA - Circuit 73 | 73 | 6128 |  | 5168 | UINT16 | 11104 | 11105 | AI | 569 | R |  | kVA
| kVA - Circuit 74 | 74 | 6129 |  | 5169 | UINT16 | 11106 | 11107 | AI | 570 | R |  | kVA
| kVA - Circuit 75 | 75 | 6130 |  | 5170 | UINT16 | 11108 | 11109 | AI | 571 | R |  | kVA
| kVA - Circuit 76 | 76 | 6131 |  | 5171 | UINT16 | 11110 | 11111 | AI | 572 | R |  | kVA
| kVA - Circuit 77 | 77 | 6132 |  | 5172 | UINT16 | 11112 | 11113 | AI | 573 | R |  | kVA
| kVA - Circuit 78 | 78 | 6133 |  | 5173 | UINT16 | 11114 | 11115 | AI | 574 | R |  | kVA
| kVA - Circuit 79 | 79 | 6134 |  | 5174 | UINT16 | 11116 | 11117 | AI | 575 | R |  | kVA
| kVA - Circuit 80 | 80 | 6135 |  | 5175 | UINT16 | 11118 | 11119 | AI | 576 | R |  | kVA
| kVA - Circuit 81 | 81 | 6136 |  | 5176 | UINT16 | 11120 | 11121 | AI | 577 | R |  | kVA
| kVA - Circuit 82 | 82 | 6137 |  | 5177 | UINT16 | 11122 | 11123 | AI | 578 | R |  | kVA
| kVA - Circuit 83 | 83 | 6138 |  | 5178 | UINT16 | 11124 | 11125 | AI | 579 | R |  | kVA
| kVA - Circuit 84 | 84 | 6139 |  | 5179 | UINT16 | 11126 | 11127 | AI | 580 | R |  | kVA
| kVA - Circuit 85 | 85 | 6140 |  | 5180 | UINT16 | 11128 | 11129 | AI | 581 | R |  | kVA
| kVA - Circuit 86 | 86 | 6141 |  | 5181 | UINT16 | 11130 | 11131 | AI | 582 | R |  | kVA
| kVA - Circuit 87 | 87 | 6142 |  | 5182 | UINT16 | 11132 | 11133 | AI | 583 | R |  | kVA
| kVA - Circuit 88 | 88 | 6143 |  | 5183 | UINT16 | 11134 | 11135 | AI | 584 | R |  | kVA
| kVA - Circuit 89 | 89 | 6144 |  | 5184 | UINT16 | 11136 | 11137 | AI | 585 | R |  | kVA
| kVA - Circuit 90 | 90 | 6145 |  | 5185 | UINT16 | 11138 | 11139 | AI | 586 | R |  | kVA
| kVA - Circuit 91 | 91 | 6146 |  | 5186 | UINT16 | 11140 | 11141 | AI | 587 | R |  | kVA
| kVA - Circuit 92 | 92 | 6147 |  | 5187 | UINT16 | 11142 | 11143 | AI | 588 | R |  | kVA
| kVA - Circuit 93 | 93 | 6148 |  | 5188 | UINT16 | 11144 | 11145 | AI | 589 | R |  | kVA
| kVA - Circuit 94 | 94 | 6149 |  | 5189 | UINT16 | 11146 | 11147 | AI | 590 | R |  | kVA
| kVA - Circuit 95 | 95 | 6150 |  | 5190 | UINT16 | 11148 | 11149 | AI | 591 | R |  | kVA
| kVA - Circuit 96 | 96 | 6151 |  | 5191 | UINT16 | 11150 | 11151 | AI | 592 | R |  | kVA
| Current |  | 6152 | 6247 | Current | UINT16 | 11152 | 11343 | AI |  | R |  | Amps
| Current - Circuit 1 | 1 | 6152 |  | 5192 | UINT16 | 11152 | 11153 | AI | 593 | R |  | Amps
| Current - Circuit 2 | 2 | 6153 |  | 5193 | UINT16 | 11154 | 11155 | AI | 594 | R |  | Amps
| Current - Circuit 3 | 3 | 6154 |  | 5194 | UINT16 | 11156 | 11157 | AI | 595 | R |  | Amps
| Current - Circuit 4 | 4 | 6155 |  | 5195 | UINT16 | 11158 | 11159 | AI | 596 | R |  | Amps
| Current - Circuit 5 | 5 | 6156 |  | 5196 | UINT16 | 11160 | 11161 | AI | 597 | R |  | Amps
| Current - Circuit 6 | 6 | 6157 |  | 5197 | UINT16 | 11162 | 11163 | AI | 598 | R |  | Amps
| Current - Circuit 7 | 7 | 6158 |  | 5198 | UINT16 | 11164 | 11165 | AI | 599 | R |  | Amps
| Current - Circuit 8 | 8 | 6159 |  | 5199 | UINT16 | 11166 | 11167 | AI | 600 | R |  | Amps
| Current - Circuit 9 | 9 | 6160 |  | 5200 | UINT16 | 11168 | 11169 | AI | 601 | R |  | Amps
| Current - Circuit 10 | 10 | 6161 |  | 5201 | UINT16 | 11170 | 11171 | AI | 602 | R |  | Amps
| Current - Circuit 11 | 11 | 6162 |  | 5202 | UINT16 | 11172 | 11173 | AI | 603 | R |  | Amps
| Current - Circuit 12 | 12 | 6163 |  | 5203 | UINT16 | 11174 | 11175 | AI | 604 | R |  | Amps
| Current - Circuit 13 | 13 | 6164 |  | 5204 | UINT16 | 11176 | 11177 | AI | 605 | R |  | Amps
| Current - Circuit 14 | 14 | 6165 |  | 5205 | UINT16 | 11178 | 11179 | AI | 606 | R |  | Amps
| Current - Circuit 15 | 15 | 6166 |  | 5206 | UINT16 | 11180 | 11181 | AI | 607 | R |  | Amps
| Current - Circuit 16 | 16 | 6167 |  | 5207 | UINT16 | 11182 | 11183 | AI | 608 | R |  | Amps
| Current - Circuit 17 | 17 | 6168 |  | 5208 | UINT16 | 11184 | 11185 | AI | 609 | R |  | Amps
| Current - Circuit 18 | 18 | 6169 |  | 5209 | UINT16 | 11186 | 11187 | AI | 610 | R |  | Amps
| Current - Circuit 19 | 19 | 6170 |  | 5210 | UINT16 | 11188 | 11189 | AI | 611 | R |  | Amps
| Current - Circuit 20 | 20 | 6171 |  | 5211 | UINT16 | 11190 | 11191 | AI | 612 | R |  | Amps
| Current - Circuit 21 | 21 | 6172 |  | 5212 | UINT16 | 11192 | 11193 | AI | 613 | R |  | Amps
| Current - Circuit 22 | 22 | 6173 |  | 5213 | UINT16 | 11194 | 11195 | AI | 614 | R |  | Amps
| Current - Circuit 23 | 23 | 6174 |  | 5214 | UINT16 | 11196 | 11197 | AI | 615 | R |  | Amps
| Current - Circuit 24 | 24 | 6175 |  | 5215 | UINT16 | 11198 | 11199 | AI | 616 | R |  | Amps
| Current - Circuit 25 | 25 | 6176 |  | 5216 | UINT16 | 11200 | 11201 | AI | 617 | R |  | Amps
| Current - Circuit 26 | 26 | 6177 |  | 5217 | UINT16 | 11202 | 11203 | AI | 618 | R |  | Amps
| Current - Circuit 27 | 27 | 6178 |  | 5218 | UINT16 | 11204 | 11205 | AI | 619 | R |  | Amps
| Current - Circuit 28 | 28 | 6179 |  | 5219 | UINT16 | 11206 | 11207 | AI | 620 | R |  | Amps
| Current - Circuit 29 | 29 | 6180 |  | 5220 | UINT16 | 11208 | 11209 | AI | 621 | R |  | Amps
| Current - Circuit 30 | 30 | 6181 |  | 5221 | UINT16 | 11210 | 11211 | AI | 622 | R |  | Amps
| Current - Circuit 31 | 31 | 6182 |  | 5222 | UINT16 | 11212 | 11213 | AI | 623 | R |  | Amps
| Current - Circuit 32 | 32 | 6183 |  | 5223 | UINT16 | 11214 | 11215 | AI | 624 | R |  | Amps
| Current - Circuit 33 | 33 | 6184 |  | 5224 | UINT16 | 11216 | 11217 | AI | 625 | R |  | Amps
| Current - Circuit 34 | 34 | 6185 |  | 5225 | UINT16 | 11218 | 11219 | AI | 626 | R |  | Amps
| Current - Circuit 35 | 35 | 6186 |  | 5226 | UINT16 | 11220 | 11221 | AI | 627 | R |  | Amps
| Current - Circuit 36 | 36 | 6187 |  | 5227 | UINT16 | 11222 | 11223 | AI | 628 | R |  | Amps
| Current - Circuit 37 | 37 | 6188 |  | 5228 | UINT16 | 11224 | 11225 | AI | 629 | R |  | Amps
| Current - Circuit 38 | 38 | 6189 |  | 5229 | UINT16 | 11226 | 11227 | AI | 630 | R |  | Amps
| Current - Circuit 39 | 39 | 6190 |  | 5230 | UINT16 | 11228 | 11229 | AI | 631 | R |  | Amps
| Current - Circuit 40 | 40 | 6191 |  | 5231 | UINT16 | 11230 | 11231 | AI | 632 | R |  | Amps
| Current - Circuit 41 | 41 | 6192 |  | 5232 | UINT16 | 11232 | 11233 | AI | 633 | R |  | Amps
| Current - Circuit 42 | 42 | 6193 |  | 5233 | UINT16 | 11234 | 11235 | AI | 634 | R |  | Amps
| Current - Circuit 43 | 43 | 6194 |  | 5234 | UINT16 | 11236 | 11237 | AI | 635 | R |  | Amps
| Current - Circuit 44 | 44 | 6195 |  | 5235 | UINT16 | 11238 | 11239 | AI | 636 | R |  | Amps
| Current - Circuit 45 | 45 | 6196 |  | 5236 | UINT16 | 11240 | 11241 | AI | 637 | R |  | Amps
| Current - Circuit 46 | 46 | 6197 |  | 5237 | UINT16 | 11242 | 11243 | AI | 638 | R |  | Amps
| Current - Circuit 47 | 47 | 6198 |  | 5238 | UINT16 | 11244 | 11245 | AI | 639 | R |  | Amps
| Current - Circuit 48 | 48 | 6199 |  | 5239 | UINT16 | 11246 | 11247 | AI | 640 | R |  | Amps
| Current - Circuit 49 | 49 | 6200 |  | 5240 | UINT16 | 11248 | 11249 | AI | 641 | R |  | Amps
| Current - Circuit 50 | 50 | 6201 |  | 5241 | UINT16 | 11250 | 11251 | AI | 642 | R |  | Amps
| Current - Circuit 51 | 51 | 6202 |  | 5242 | UINT16 | 11252 | 11253 | AI | 643 | R |  | Amps
| Current - Circuit 52 | 52 | 6203 |  | 5243 | UINT16 | 11254 | 11255 | AI | 644 | R |  | Amps
| Current - Circuit 53 | 53 | 6204 |  | 5244 | UINT16 | 11256 | 11257 | AI | 645 | R |  | Amps
| Current - Circuit 54 | 54 | 6205 |  | 5245 | UINT16 | 11258 | 11259 | AI | 646 | R |  | Amps
| Current - Circuit 55 | 55 | 6206 |  | 5246 | UINT16 | 11260 | 11261 | AI | 647 | R |  | Amps
| Current - Circuit 56 | 56 | 6207 |  | 5247 | UINT16 | 11262 | 11263 | AI | 648 | R |  | Amps
| Current - Circuit 57 | 57 | 6208 |  | 5248 | UINT16 | 11264 | 11265 | AI | 649 | R |  | Amps
| Current - Circuit 58 | 58 | 6209 |  | 5249 | UINT16 | 11266 | 11267 | AI | 650 | R |  | Amps
| Current - Circuit 59 | 59 | 6210 |  | 5250 | UINT16 | 11268 | 11269 | AI | 651 | R |  | Amps
| Current - Circuit 60 | 60 | 6211 |  | 5251 | UINT16 | 11270 | 11271 | AI | 652 | R |  | Amps
| Current - Circuit 61 | 61 | 6212 |  | 5252 | UINT16 | 11272 | 11273 | AI | 653 | R |  | Amps
| Current - Circuit 62 | 62 | 6213 |  | 5253 | UINT16 | 11274 | 11275 | AI | 654 | R |  | Amps
| Current - Circuit 63 | 63 | 6214 |  | 5254 | UINT16 | 11276 | 11277 | AI | 655 | R |  | Amps
| Current - Circuit 64 | 64 | 6215 |  | 5255 | UINT16 | 11278 | 11279 | AI | 656 | R |  | Amps
| Current - Circuit 65 | 65 | 6216 |  | 5256 | UINT16 | 11280 | 11281 | AI | 657 | R |  | Amps
| Current - Circuit 66 | 66 | 6217 |  | 5257 | UINT16 | 11282 | 11283 | AI | 658 | R |  | Amps
| Current - Circuit 67 | 67 | 6218 |  | 5258 | UINT16 | 11284 | 11285 | AI | 659 | R |  | Amps
| Current - Circuit 68 | 68 | 6219 |  | 5259 | UINT16 | 11286 | 11287 | AI | 660 | R |  | Amps
| Current - Circuit 69 | 69 | 6220 |  | 5260 | UINT16 | 11288 | 11289 | AI | 661 | R |  | Amps
| Current - Circuit 70 | 70 | 6221 |  | 5261 | UINT16 | 11290 | 11291 | AI | 662 | R |  | Amps
| Current - Circuit 71 | 71 | 6222 |  | 5262 | UINT16 | 11292 | 11293 | AI | 663 | R |  | Amps
| Current - Circuit 72 | 72 | 6223 |  | 5263 | UINT16 | 11294 | 11295 | AI | 664 | R |  | Amps
| Current - Circuit 73 | 73 | 6224 |  | 5264 | UINT16 | 11296 | 11297 | AI | 665 | R |  | Amps
| Current - Circuit 74 | 74 | 6225 |  | 5265 | UINT16 | 11298 | 11299 | AI | 666 | R |  | Amps
| Current - Circuit 75 | 75 | 6226 |  | 5266 | UINT16 | 11300 | 11301 | AI | 667 | R |  | Amps
| Current - Circuit 76 | 76 | 6227 |  | 5267 | UINT16 | 11302 | 11303 | AI | 668 | R |  | Amps
| Current - Circuit 77 | 77 | 6228 |  | 5268 | UINT16 | 11304 | 11305 | AI | 669 | R |  | Amps
| Current - Circuit 78 | 78 | 6229 |  | 5269 | UINT16 | 11306 | 11307 | AI | 670 | R |  | Amps
| Current - Circuit 79 | 79 | 6230 |  | 5270 | UINT16 | 11308 | 11309 | AI | 671 | R |  | Amps
| Current - Circuit 80 | 80 | 6231 |  | 5271 | UINT16 | 11310 | 11311 | AI | 672 | R |  | Amps
| Current - Circuit 81 | 81 | 6232 |  | 5272 | UINT16 | 11312 | 11313 | AI | 673 | R |  | Amps
| Current - Circuit 82 | 82 | 6233 |  | 5273 | UINT16 | 11314 | 11315 | AI | 674 | R |  | Amps
| Current - Circuit 83 | 83 | 6234 |  | 5274 | UINT16 | 11316 | 11317 | AI | 675 | R |  | Amps
| Current - Circuit 84 | 84 | 6235 |  | 5275 | UINT16 | 11318 | 11319 | AI | 676 | R |  | Amps
| Current - Circuit 85 | 85 | 6236 |  | 5276 | UINT16 | 11320 | 11321 | AI | 677 | R |  | Amps
| Current - Circuit 86 | 86 | 6237 |  | 5277 | UINT16 | 11322 | 11323 | AI | 678 | R |  | Amps
| Current - Circuit 87 | 87 | 6238 |  | 5278 | UINT16 | 11324 | 11325 | AI | 679 | R |  | Amps
| Current - Circuit 88 | 88 | 6239 |  | 5279 | UINT16 | 11326 | 11327 | AI | 680 | R |  | Amps
| Current - Circuit 89 | 89 | 6240 |  | 5280 | UINT16 | 11328 | 11329 | AI | 681 | R |  | Amps
| Current - Circuit 90 | 90 | 6241 |  | 5281 | UINT16 | 11330 | 11331 | AI | 682 | R |  | Amps
| Current - Circuit 91 | 91 | 6242 |  | 5282 | UINT16 | 11332 | 11333 | AI | 683 | R |  | Amps
| Current - Circuit 92 | 92 | 6243 |  | 5283 | UINT16 | 11334 | 11335 | AI | 684 | R |  | Amps
| Current - Circuit 93 | 93 | 6244 |  | 5284 | UINT16 | 11336 | 11337 | AI | 685 | R |  | Amps
| Current - Circuit 94 | 94 | 6245 |  | 5285 | UINT16 | 11338 | 11339 | AI | 686 | R |  | Amps
| Current - Circuit 95 | 95 | 6246 |  | 5286 | UINT16 | 11340 | 11341 | AI | 687 | R |  | Amps
| Current - Circuit 96 | 96 | 6247 |  | 5287 | UINT16 | 11342 | 11343 | AI | 688 | R |  | Amps
| Power Factor |  | 6248 | 6343 | -3 | INT16 | 11344 | 11535 | AI |  | R
| Power Factor - Circuit 1 | 1 | 6248 |  | -3 | INT16 | 11344 | 11345 | AI | 689 | R
| Power Factor - Circuit 2 | 2 | 6249 |  | -3 | INT16 | 11346 | 11347 | AI | 690 | R
| Power Factor - Circuit 3 | 3 | 6250 |  | -3 | INT16 | 11348 | 11349 | AI | 691 | R
| Power Factor - Circuit 4 | 4 | 6251 |  | -3 | INT16 | 11350 | 11351 | AI | 692 | R
| Power Factor - Circuit 5 | 5 | 6252 |  | -3 | INT16 | 11352 | 11353 | AI | 693 | R
| Power Factor - Circuit 6 | 6 | 6253 |  | -3 | INT16 | 11354 | 11355 | AI | 694 | R
| Power Factor - Circuit 7 | 7 | 6254 |  | -3 | INT16 | 11356 | 11357 | AI | 695 | R
| Power Factor - Circuit 8 | 8 | 6255 |  | -3 | INT16 | 11358 | 11359 | AI | 696 | R
| Power Factor - Circuit 9 | 9 | 6256 |  | -3 | INT16 | 11360 | 11361 | AI | 697 | R
| Power Factor - Circuit 10 | 10 | 6257 |  | -3 | INT16 | 11362 | 11363 | AI | 698 | R
| Power Factor - Circuit 11 | 11 | 6258 |  | -3 | INT16 | 11364 | 11365 | AI | 699 | R
| Power Factor - Circuit 12 | 12 | 6259 |  | -3 | INT16 | 11366 | 11367 | AI | 700 | R
| Power Factor - Circuit 13 | 13 | 6260 |  | -3 | INT16 | 11368 | 11369 | AI | 701 | R
| Power Factor - Circuit 14 | 14 | 6261 |  | -3 | INT16 | 11370 | 11371 | AI | 702 | R
| Power Factor - Circuit 15 | 15 | 6262 |  | -3 | INT16 | 11372 | 11373 | AI | 703 | R
| Power Factor - Circuit 16 | 16 | 6263 |  | -3 | INT16 | 11374 | 11375 | AI | 704 | R
| Power Factor - Circuit 17 | 17 | 6264 |  | -3 | INT16 | 11376 | 11377 | AI | 705 | R
| Power Factor - Circuit 18 | 18 | 6265 |  | -3 | INT16 | 11378 | 11379 | AI | 706 | R
| Power Factor - Circuit 19 | 19 | 6266 |  | -3 | INT16 | 11380 | 11381 | AI | 707 | R
| Power Factor - Circuit 20 | 20 | 6267 |  | -3 | INT16 | 11382 | 11383 | AI | 708 | R
| Power Factor - Circuit 21 | 21 | 6268 |  | -3 | INT16 | 11384 | 11385 | AI | 709 | R
| Power Factor - Circuit 22 | 22 | 6269 |  | -3 | INT16 | 11386 | 11387 | AI | 710 | R
| Power Factor - Circuit 23 | 23 | 6270 |  | -3 | INT16 | 11388 | 11389 | AI | 711 | R
| Power Factor - Circuit 24 | 24 | 6271 |  | -3 | INT16 | 11390 | 11391 | AI | 712 | R
| Power Factor - Circuit 25 | 25 | 6272 |  | -3 | INT16 | 11392 | 11393 | AI | 713 | R
| Power Factor - Circuit 26 | 26 | 6273 |  | -3 | INT16 | 11394 | 11395 | AI | 714 | R
| Power Factor - Circuit 27 | 27 | 6274 |  | -3 | INT16 | 11396 | 11397 | AI | 715 | R
| Power Factor - Circuit 28 | 28 | 6275 |  | -3 | INT16 | 11398 | 11399 | AI | 716 | R
| Power Factor - Circuit 29 | 29 | 6276 |  | -3 | INT16 | 11400 | 11401 | AI | 717 | R
| Power Factor - Circuit 30 | 30 | 6277 |  | -3 | INT16 | 11402 | 11403 | AI | 718 | R
| Power Factor - Circuit 31 | 31 | 6278 |  | -3 | INT16 | 11404 | 11405 | AI | 719 | R
| Power Factor - Circuit 32 | 32 | 6279 |  | -3 | INT16 | 11406 | 11407 | AI | 720 | R
| Power Factor - Circuit 33 | 33 | 6280 |  | -3 | INT16 | 11408 | 11409 | AI | 721 | R
| Power Factor - Circuit 34 | 34 | 6281 |  | -3 | INT16 | 11410 | 11411 | AI | 722 | R
| Power Factor - Circuit 35 | 35 | 6282 |  | -3 | INT16 | 11412 | 11413 | AI | 723 | R
| Power Factor - Circuit 36 | 36 | 6283 |  | -3 | INT16 | 11414 | 11415 | AI | 724 | R
| Power Factor - Circuit 37 | 37 | 6284 |  | -3 | INT16 | 11416 | 11417 | AI | 725 | R
| Power Factor - Circuit 38 | 38 | 6285 |  | -3 | INT16 | 11418 | 11419 | AI | 726 | R
| Power Factor - Circuit 39 | 39 | 6286 |  | -3 | INT16 | 11420 | 11421 | AI | 727 | R
| Power Factor - Circuit 40 | 40 | 6287 |  | -3 | INT16 | 11422 | 11423 | AI | 728 | R
| Power Factor - Circuit 41 | 41 | 6288 |  | -3 | INT16 | 11424 | 11425 | AI | 729 | R
| Power Factor - Circuit 42 | 42 | 6289 |  | -3 | INT16 | 11426 | 11427 | AI | 730 | R
| Power Factor - Circuit 43 | 43 | 6290 |  | -3 | INT16 | 11428 | 11429 | AI | 731 | R
| Power Factor - Circuit 44 | 44 | 6291 |  | -3 | INT16 | 11430 | 11431 | AI | 732 | R
| Power Factor - Circuit 45 | 45 | 6292 |  | -3 | INT16 | 11432 | 11433 | AI | 733 | R
| Power Factor - Circuit 46 | 46 | 6293 |  | -3 | INT16 | 11434 | 11435 | AI | 734 | R
| Power Factor - Circuit 47 | 47 | 6294 |  | -3 | INT16 | 11436 | 11437 | AI | 735 | R
| Power Factor - Circuit 48 | 48 | 6295 |  | -3 | INT16 | 11438 | 11439 | AI | 736 | R
| Power Factor - Circuit 49 | 49 | 6296 |  | -3 | INT16 | 11440 | 11441 | AI | 737 | R
| Power Factor - Circuit 50 | 50 | 6297 |  | -3 | INT16 | 11442 | 11443 | AI | 738 | R
| Power Factor - Circuit 51 | 51 | 6298 |  | -3 | INT16 | 11444 | 11445 | AI | 739 | R
| Power Factor - Circuit 52 | 52 | 6299 |  | -3 | INT16 | 11446 | 11447 | AI | 740 | R
| Power Factor - Circuit 53 | 53 | 6300 |  | -3 | INT16 | 11448 | 11449 | AI | 741 | R
| Power Factor - Circuit 54 | 54 | 6301 |  | -3 | INT16 | 11450 | 11451 | AI | 742 | R
| Power Factor - Circuit 55 | 55 | 6302 |  | -3 | INT16 | 11452 | 11453 | AI | 743 | R
| Power Factor - Circuit 56 | 56 | 6303 |  | -3 | INT16 | 11454 | 11455 | AI | 744 | R
| Power Factor - Circuit 57 | 57 | 6304 |  | -3 | INT16 | 11456 | 11457 | AI | 745 | R
| Power Factor - Circuit 58 | 58 | 6305 |  | -3 | INT16 | 11458 | 11459 | AI | 746 | R
| Power Factor - Circuit 59 | 59 | 6306 |  | -3 | INT16 | 11460 | 11461 | AI | 747 | R
| Power Factor - Circuit 60 | 60 | 6307 |  | -3 | INT16 | 11462 | 11463 | AI | 748 | R
| Power Factor - Circuit 61 | 61 | 6308 |  | -3 | INT16 | 11464 | 11465 | AI | 749 | R
| Power Factor - Circuit 62 | 62 | 6309 |  | -3 | INT16 | 11466 | 11467 | AI | 750 | R
| Power Factor - Circuit 63 | 63 | 6310 |  | -3 | INT16 | 11468 | 11469 | AI | 751 | R
| Power Factor - Circuit 64 | 64 | 6311 |  | -3 | INT16 | 11470 | 11471 | AI | 752 | R
| Power Factor - Circuit 65 | 65 | 6312 |  | -3 | INT16 | 11472 | 11473 | AI | 753 | R
| Power Factor - Circuit 66 | 66 | 6313 |  | -3 | INT16 | 11474 | 11475 | AI | 754 | R
| Power Factor - Circuit 67 | 67 | 6314 |  | -3 | INT16 | 11476 | 11477 | AI | 755 | R
| Power Factor - Circuit 68 | 68 | 6315 |  | -3 | INT16 | 11478 | 11479 | AI | 756 | R
| Power Factor - Circuit 69 | 69 | 6316 |  | -3 | INT16 | 11480 | 11481 | AI | 757 | R
| Power Factor - Circuit 70 | 70 | 6317 |  | -3 | INT16 | 11482 | 11483 | AI | 758 | R
| Power Factor - Circuit 71 | 71 | 6318 |  | -3 | INT16 | 11484 | 11485 | AI | 759 | R
| Power Factor - Circuit 72 | 72 | 6319 |  | -3 | INT16 | 11486 | 11487 | AI | 760 | R
| Power Factor - Circuit 73 | 73 | 6320 |  | -3 | INT16 | 11488 | 11489 | AI | 761 | R
| Power Factor - Circuit 74 | 74 | 6321 |  | -3 | INT16 | 11490 | 11491 | AI | 762 | R
| Power Factor - Circuit 75 | 75 | 6322 |  | -3 | INT16 | 11492 | 11493 | AI | 763 | R
| Power Factor - Circuit 76 | 76 | 6323 |  | -3 | INT16 | 11494 | 11495 | AI | 764 | R
| Power Factor - Circuit 77 | 77 | 6324 |  | -3 | INT16 | 11496 | 11497 | AI | 765 | R
| Power Factor - Circuit 78 | 78 | 6325 |  | -3 | INT16 | 11498 | 11499 | AI | 766 | R
| Power Factor - Circuit 79 | 79 | 6326 |  | -3 | INT16 | 11500 | 11501 | AI | 767 | R
| Power Factor - Circuit 80 | 80 | 6327 |  | -3 | INT16 | 11502 | 11503 | AI | 768 | R
| Power Factor - Circuit 81 | 81 | 6328 |  | -3 | INT16 | 11504 | 11505 | AI | 769 | R
| Power Factor - Circuit 82 | 82 | 6329 |  | -3 | INT16 | 11506 | 11507 | AI | 770 | R
| Power Factor - Circuit 83 | 83 | 6330 |  | -3 | INT16 | 11508 | 11509 | AI | 771 | R
| Power Factor - Circuit 84 | 84 | 6331 |  | -3 | INT16 | 11510 | 11511 | AI | 772 | R
| Power Factor - Circuit 85 | 85 | 6332 |  | -3 | INT16 | 11512 | 11513 | AI | 773 | R
| Power Factor - Circuit 86 | 86 | 6333 |  | -3 | INT16 | 11514 | 11515 | AI | 774 | R
| Power Factor - Circuit 87 | 87 | 6334 |  | -3 | INT16 | 11516 | 11517 | AI | 775 | R
| Power Factor - Circuit 88 | 88 | 6335 |  | -3 | INT16 | 11518 | 11519 | AI | 776 | R
| Power Factor - Circuit 89 | 89 | 6336 |  | -3 | INT16 | 11520 | 11521 | AI | 777 | R
| Power Factor - Circuit 90 | 90 | 6337 |  | -3 | INT16 | 11522 | 11523 | AI | 778 | R
| Power Factor - Circuit 91 | 91 | 6338 |  | -3 | INT16 | 11524 | 11525 | AI | 779 | R
| Power Factor - Circuit 92 | 92 | 6339 |  | -3 | INT16 | 11526 | 11527 | AI | 780 | R
| Power Factor - Circuit 93 | 93 | 6340 |  | -3 | INT16 | 11528 | 11529 | AI | 781 | R
| Power Factor - Circuit 94 | 94 | 6341 |  | -3 | INT16 | 11530 | 11531 | AI | 782 | R
| Power Factor - Circuit 95 | 95 | 6342 |  | -3 | INT16 | 11532 | 11533 | AI | 783 | R
| Power Factor - Circuit 96 | 96 | 6343 |  | -3 | INT16 | 11534 | 11535 | AI | 784 | R
| Current Angle |  | 6344 | 6439 | -1 | INT16 | 11536 | 11727 | AI |  | R |  | Degrees
| Current Angle- Circuit 1 | 1 | 6344 |  | -1 | INT16 | 11536 | 11537 | AI | 785 | R |  | Degrees
| Current Angle- Circuit 2 | 2 | 6345 |  | -1 | INT16 | 11538 | 11539 | AI | 786 | R |  | Degrees
| Current Angle- Circuit 3 | 3 | 6346 |  | -1 | INT16 | 11540 | 11541 | AI | 787 | R |  | Degrees
| Current Angle- Circuit 4 | 4 | 6347 |  | -1 | INT16 | 11542 | 11543 | AI | 788 | R |  | Degrees
| Current Angle- Circuit 5 | 5 | 6348 |  | -1 | INT16 | 11544 | 11545 | AI | 789 | R |  | Degrees
| Current Angle- Circuit 6 | 6 | 6349 |  | -1 | INT16 | 11546 | 11547 | AI | 790 | R |  | Degrees
| Current Angle- Circuit 7 | 7 | 6350 |  | -1 | INT16 | 11548 | 11549 | AI | 791 | R |  | Degrees
| Current Angle- Circuit 8 | 8 | 6351 |  | -1 | INT16 | 11550 | 11551 | AI | 792 | R |  | Degrees
| Current Angle- Circuit 9 | 9 | 6352 |  | -1 | INT16 | 11552 | 11553 | AI | 793 | R |  | Degrees
| Current Angle- Circuit 10 | 10 | 6353 |  | -1 | INT16 | 11554 | 11555 | AI | 794 | R |  | Degrees
| Current Angle- Circuit 11 | 11 | 6354 |  | -1 | INT16 | 11556 | 11557 | AI | 795 | R |  | Degrees
| Current Angle- Circuit 12 | 12 | 6355 |  | -1 | INT16 | 11558 | 11559 | AI | 796 | R |  | Degrees
| Current Angle- Circuit 13 | 13 | 6356 |  | -1 | INT16 | 11560 | 11561 | AI | 797 | R |  | Degrees
| Current Angle- Circuit 14 | 14 | 6357 |  | -1 | INT16 | 11562 | 11563 | AI | 798 | R |  | Degrees
| Current Angle- Circuit 15 | 15 | 6358 |  | -1 | INT16 | 11564 | 11565 | AI | 799 | R |  | Degrees
| Current Angle- Circuit 16 | 16 | 6359 |  | -1 | INT16 | 11566 | 11567 | AI | 800 | R |  | Degrees
| Current Angle- Circuit 17 | 17 | 6360 |  | -1 | INT16 | 11568 | 11569 | AI | 801 | R |  | Degrees
| Current Angle- Circuit 18 | 18 | 6361 |  | -1 | INT16 | 11570 | 11571 | AI | 802 | R |  | Degrees
| Current Angle- Circuit 19 | 19 | 6362 |  | -1 | INT16 | 11572 | 11573 | AI | 803 | R |  | Degrees
| Current Angle- Circuit 20 | 20 | 6363 |  | -1 | INT16 | 11574 | 11575 | AI | 804 | R |  | Degrees
| Current Angle- Circuit 21 | 21 | 6364 |  | -1 | INT16 | 11576 | 11577 | AI | 805 | R |  | Degrees
| Current Angle- Circuit 22 | 22 | 6365 |  | -1 | INT16 | 11578 | 11579 | AI | 806 | R |  | Degrees
| Current Angle- Circuit 23 | 23 | 6366 |  | -1 | INT16 | 11580 | 11581 | AI | 807 | R |  | Degrees
| Current Angle- Circuit 24 | 24 | 6367 |  | -1 | INT16 | 11582 | 11583 | AI | 808 | R |  | Degrees
| Current Angle- Circuit 25 | 25 | 6368 |  | -1 | INT16 | 11584 | 11585 | AI | 809 | R |  | Degrees
| Current Angle- Circuit 26 | 26 | 6369 |  | -1 | INT16 | 11586 | 11587 | AI | 810 | R |  | Degrees
| Current Angle- Circuit 27 | 27 | 6370 |  | -1 | INT16 | 11588 | 11589 | AI | 811 | R |  | Degrees
| Current Angle- Circuit 28 | 28 | 6371 |  | -1 | INT16 | 11590 | 11591 | AI | 812 | R |  | Degrees
| Current Angle- Circuit 29 | 29 | 6372 |  | -1 | INT16 | 11592 | 11593 | AI | 813 | R |  | Degrees
| Current Angle- Circuit 30 | 30 | 6373 |  | -1 | INT16 | 11594 | 11595 | AI | 814 | R |  | Degrees
| Current Angle- Circuit 31 | 31 | 6374 |  | -1 | INT16 | 11596 | 11597 | AI | 815 | R |  | Degrees
| Current Angle- Circuit 32 | 32 | 6375 |  | -1 | INT16 | 11598 | 11599 | AI | 816 | R |  | Degrees
| Current Angle- Circuit 33 | 33 | 6376 |  | -1 | INT16 | 11600 | 11601 | AI | 817 | R |  | Degrees
| Current Angle- Circuit 34 | 34 | 6377 |  | -1 | INT16 | 11602 | 11603 | AI | 818 | R |  | Degrees
| Current Angle- Circuit 35 | 35 | 6378 |  | -1 | INT16 | 11604 | 11605 | AI | 819 | R |  | Degrees
| Current Angle- Circuit 36 | 36 | 6379 |  | -1 | INT16 | 11606 | 11607 | AI | 820 | R |  | Degrees
| Current Angle- Circuit 37 | 37 | 6380 |  | -1 | INT16 | 11608 | 11609 | AI | 821 | R |  | Degrees
| Current Angle- Circuit 38 | 38 | 6381 |  | -1 | INT16 | 11610 | 11611 | AI | 822 | R |  | Degrees
| Current Angle- Circuit 39 | 39 | 6382 |  | -1 | INT16 | 11612 | 11613 | AI | 823 | R |  | Degrees
| Current Angle- Circuit 40 | 40 | 6383 |  | -1 | INT16 | 11614 | 11615 | AI | 824 | R |  | Degrees
| Current Angle- Circuit 41 | 41 | 6384 |  | -1 | INT16 | 11616 | 11617 | AI | 825 | R |  | Degrees
| Current Angle- Circuit 42 | 42 | 6385 |  | -1 | INT16 | 11618 | 11619 | AI | 826 | R |  | Degrees
| Current Angle- Circuit 43 | 43 | 6386 |  | -1 | INT16 | 11620 | 11621 | AI | 827 | R |  | Degrees
| Current Angle- Circuit 44 | 44 | 6387 |  | -1 | INT16 | 11622 | 11623 | AI | 828 | R |  | Degrees
| Current Angle- Circuit 45 | 45 | 6388 |  | -1 | INT16 | 11624 | 11625 | AI | 829 | R |  | Degrees
| Current Angle- Circuit 46 | 46 | 6389 |  | -1 | INT16 | 11626 | 11627 | AI | 830 | R |  | Degrees
| Current Angle- Circuit 47 | 47 | 6390 |  | -1 | INT16 | 11628 | 11629 | AI | 831 | R |  | Degrees
| Current Angle- Circuit 48 | 48 | 6391 |  | -1 | INT16 | 11630 | 11631 | AI | 832 | R |  | Degrees
| Current Angle- Circuit 49 | 49 | 6392 |  | -1 | INT16 | 11632 | 11633 | AI | 833 | R |  | Degrees
| Current Angle- Circuit 50 | 50 | 6393 |  | -1 | INT16 | 11634 | 11635 | AI | 834 | R |  | Degrees
| Current Angle- Circuit 51 | 51 | 6394 |  | -1 | INT16 | 11636 | 11637 | AI | 835 | R |  | Degrees
| Current Angle- Circuit 52 | 52 | 6395 |  | -1 | INT16 | 11638 | 11639 | AI | 836 | R |  | Degrees
| Current Angle- Circuit 53 | 53 | 6396 |  | -1 | INT16 | 11640 | 11641 | AI | 837 | R |  | Degrees
| Current Angle- Circuit 54 | 54 | 6397 |  | -1 | INT16 | 11642 | 11643 | AI | 838 | R |  | Degrees
| Current Angle- Circuit 55 | 55 | 6398 |  | -1 | INT16 | 11644 | 11645 | AI | 839 | R |  | Degrees
| Current Angle- Circuit 56 | 56 | 6399 |  | -1 | INT16 | 11646 | 11647 | AI | 840 | R |  | Degrees
| Current Angle- Circuit 57 | 57 | 6400 |  | -1 | INT16 | 11648 | 11649 | AI | 841 | R |  | Degrees
| Current Angle- Circuit 58 | 58 | 6401 |  | -1 | INT16 | 11650 | 11651 | AI | 842 | R |  | Degrees
| Current Angle- Circuit 59 | 59 | 6402 |  | -1 | INT16 | 11652 | 11653 | AI | 843 | R |  | Degrees
| Current Angle- Circuit 60 | 60 | 6403 |  | -1 | INT16 | 11654 | 11655 | AI | 844 | R |  | Degrees
| Current Angle- Circuit 61 | 61 | 6404 |  | -1 | INT16 | 11656 | 11657 | AI | 845 | R |  | Degrees
| Current Angle- Circuit 62 | 62 | 6405 |  | -1 | INT16 | 11658 | 11659 | AI | 846 | R |  | Degrees
| Current Angle- Circuit 63 | 63 | 6406 |  | -1 | INT16 | 11660 | 11661 | AI | 847 | R |  | Degrees
| Current Angle- Circuit 64 | 64 | 6407 |  | -1 | INT16 | 11662 | 11663 | AI | 848 | R |  | Degrees
| Current Angle- Circuit 65 | 65 | 6408 |  | -1 | INT16 | 11664 | 11665 | AI | 849 | R |  | Degrees
| Current Angle- Circuit 66 | 66 | 6409 |  | -1 | INT16 | 11666 | 11667 | AI | 850 | R |  | Degrees
| Current Angle- Circuit 67 | 67 | 6410 |  | -1 | INT16 | 11668 | 11669 | AI | 851 | R |  | Degrees
| Current Angle- Circuit 68 | 68 | 6411 |  | -1 | INT16 | 11670 | 11671 | AI | 852 | R |  | Degrees
| Current Angle- Circuit 69 | 69 | 6412 |  | -1 | INT16 | 11672 | 11673 | AI | 853 | R |  | Degrees
| Current Angle- Circuit 70 | 70 | 6413 |  | -1 | INT16 | 11674 | 11675 | AI | 854 | R |  | Degrees
| Current Angle- Circuit 71 | 71 | 6414 |  | -1 | INT16 | 11676 | 11677 | AI | 855 | R |  | Degrees
| Current Angle- Circuit 72 | 72 | 6415 |  | -1 | INT16 | 11678 | 11679 | AI | 856 | R |  | Degrees
| Current Angle- Circuit 73 | 73 | 6416 |  | -1 | INT16 | 11680 | 11681 | AI | 857 | R |  | Degrees
| Current Angle- Circuit 74 | 74 | 6417 |  | -1 | INT16 | 11682 | 11683 | AI | 858 | R |  | Degrees
| Current Angle- Circuit 75 | 75 | 6418 |  | -1 | INT16 | 11684 | 11685 | AI | 859 | R |  | Degrees
| Current Angle- Circuit 76 | 76 | 6419 |  | -1 | INT16 | 11686 | 11687 | AI | 860 | R |  | Degrees
| Current Angle- Circuit 77 | 77 | 6420 |  | -1 | INT16 | 11688 | 11689 | AI | 861 | R |  | Degrees
| Current Angle- Circuit 78 | 78 | 6421 |  | -1 | INT16 | 11690 | 11691 | AI | 862 | R |  | Degrees
| Current Angle- Circuit 79 | 79 | 6422 |  | -1 | INT16 | 11692 | 11693 | AI | 863 | R |  | Degrees
| Current Angle- Circuit 80 | 80 | 6423 |  | -1 | INT16 | 11694 | 11695 | AI | 864 | R |  | Degrees
| Current Angle- Circuit 81 | 81 | 6424 |  | -1 | INT16 | 11696 | 11697 | AI | 865 | R |  | Degrees
| Current Angle- Circuit 82 | 82 | 6425 |  | -1 | INT16 | 11698 | 11699 | AI | 866 | R |  | Degrees
| Current Angle- Circuit 83 | 83 | 6426 |  | -1 | INT16 | 11700 | 11701 | AI | 867 | R |  | Degrees
| Current Angle- Circuit 84 | 84 | 6427 |  | -1 | INT16 | 11702 | 11703 | AI | 868 | R |  | Degrees
| Current Angle- Circuit 85 | 85 | 6428 |  | -1 | INT16 | 11704 | 11705 | AI | 869 | R |  | Degrees
| Current Angle- Circuit 86 | 86 | 6429 |  | -1 | INT16 | 11706 | 11707 | AI | 870 | R |  | Degrees
| Current Angle- Circuit 87 | 87 | 6430 |  | -1 | INT16 | 11708 | 11709 | AI | 871 | R |  | Degrees
| Current Angle- Circuit 88 | 88 | 6431 |  | -1 | INT16 | 11710 | 11711 | AI | 872 | R |  | Degrees
| Current Angle- Circuit 89 | 89 | 6432 |  | -1 | INT16 | 11712 | 11713 | AI | 873 | R |  | Degrees
| Current Angle- Circuit 90 | 90 | 6433 |  | -1 | INT16 | 11714 | 11715 | AI | 874 | R |  | Degrees
| Current Angle- Circuit 91 | 91 | 6434 |  | -1 | INT16 | 11716 | 11717 | AI | 875 | R |  | Degrees
| Current Angle- Circuit 92 | 92 | 6435 |  | -1 | INT16 | 11718 | 11719 | AI | 876 | R |  | Degrees
| Current Angle- Circuit 93 | 93 | 6436 |  | -1 | INT16 | 11720 | 11721 | AI | 877 | R |  | Degrees
| Current Angle- Circuit 94 | 94 | 6437 |  | -1 | INT16 | 11722 | 11723 | AI | 878 | R |  | Degrees
| Current Angle- Circuit 95 | 95 | 6438 |  | -1 | INT16 | 11724 | 11725 | AI | 879 | R |  | Degrees
| Current Angle- Circuit 96 | 96 | 6439 |  | -1 | INT16 | 11726 | 11727 | AI | 880 | R |  | Degrees
| Percent THD |  | 6440 | 6535 | -1 | UINT16 | 11728 | 11919 | AI |  | R |  | Percent
| Percent THD - Circuit 1 | 1 | 6440 |  | -1 | UINT16 | 11728 | 11729 | AI | 881 | R |  | Percent
| Percent THD - Circuit 2 | 2 | 6441 |  | -1 | UINT16 | 11730 | 11731 | AI | 882 | R |  | Percent
| Percent THD - Circuit 3 | 3 | 6442 |  | -1 | UINT16 | 11732 | 11733 | AI | 883 | R |  | Percent
| Percent THD - Circuit 4 | 4 | 6443 |  | -1 | UINT16 | 11734 | 11735 | AI | 884 | R |  | Percent
| Percent THD - Circuit 5 | 5 | 6444 |  | -1 | UINT16 | 11736 | 11737 | AI | 885 | R |  | Percent
| Percent THD - Circuit 6 | 6 | 6445 |  | -1 | UINT16 | 11738 | 11739 | AI | 886 | R |  | Percent
| Percent THD - Circuit 7 | 7 | 6446 |  | -1 | UINT16 | 11740 | 11741 | AI | 887 | R |  | Percent
| Percent THD - Circuit 8 | 8 | 6447 |  | -1 | UINT16 | 11742 | 11743 | AI | 888 | R |  | Percent
| Percent THD - Circuit 9 | 9 | 6448 |  | -1 | UINT16 | 11744 | 11745 | AI | 889 | R |  | Percent
| Percent THD - Circuit 10 | 10 | 6449 |  | -1 | UINT16 | 11746 | 11747 | AI | 890 | R |  | Percent
| Percent THD - Circuit 11 | 11 | 6450 |  | -1 | UINT16 | 11748 | 11749 | AI | 891 | R |  | Percent
| Percent THD - Circuit 12 | 12 | 6451 |  | -1 | UINT16 | 11750 | 11751 | AI | 892 | R |  | Percent
| Percent THD - Circuit 13 | 13 | 6452 |  | -1 | UINT16 | 11752 | 11753 | AI | 893 | R |  | Percent
| Percent THD - Circuit 14 | 14 | 6453 |  | -1 | UINT16 | 11754 | 11755 | AI | 894 | R |  | Percent
| Percent THD - Circuit 15 | 15 | 6454 |  | -1 | UINT16 | 11756 | 11757 | AI | 895 | R |  | Percent
| Percent THD - Circuit 16 | 16 | 6455 |  | -1 | UINT16 | 11758 | 11759 | AI | 896 | R |  | Percent
| Percent THD - Circuit 17 | 17 | 6456 |  | -1 | UINT16 | 11760 | 11761 | AI | 897 | R |  | Percent
| Percent THD - Circuit 18 | 18 | 6457 |  | -1 | UINT16 | 11762 | 11763 | AI | 898 | R |  | Percent
| Percent THD - Circuit 19 | 19 | 6458 |  | -1 | UINT16 | 11764 | 11765 | AI | 899 | R |  | Percent
| Percent THD - Circuit 20 | 20 | 6459 |  | -1 | UINT16 | 11766 | 11767 | AI | 900 | R |  | Percent
| Percent THD - Circuit 21 | 21 | 6460 |  | -1 | UINT16 | 11768 | 11769 | AI | 901 | R |  | Percent
| Percent THD - Circuit 22 | 22 | 6461 |  | -1 | UINT16 | 11770 | 11771 | AI | 902 | R |  | Percent
| Percent THD - Circuit 23 | 23 | 6462 |  | -1 | UINT16 | 11772 | 11773 | AI | 903 | R |  | Percent
| Percent THD - Circuit 24 | 24 | 6463 |  | -1 | UINT16 | 11774 | 11775 | AI | 904 | R |  | Percent
| Percent THD - Circuit 25 | 25 | 6464 |  | -1 | UINT16 | 11776 | 11777 | AI | 905 | R |  | Percent
| Percent THD - Circuit 26 | 26 | 6465 |  | -1 | UINT16 | 11778 | 11779 | AI | 906 | R |  | Percent
| Percent THD - Circuit 27 | 27 | 6466 |  | -1 | UINT16 | 11780 | 11781 | AI | 907 | R |  | Percent
| Percent THD - Circuit 28 | 28 | 6467 |  | -1 | UINT16 | 11782 | 11783 | AI | 908 | R |  | Percent
| Percent THD - Circuit 29 | 29 | 6468 |  | -1 | UINT16 | 11784 | 11785 | AI | 909 | R |  | Percent
| Percent THD - Circuit 30 | 30 | 6469 |  | -1 | UINT16 | 11786 | 11787 | AI | 910 | R |  | Percent
| Percent THD - Circuit 31 | 31 | 6470 |  | -1 | UINT16 | 11788 | 11789 | AI | 911 | R |  | Percent
| Percent THD - Circuit 32 | 32 | 6471 |  | -1 | UINT16 | 11790 | 11791 | AI | 912 | R |  | Percent
| Percent THD - Circuit 33 | 33 | 6472 |  | -1 | UINT16 | 11792 | 11793 | AI | 913 | R |  | Percent
| Percent THD - Circuit 34 | 34 | 6473 |  | -1 | UINT16 | 11794 | 11795 | AI | 914 | R |  | Percent
| Percent THD - Circuit 35 | 35 | 6474 |  | -1 | UINT16 | 11796 | 11797 | AI | 915 | R |  | Percent
| Percent THD - Circuit 36 | 36 | 6475 |  | -1 | UINT16 | 11798 | 11799 | AI | 916 | R |  | Percent
| Percent THD - Circuit 37 | 37 | 6476 |  | -1 | UINT16 | 11800 | 11801 | AI | 917 | R |  | Percent
| Percent THD - Circuit 38 | 38 | 6477 |  | -1 | UINT16 | 11802 | 11803 | AI | 918 | R |  | Percent
| Percent THD - Circuit 39 | 39 | 6478 |  | -1 | UINT16 | 11804 | 11805 | AI | 919 | R |  | Percent
| Percent THD - Circuit 40 | 40 | 6479 |  | -1 | UINT16 | 11806 | 11807 | AI | 920 | R |  | Percent
| Percent THD - Circuit 41 | 41 | 6480 |  | -1 | UINT16 | 11808 | 11809 | AI | 921 | R |  | Percent
| Percent THD - Circuit 42 | 42 | 6481 |  | -1 | UINT16 | 11810 | 11811 | AI | 922 | R |  | Percent
| Percent THD - Circuit 43 | 43 | 6482 |  | -1 | UINT16 | 11812 | 11813 | AI | 923 | R |  | Percent
| Percent THD - Circuit 44 | 44 | 6483 |  | -1 | UINT16 | 11814 | 11815 | AI | 924 | R |  | Percent
| Percent THD - Circuit 45 | 45 | 6484 |  | -1 | UINT16 | 11816 | 11817 | AI | 925 | R |  | Percent
| Percent THD - Circuit 46 | 46 | 6485 |  | -1 | UINT16 | 11818 | 11819 | AI | 926 | R |  | Percent
| Percent THD - Circuit 47 | 47 | 6486 |  | -1 | UINT16 | 11820 | 11821 | AI | 927 | R |  | Percent
| Percent THD - Circuit 48 | 48 | 6487 |  | -1 | UINT16 | 11822 | 11823 | AI | 928 | R |  | Percent
| Percent THD - Circuit 49 | 49 | 6488 |  | -1 | UINT16 | 11824 | 11825 | AI | 929 | R |  | Percent
| Percent THD - Circuit 50 | 50 | 6489 |  | -1 | UINT16 | 11826 | 11827 | AI | 930 | R |  | Percent
| Percent THD - Circuit 51 | 51 | 6490 |  | -1 | UINT16 | 11828 | 11829 | AI | 931 | R |  | Percent
| Percent THD - Circuit 52 | 52 | 6491 |  | -1 | UINT16 | 11830 | 11831 | AI | 932 | R |  | Percent
| Percent THD - Circuit 53 | 53 | 6492 |  | -1 | UINT16 | 11832 | 11833 | AI | 933 | R |  | Percent
| Percent THD - Circuit 54 | 54 | 6493 |  | -1 | UINT16 | 11834 | 11835 | AI | 934 | R |  | Percent
| Percent THD - Circuit 55 | 55 | 6494 |  | -1 | UINT16 | 11836 | 11837 | AI | 935 | R |  | Percent
| Percent THD - Circuit 56 | 56 | 6495 |  | -1 | UINT16 | 11838 | 11839 | AI | 936 | R |  | Percent
| Percent THD - Circuit 57 | 57 | 6496 |  | -1 | UINT16 | 11840 | 11841 | AI | 937 | R |  | Percent
| Percent THD - Circuit 58 | 58 | 6497 |  | -1 | UINT16 | 11842 | 11843 | AI | 938 | R |  | Percent
| Percent THD - Circuit 59 | 59 | 6498 |  | -1 | UINT16 | 11844 | 11845 | AI | 939 | R |  | Percent
| Percent THD - Circuit 60 | 60 | 6499 |  | -1 | UINT16 | 11846 | 11847 | AI | 940 | R |  | Percent
| Percent THD - Circuit 61 | 61 | 6500 |  | -1 | UINT16 | 11848 | 11849 | AI | 941 | R |  | Percent
| Percent THD - Circuit 62 | 62 | 6501 |  | -1 | UINT16 | 11850 | 11851 | AI | 942 | R |  | Percent
| Percent THD - Circuit 63 | 63 | 6502 |  | -1 | UINT16 | 11852 | 11853 | AI | 943 | R |  | Percent
| Percent THD - Circuit 64 | 64 | 6503 |  | -1 | UINT16 | 11854 | 11855 | AI | 944 | R |  | Percent
| Percent THD - Circuit 65 | 65 | 6504 |  | -1 | UINT16 | 11856 | 11857 | AI | 945 | R |  | Percent
| Percent THD - Circuit 66 | 66 | 6505 |  | -1 | UINT16 | 11858 | 11859 | AI | 946 | R |  | Percent
| Percent THD - Circuit 67 | 67 | 6506 |  | -1 | UINT16 | 11860 | 11861 | AI | 947 | R |  | Percent
| Percent THD - Circuit 68 | 68 | 6507 |  | -1 | UINT16 | 11862 | 11863 | AI | 948 | R |  | Percent
| Percent THD - Circuit 69 | 69 | 6508 |  | -1 | UINT16 | 11864 | 11865 | AI | 949 | R |  | Percent
| Percent THD - Circuit 70 | 70 | 6509 |  | -1 | UINT16 | 11866 | 11867 | AI | 950 | R |  | Percent
| Percent THD - Circuit 71 | 71 | 6510 |  | -1 | UINT16 | 11868 | 11869 | AI | 951 | R |  | Percent
| Percent THD - Circuit 72 | 72 | 6511 |  | -1 | UINT16 | 11870 | 11871 | AI | 952 | R |  | Percent
| Percent THD - Circuit 73 | 73 | 6512 |  | -1 | UINT16 | 11872 | 11873 | AI | 953 | R |  | Percent
| Percent THD - Circuit 74 | 74 | 6513 |  | -1 | UINT16 | 11874 | 11875 | AI | 954 | R |  | Percent
| Percent THD - Circuit 75 | 75 | 6514 |  | -1 | UINT16 | 11876 | 11877 | AI | 955 | R |  | Percent
| Percent THD - Circuit 76 | 76 | 6515 |  | -1 | UINT16 | 11878 | 11879 | AI | 956 | R |  | Percent
| Percent THD - Circuit 77 | 77 | 6516 |  | -1 | UINT16 | 11880 | 11881 | AI | 957 | R |  | Percent
| Percent THD - Circuit 78 | 78 | 6517 |  | -1 | UINT16 | 11882 | 11883 | AI | 958 | R |  | Percent
| Percent THD - Circuit 79 | 79 | 6518 |  | -1 | UINT16 | 11884 | 11885 | AI | 959 | R |  | Percent
| Percent THD - Circuit 80 | 80 | 6519 |  | -1 | UINT16 | 11886 | 11887 | AI | 960 | R |  | Percent
| Percent THD - Circuit 81 | 81 | 6520 |  | -1 | UINT16 | 11888 | 11889 | AI | 961 | R |  | Percent
| Percent THD - Circuit 82 | 82 | 6521 |  | -1 | UINT16 | 11890 | 11891 | AI | 962 | R |  | Percent
| Percent THD - Circuit 83 | 83 | 6522 |  | -1 | UINT16 | 11892 | 11893 | AI | 963 | R |  | Percent
| Percent THD - Circuit 84 | 84 | 6523 |  | -1 | UINT16 | 11894 | 11895 | AI | 964 | R |  | Percent
| Percent THD - Circuit 85 | 85 | 6524 |  | -1 | UINT16 | 11896 | 11897 | AI | 965 | R |  | Percent
| Percent THD - Circuit 86 | 86 | 6525 |  | -1 | UINT16 | 11898 | 11899 | AI | 966 | R |  | Percent
| Percent THD - Circuit 87 | 87 | 6526 |  | -1 | UINT16 | 11900 | 11901 | AI | 967 | R |  | Percent
| Percent THD - Circuit 88 | 88 | 6527 |  | -1 | UINT16 | 11902 | 11903 | AI | 968 | R |  | Percent
| Percent THD - Circuit 89 | 89 | 6528 |  | -1 | UINT16 | 11904 | 11905 | AI | 969 | R |  | Percent
| Percent THD - Circuit 90 | 90 | 6529 |  | -1 | UINT16 | 11906 | 11907 | AI | 970 | R |  | Percent
| Percent THD - Circuit 91 | 91 | 6530 |  | -1 | UINT16 | 11908 | 11909 | AI | 971 | R |  | Percent
| Percent THD - Circuit 92 | 92 | 6531 |  | -1 | UINT16 | 11910 | 11911 | AI | 972 | R |  | Percent
| Percent THD - Circuit 93 | 93 | 6532 |  | -1 | UINT16 | 11912 | 11913 | AI | 973 | R |  | Percent
| Percent THD - Circuit 94 | 94 | 6533 |  | -1 | UINT16 | 11914 | 11915 | AI | 974 | R |  | Percent
| Percent THD - Circuit 95 | 95 | 6534 |  | -1 | UINT16 | 11916 | 11917 | AI | 975 | R |  | Percent
| Percent THD - Circuit 96 | 96 | 6535 |  | -1 | UINT16 | 11918 | 11919 | AI | 976 | R |  | Percent
| Max Current |  | 6536 | 6631 | Current | UINT16 | 11920 | 12111 | AI |  | R | NV | Amps
| Max Current- Circuit 1 | 1 | 6536 |  | 5192 | UINT16 | 11920 | 11921 | AI | 977 | R | NV | Amps
| Max Current- Circuit 2 | 2 | 6537 |  | 5193 | UINT16 | 11922 | 11923 | AI | 978 | R | NV | Amps
| Max Current- Circuit 3 | 3 | 6538 |  | 5194 | UINT16 | 11924 | 11925 | AI | 979 | R | NV | Amps
| Max Current- Circuit 4 | 4 | 6539 |  | 5195 | UINT16 | 11926 | 11927 | AI | 980 | R | NV | Amps
| Max Current- Circuit 5 | 5 | 6540 |  | 5196 | UINT16 | 11928 | 11929 | AI | 981 | R | NV | Amps
| Max Current- Circuit 6 | 6 | 6541 |  | 5197 | UINT16 | 11930 | 11931 | AI | 982 | R | NV | Amps
| Max Current- Circuit 7 | 7 | 6542 |  | 5198 | UINT16 | 11932 | 11933 | AI | 983 | R | NV | Amps
| Max Current- Circuit 8 | 8 | 6543 |  | 5199 | UINT16 | 11934 | 11935 | AI | 984 | R | NV | Amps
| Max Current- Circuit 9 | 9 | 6544 |  | 5200 | UINT16 | 11936 | 11937 | AI | 985 | R | NV | Amps
| Max Current- Circuit 10 | 10 | 6545 |  | 5201 | UINT16 | 11938 | 11939 | AI | 986 | R | NV | Amps
| Max Current- Circuit 11 | 11 | 6546 |  | 5202 | UINT16 | 11940 | 11941 | AI | 987 | R | NV | Amps
| Max Current- Circuit 12 | 12 | 6547 |  | 5203 | UINT16 | 11942 | 11943 | AI | 988 | R | NV | Amps
| Max Current- Circuit 13 | 13 | 6548 |  | 5204 | UINT16 | 11944 | 11945 | AI | 989 | R | NV | Amps
| Max Current- Circuit 14 | 14 | 6549 |  | 5205 | UINT16 | 11946 | 11947 | AI | 990 | R | NV | Amps
| Max Current- Circuit 15 | 15 | 6550 |  | 5206 | UINT16 | 11948 | 11949 | AI | 991 | R | NV | Amps
| Max Current- Circuit 16 | 16 | 6551 |  | 5207 | UINT16 | 11950 | 11951 | AI | 992 | R | NV | Amps
| Max Current- Circuit 17 | 17 | 6552 |  | 5208 | UINT16 | 11952 | 11953 | AI | 993 | R | NV | Amps
| Max Current- Circuit 18 | 18 | 6553 |  | 5209 | UINT16 | 11954 | 11955 | AI | 994 | R | NV | Amps
| Max Current- Circuit 19 | 19 | 6554 |  | 5210 | UINT16 | 11956 | 11957 | AI | 995 | R | NV | Amps
| Max Current- Circuit 20 | 20 | 6555 |  | 5211 | UINT16 | 11958 | 11959 | AI | 996 | R | NV | Amps
| Max Current- Circuit 21 | 21 | 6556 |  | 5212 | UINT16 | 11960 | 11961 | AI | 997 | R | NV | Amps
| Max Current- Circuit 22 | 22 | 6557 |  | 5213 | UINT16 | 11962 | 11963 | AI | 998 | R | NV | Amps
| Max Current- Circuit 23 | 23 | 6558 |  | 5214 | UINT16 | 11964 | 11965 | AI | 999 | R | NV | Amps
| Max Current- Circuit 24 | 24 | 6559 |  | 5215 | UINT16 | 11966 | 11967 | AI | 1000 | R | NV | Amps
| Max Current- Circuit 25 | 25 | 6560 |  | 5216 | UINT16 | 11968 | 11969 | AI | 1001 | R | NV | Amps
| Max Current- Circuit 26 | 26 | 6561 |  | 5217 | UINT16 | 11970 | 11971 | AI | 1002 | R | NV | Amps
| Max Current- Circuit 27 | 27 | 6562 |  | 5218 | UINT16 | 11972 | 11973 | AI | 1003 | R | NV | Amps
| Max Current- Circuit 28 | 28 | 6563 |  | 5219 | UINT16 | 11974 | 11975 | AI | 1004 | R | NV | Amps
| Max Current- Circuit 29 | 29 | 6564 |  | 5220 | UINT16 | 11976 | 11977 | AI | 1005 | R | NV | Amps
| Max Current- Circuit 30 | 30 | 6565 |  | 5221 | UINT16 | 11978 | 11979 | AI | 1006 | R | NV | Amps
| Max Current- Circuit 31 | 31 | 6566 |  | 5222 | UINT16 | 11980 | 11981 | AI | 1007 | R | NV | Amps
| Max Current- Circuit 32 | 32 | 6567 |  | 5223 | UINT16 | 11982 | 11983 | AI | 1008 | R | NV | Amps
| Max Current- Circuit 33 | 33 | 6568 |  | 5224 | UINT16 | 11984 | 11985 | AI | 1009 | R | NV | Amps
| Max Current- Circuit 34 | 34 | 6569 |  | 5225 | UINT16 | 11986 | 11987 | AI | 1010 | R | NV | Amps
| Max Current- Circuit 35 | 35 | 6570 |  | 5226 | UINT16 | 11988 | 11989 | AI | 1011 | R | NV | Amps
| Max Current- Circuit 36 | 36 | 6571 |  | 5227 | UINT16 | 11990 | 11991 | AI | 1012 | R | NV | Amps
| Max Current- Circuit 37 | 37 | 6572 |  | 5228 | UINT16 | 11992 | 11993 | AI | 1013 | R | NV | Amps
| Max Current- Circuit 38 | 38 | 6573 |  | 5229 | UINT16 | 11994 | 11995 | AI | 1014 | R | NV | Amps
| Max Current- Circuit 39 | 39 | 6574 |  | 5230 | UINT16 | 11996 | 11997 | AI | 1015 | R | NV | Amps
| Max Current- Circuit 40 | 40 | 6575 |  | 5231 | UINT16 | 11998 | 11999 | AI | 1016 | R | NV | Amps
| Max Current- Circuit 41 | 41 | 6576 |  | 5232 | UINT16 | 12000 | 12001 | AI | 1017 | R | NV | Amps
| Max Current- Circuit 42 | 42 | 6577 |  | 5233 | UINT16 | 12002 | 12003 | AI | 1018 | R | NV | Amps
| Max Current- Circuit 43 | 43 | 6578 |  | 5234 | UINT16 | 12004 | 12005 | AI | 1019 | R | NV | Amps
| Max Current- Circuit 44 | 44 | 6579 |  | 5235 | UINT16 | 12006 | 12007 | AI | 1020 | R | NV | Amps
| Max Current- Circuit 45 | 45 | 6580 |  | 5236 | UINT16 | 12008 | 12009 | AI | 1021 | R | NV | Amps
| Max Current- Circuit 46 | 46 | 6581 |  | 5237 | UINT16 | 12010 | 12011 | AI | 1022 | R | NV | Amps
| Max Current- Circuit 47 | 47 | 6582 |  | 5238 | UINT16 | 12012 | 12013 | AI | 1023 | R | NV | Amps
| Max Current- Circuit 48 | 48 | 6583 |  | 5239 | UINT16 | 12014 | 12015 | AI | 1024 | R | NV | Amps
| Max Current- Circuit 49 | 49 | 6584 |  | 5240 | UINT16 | 12016 | 12017 | AI | 1025 | R | NV | Amps
| Max Current- Circuit 50 | 50 | 6585 |  | 5241 | UINT16 | 12018 | 12019 | AI | 1026 | R | NV | Amps
| Max Current- Circuit 51 | 51 | 6586 |  | 5242 | UINT16 | 12020 | 12021 | AI | 1027 | R | NV | Amps
| Max Current- Circuit 52 | 52 | 6587 |  | 5243 | UINT16 | 12022 | 12023 | AI | 1028 | R | NV | Amps
| Max Current- Circuit 53 | 53 | 6588 |  | 5244 | UINT16 | 12024 | 12025 | AI | 1029 | R | NV | Amps
| Max Current- Circuit 54 | 54 | 6589 |  | 5245 | UINT16 | 12026 | 12027 | AI | 1030 | R | NV | Amps
| Max Current- Circuit 55 | 55 | 6590 |  | 5246 | UINT16 | 12028 | 12029 | AI | 1031 | R | NV | Amps
| Max Current- Circuit 56 | 56 | 6591 |  | 5247 | UINT16 | 12030 | 12031 | AI | 1032 | R | NV | Amps
| Max Current- Circuit 57 | 57 | 6592 |  | 5248 | UINT16 | 12032 | 12033 | AI | 1033 | R | NV | Amps
| Max Current- Circuit 58 | 58 | 6593 |  | 5249 | UINT16 | 12034 | 12035 | AI | 1034 | R | NV | Amps
| Max Current- Circuit 59 | 59 | 6594 |  | 5250 | UINT16 | 12036 | 12037 | AI | 1035 | R | NV | Amps
| Max Current- Circuit 60 | 60 | 6595 |  | 5251 | UINT16 | 12038 | 12039 | AI | 1036 | R | NV | Amps
| Max Current- Circuit 61 | 61 | 6596 |  | 5252 | UINT16 | 12040 | 12041 | AI | 1037 | R | NV | Amps
| Max Current- Circuit 62 | 62 | 6597 |  | 5253 | UINT16 | 12042 | 12043 | AI | 1038 | R | NV | Amps
| Max Current- Circuit 63 | 63 | 6598 |  | 5254 | UINT16 | 12044 | 12045 | AI | 1039 | R | NV | Amps
| Max Current- Circuit 64 | 64 | 6599 |  | 5255 | UINT16 | 12046 | 12047 | AI | 1040 | R | NV | Amps
| Max Current- Circuit 65 | 65 | 6600 |  | 5256 | UINT16 | 12048 | 12049 | AI | 1041 | R | NV | Amps
| Max Current- Circuit 66 | 66 | 6601 |  | 5257 | UINT16 | 12050 | 12051 | AI | 1042 | R | NV | Amps
| Max Current- Circuit 67 | 67 | 6602 |  | 5258 | UINT16 | 12052 | 12053 | AI | 1043 | R | NV | Amps
| Max Current- Circuit 68 | 68 | 6603 |  | 5259 | UINT16 | 12054 | 12055 | AI | 1044 | R | NV | Amps
| Max Current- Circuit 69 | 69 | 6604 |  | 5260 | UINT16 | 12056 | 12057 | AI | 1045 | R | NV | Amps
| Max Current- Circuit 70 | 70 | 6605 |  | 5261 | UINT16 | 12058 | 12059 | AI | 1046 | R | NV | Amps
| Max Current- Circuit 71 | 71 | 6606 |  | 5262 | UINT16 | 12060 | 12061 | AI | 1047 | R | NV | Amps
| Max Current- Circuit 72 | 72 | 6607 |  | 5263 | UINT16 | 12062 | 12063 | AI | 1048 | R | NV | Amps
| Max Current- Circuit 73 | 73 | 6608 |  | 5264 | UINT16 | 12064 | 12065 | AI | 1049 | R | NV | Amps
| Max Current- Circuit 74 | 74 | 6609 |  | 5265 | UINT16 | 12066 | 12067 | AI | 1050 | R | NV | Amps
| Max Current- Circuit 75 | 75 | 6610 |  | 5266 | UINT16 | 12068 | 12069 | AI | 1051 | R | NV | Amps
| Max Current- Circuit 76 | 76 | 6611 |  | 5267 | UINT16 | 12070 | 12071 | AI | 1052 | R | NV | Amps
| Max Current- Circuit 77 | 77 | 6612 |  | 5268 | UINT16 | 12072 | 12073 | AI | 1053 | R | NV | Amps
| Max Current- Circuit 78 | 78 | 6613 |  | 5269 | UINT16 | 12074 | 12075 | AI | 1054 | R | NV | Amps
| Max Current- Circuit 79 | 79 | 6614 |  | 5270 | UINT16 | 12076 | 12077 | AI | 1055 | R | NV | Amps
| Max Current- Circuit 80 | 80 | 6615 |  | 5271 | UINT16 | 12078 | 12079 | AI | 1056 | R | NV | Amps
| Max Current- Circuit 81 | 81 | 6616 |  | 5272 | UINT16 | 12080 | 12081 | AI | 1057 | R | NV | Amps
| Max Current- Circuit 82 | 82 | 6617 |  | 5273 | UINT16 | 12082 | 12083 | AI | 1058 | R | NV | Amps
| Max Current- Circuit 83 | 83 | 6618 |  | 5274 | UINT16 | 12084 | 12085 | AI | 1059 | R | NV | Amps
| Max Current- Circuit 84 | 84 | 6619 |  | 5275 | UINT16 | 12086 | 12087 | AI | 1060 | R | NV | Amps
| Max Current- Circuit 85 | 85 | 6620 |  | 5276 | UINT16 | 12088 | 12089 | AI | 1061 | R | NV | Amps
| Max Current- Circuit 86 | 86 | 6621 |  | 5277 | UINT16 | 12090 | 12091 | AI | 1062 | R | NV | Amps
| Max Current- Circuit 87 | 87 | 6622 |  | 5278 | UINT16 | 12092 | 12093 | AI | 1063 | R | NV | Amps
| Max Current- Circuit 88 | 88 | 6623 |  | 5279 | UINT16 | 12094 | 12095 | AI | 1064 | R | NV | Amps
| Max Current- Circuit 89 | 89 | 6624 |  | 5280 | UINT16 | 12096 | 12097 | AI | 1065 | R | NV | Amps
| Max Current- Circuit 90 | 90 | 6625 |  | 5281 | UINT16 | 12098 | 12099 | AI | 1066 | R | NV | Amps
| Max Current- Circuit 91 | 91 | 6626 |  | 5282 | UINT16 | 12100 | 12101 | AI | 1067 | R | NV | Amps
| Max Current- Circuit 92 | 92 | 6627 |  | 5283 | UINT16 | 12102 | 12103 | AI | 1068 | R | NV | Amps
| Max Current- Circuit 93 | 93 | 6628 |  | 5284 | UINT16 | 12104 | 12105 | AI | 1069 | R | NV | Amps
| Max Current- Circuit 94 | 94 | 6629 |  | 5285 | UINT16 | 12106 | 12107 | AI | 1070 | R | NV | Amps
| Max Current- Circuit 95 | 95 | 6630 |  | 5286 | UINT16 | 12108 | 12109 | AI | 1071 | R | NV | Amps
| Max Current- Circuit 96 | 96 | 6631 |  | 5287 | UINT16 | 12110 | 12111 | AI | 1072 | R | NV | Amps
| Max kW |  | 6632 | 6727 | Power | UINT16 | 12112 | 12303 | AI |  | R | NV | kW
| Max kW- Circuit 1 | 1 | 6632 |  | 5096 | UINT16 | 12112 | 12113 | AI | 1073 | R | NV | kW
| Max kW- Circuit 2 | 2 | 6633 |  | 5097 | UINT16 | 12114 | 12115 | AI | 1074 | R | NV | kW
| Max kW- Circuit 3 | 3 | 6634 |  | 5098 | UINT16 | 12116 | 12117 | AI | 1075 | R | NV | kW
| Max kW- Circuit 4 | 4 | 6635 |  | 5099 | UINT16 | 12118 | 12119 | AI | 1076 | R | NV | kW
| Max kW- Circuit 5 | 5 | 6636 |  | 5100 | UINT16 | 12120 | 12121 | AI | 1077 | R | NV | kW
| Max kW- Circuit 6 | 6 | 6637 |  | 5101 | UINT16 | 12122 | 12123 | AI | 1078 | R | NV | kW
| Max kW- Circuit 7 | 7 | 6638 |  | 5102 | UINT16 | 12124 | 12125 | AI | 1079 | R | NV | kW
| Max kW- Circuit 8 | 8 | 6639 |  | 5103 | UINT16 | 12126 | 12127 | AI | 1080 | R | NV | kW
| Max kW- Circuit 9 | 9 | 6640 |  | 5104 | UINT16 | 12128 | 12129 | AI | 1081 | R | NV | kW
| Max kW- Circuit 10 | 10 | 6641 |  | 5105 | UINT16 | 12130 | 12131 | AI | 1082 | R | NV | kW
| Max kW- Circuit 11 | 11 | 6642 |  | 5106 | UINT16 | 12132 | 12133 | AI | 1083 | R | NV | kW
| Max kW- Circuit 12 | 12 | 6643 |  | 5107 | UINT16 | 12134 | 12135 | AI | 1084 | R | NV | kW
| Max kW- Circuit 13 | 13 | 6644 |  | 5108 | UINT16 | 12136 | 12137 | AI | 1085 | R | NV | kW
| Max kW- Circuit 14 | 14 | 6645 |  | 5109 | UINT16 | 12138 | 12139 | AI | 1086 | R | NV | kW
| Max kW- Circuit 15 | 15 | 6646 |  | 5110 | UINT16 | 12140 | 12141 | AI | 1087 | R | NV | kW
| Max kW- Circuit 16 | 16 | 6647 |  | 5111 | UINT16 | 12142 | 12143 | AI | 1088 | R | NV | kW
| Max kW- Circuit 17 | 17 | 6648 |  | 5112 | UINT16 | 12144 | 12145 | AI | 1089 | R | NV | kW
| Max kW- Circuit 18 | 18 | 6649 |  | 5113 | UINT16 | 12146 | 12147 | AI | 1090 | R | NV | kW
| Max kW- Circuit 19 | 19 | 6650 |  | 5114 | UINT16 | 12148 | 12149 | AI | 1091 | R | NV | kW
| Max kW- Circuit 20 | 20 | 6651 |  | 5115 | UINT16 | 12150 | 12151 | AI | 1092 | R | NV | kW
| Max kW- Circuit 21 | 21 | 6652 |  | 5116 | UINT16 | 12152 | 12153 | AI | 1093 | R | NV | kW
| Max kW- Circuit 22 | 22 | 6653 |  | 5117 | UINT16 | 12154 | 12155 | AI | 1094 | R | NV | kW
| Max kW- Circuit 23 | 23 | 6654 |  | 5118 | UINT16 | 12156 | 12157 | AI | 1095 | R | NV | kW
| Max kW- Circuit 24 | 24 | 6655 |  | 5119 | UINT16 | 12158 | 12159 | AI | 1096 | R | NV | kW
| Max kW- Circuit 25 | 25 | 6656 |  | 5120 | UINT16 | 12160 | 12161 | AI | 1097 | R | NV | kW
| Max kW- Circuit 26 | 26 | 6657 |  | 5121 | UINT16 | 12162 | 12163 | AI | 1098 | R | NV | kW
| Max kW- Circuit 27 | 27 | 6658 |  | 5122 | UINT16 | 12164 | 12165 | AI | 1099 | R | NV | kW
| Max kW- Circuit 28 | 28 | 6659 |  | 5123 | UINT16 | 12166 | 12167 | AI | 1100 | R | NV | kW
| Max kW- Circuit 29 | 29 | 6660 |  | 5124 | UINT16 | 12168 | 12169 | AI | 1101 | R | NV | kW
| Max kW- Circuit 30 | 30 | 6661 |  | 5125 | UINT16 | 12170 | 12171 | AI | 1102 | R | NV | kW
| Max kW- Circuit 31 | 31 | 6662 |  | 5126 | UINT16 | 12172 | 12173 | AI | 1103 | R | NV | kW
| Max kW- Circuit 32 | 32 | 6663 |  | 5127 | UINT16 | 12174 | 12175 | AI | 1104 | R | NV | kW
| Max kW- Circuit 33 | 33 | 6664 |  | 5128 | UINT16 | 12176 | 12177 | AI | 1105 | R | NV | kW
| Max kW- Circuit 34 | 34 | 6665 |  | 5129 | UINT16 | 12178 | 12179 | AI | 1106 | R | NV | kW
| Max kW- Circuit 35 | 35 | 6666 |  | 5130 | UINT16 | 12180 | 12181 | AI | 1107 | R | NV | kW
| Max kW- Circuit 36 | 36 | 6667 |  | 5131 | UINT16 | 12182 | 12183 | AI | 1108 | R | NV | kW
| Max kW- Circuit 37 | 37 | 6668 |  | 5132 | UINT16 | 12184 | 12185 | AI | 1109 | R | NV | kW
| Max kW- Circuit 38 | 38 | 6669 |  | 5133 | UINT16 | 12186 | 12187 | AI | 1110 | R | NV | kW
| Max kW- Circuit 39 | 39 | 6670 |  | 5134 | UINT16 | 12188 | 12189 | AI | 1111 | R | NV | kW
| Max kW- Circuit 40 | 40 | 6671 |  | 5135 | UINT16 | 12190 | 12191 | AI | 1112 | R | NV | kW
| Max kW- Circuit 41 | 41 | 6672 |  | 5136 | UINT16 | 12192 | 12193 | AI | 1113 | R | NV | kW
| Max kW- Circuit 42 | 42 | 6673 |  | 5137 | UINT16 | 12194 | 12195 | AI | 1114 | R | NV | kW
| Max kW- Circuit 43 | 43 | 6674 |  | 5138 | UINT16 | 12196 | 12197 | AI | 1115 | R | NV | kW
| Max kW- Circuit 44 | 44 | 6675 |  | 5139 | UINT16 | 12198 | 12199 | AI | 1116 | R | NV | kW
| Max kW- Circuit 45 | 45 | 6676 |  | 5140 | UINT16 | 12200 | 12201 | AI | 1117 | R | NV | kW
| Max kW- Circuit 46 | 46 | 6677 |  | 5141 | UINT16 | 12202 | 12203 | AI | 1118 | R | NV | kW
| Max kW- Circuit 47 | 47 | 6678 |  | 5142 | UINT16 | 12204 | 12205 | AI | 1119 | R | NV | kW
| Max kW- Circuit 48 | 48 | 6679 |  | 5143 | UINT16 | 12206 | 12207 | AI | 1120 | R | NV | kW
| Max kW- Circuit 49 | 49 | 6680 |  | 5144 | UINT16 | 12208 | 12209 | AI | 1121 | R | NV | kW
| Max kW- Circuit 50 | 50 | 6681 |  | 5145 | UINT16 | 12210 | 12211 | AI | 1122 | R | NV | kW
| Max kW- Circuit 51 | 51 | 6682 |  | 5146 | UINT16 | 12212 | 12213 | AI | 1123 | R | NV | kW
| Max kW- Circuit 52 | 52 | 6683 |  | 5147 | UINT16 | 12214 | 12215 | AI | 1124 | R | NV | kW
| Max kW- Circuit 53 | 53 | 6684 |  | 5148 | UINT16 | 12216 | 12217 | AI | 1125 | R | NV | kW
| Max kW- Circuit 54 | 54 | 6685 |  | 5149 | UINT16 | 12218 | 12219 | AI | 1126 | R | NV | kW
| Max kW- Circuit 55 | 55 | 6686 |  | 5150 | UINT16 | 12220 | 12221 | AI | 1127 | R | NV | kW
| Max kW- Circuit 56 | 56 | 6687 |  | 5151 | UINT16 | 12222 | 12223 | AI | 1128 | R | NV | kW
| Max kW- Circuit 57 | 57 | 6688 |  | 5152 | UINT16 | 12224 | 12225 | AI | 1129 | R | NV | kW
| Max kW- Circuit 58 | 58 | 6689 |  | 5153 | UINT16 | 12226 | 12227 | AI | 1130 | R | NV | kW
| Max kW- Circuit 59 | 59 | 6690 |  | 5154 | UINT16 | 12228 | 12229 | AI | 1131 | R | NV | kW
| Max kW- Circuit 60 | 60 | 6691 |  | 5155 | UINT16 | 12230 | 12231 | AI | 1132 | R | NV | kW
| Max kW- Circuit 61 | 61 | 6692 |  | 5156 | UINT16 | 12232 | 12233 | AI | 1133 | R | NV | kW
| Max kW- Circuit 62 | 62 | 6693 |  | 5157 | UINT16 | 12234 | 12235 | AI | 1134 | R | NV | kW
| Max kW- Circuit 63 | 63 | 6694 |  | 5158 | UINT16 | 12236 | 12237 | AI | 1135 | R | NV | kW
| Max kW- Circuit 64 | 64 | 6695 |  | 5159 | UINT16 | 12238 | 12239 | AI | 1136 | R | NV | kW
| Max kW- Circuit 65 | 65 | 6696 |  | 5160 | UINT16 | 12240 | 12241 | AI | 1137 | R | NV | kW
| Max kW- Circuit 66 | 66 | 6697 |  | 5161 | UINT16 | 12242 | 12243 | AI | 1138 | R | NV | kW
| Max kW- Circuit 67 | 67 | 6698 |  | 5162 | UINT16 | 12244 | 12245 | AI | 1139 | R | NV | kW
| Max kW- Circuit 68 | 68 | 6699 |  | 5163 | UINT16 | 12246 | 12247 | AI | 1140 | R | NV | kW
| Max kW- Circuit 69 | 69 | 6700 |  | 5164 | UINT16 | 12248 | 12249 | AI | 1141 | R | NV | kW
| Max kW- Circuit 70 | 70 | 6701 |  | 5165 | UINT16 | 12250 | 12251 | AI | 1142 | R | NV | kW
| Max kW- Circuit 71 | 71 | 6702 |  | 5166 | UINT16 | 12252 | 12253 | AI | 1143 | R | NV | kW
| Max kW- Circuit 72 | 72 | 6703 |  | 5167 | UINT16 | 12254 | 12255 | AI | 1144 | R | NV | kW
| Max kW- Circuit 73 | 73 | 6704 |  | 5168 | UINT16 | 12256 | 12257 | AI | 1145 | R | NV | kW
| Max kW- Circuit 74 | 74 | 6705 |  | 5169 | UINT16 | 12258 | 12259 | AI | 1146 | R | NV | kW
| Max kW- Circuit 75 | 75 | 6706 |  | 5170 | UINT16 | 12260 | 12261 | AI | 1147 | R | NV | kW
| Max kW- Circuit 76 | 76 | 6707 |  | 5171 | UINT16 | 12262 | 12263 | AI | 1148 | R | NV | kW
| Max kW- Circuit 77 | 77 | 6708 |  | 5172 | UINT16 | 12264 | 12265 | AI | 1149 | R | NV | kW
| Max kW- Circuit 78 | 78 | 6709 |  | 5173 | UINT16 | 12266 | 12267 | AI | 1150 | R | NV | kW
| Max kW- Circuit 79 | 79 | 6710 |  | 5174 | UINT16 | 12268 | 12269 | AI | 1151 | R | NV | kW
| Max kW- Circuit 80 | 80 | 6711 |  | 5175 | UINT16 | 12270 | 12271 | AI | 1152 | R | NV | kW
| Max kW- Circuit 81 | 81 | 6712 |  | 5176 | UINT16 | 12272 | 12273 | AI | 1153 | R | NV | kW
| Max kW- Circuit 82 | 82 | 6713 |  | 5177 | UINT16 | 12274 | 12275 | AI | 1154 | R | NV | kW
| Max kW- Circuit 83 | 83 | 6714 |  | 5178 | UINT16 | 12276 | 12277 | AI | 1155 | R | NV | kW
| Max kW- Circuit 84 | 84 | 6715 |  | 5179 | UINT16 | 12278 | 12279 | AI | 1156 | R | NV | kW
| Max kW- Circuit 85 | 85 | 6716 |  | 5180 | UINT16 | 12280 | 12281 | AI | 1157 | R | NV | kW
| Max kW- Circuit 86 | 86 | 6717 |  | 5181 | UINT16 | 12282 | 12283 | AI | 1158 | R | NV | kW
| Max kW- Circuit 87 | 87 | 6718 |  | 5182 | UINT16 | 12284 | 12285 | AI | 1159 | R | NV | kW
| Max kW- Circuit 88 | 88 | 6719 |  | 5183 | UINT16 | 12286 | 12287 | AI | 1160 | R | NV | kW
| Max kW- Circuit 89 | 89 | 6720 |  | 5184 | UINT16 | 12288 | 12289 | AI | 1161 | R | NV | kW
| Max kW- Circuit 90 | 90 | 6721 |  | 5185 | UINT16 | 12290 | 12291 | AI | 1162 | R | NV | kW
| Max kW- Circuit 91 | 91 | 6722 |  | 5186 | UINT16 | 12292 | 12293 | AI | 1163 | R | NV | kW
| Max kW- Circuit 92 | 92 | 6723 |  | 5187 | UINT16 | 12294 | 12295 | AI | 1164 | R | NV | kW
| Max kW- Circuit 93 | 93 | 6724 |  | 5188 | UINT16 | 12296 | 12297 | AI | 1165 | R | NV | kW
| Max kW- Circuit 94 | 94 | 6725 |  | 5189 | UINT16 | 12298 | 12299 | AI | 1166 | R | NV | kW
| Max kW- Circuit 95 | 95 | 6726 |  | 5190 | UINT16 | 12300 | 12301 | AI | 1167 | R | NV | kW
| Max kW- Circuit 96 | 96 | 6727 |  | 5191 | UINT16 | 12302 | 12303 | AI | 1168 | R | NV | kW
| Current Demand |  | 6728 | 6823 | Current | UINT16 | 12304 | 12495 | AI |  | R |  | Amps
| Current Demand- Circuit 1 | 1 | 6728 |  | 5192 | UINT16 | 12304 | 12305 | AI | 1169 | R |  | Amps
| Current Demand- Circuit 2 | 2 | 6729 |  | 5193 | UINT16 | 12306 | 12307 | AI | 1170 | R |  | Amps
| Current Demand- Circuit 3 | 3 | 6730 |  | 5194 | UINT16 | 12308 | 12309 | AI | 1171 | R |  | Amps
| Current Demand- Circuit 4 | 4 | 6731 |  | 5195 | UINT16 | 12310 | 12311 | AI | 1172 | R |  | Amps
| Current Demand- Circuit 5 | 5 | 6732 |  | 5196 | UINT16 | 12312 | 12313 | AI | 1173 | R |  | Amps
| Current Demand- Circuit 6 | 6 | 6733 |  | 5197 | UINT16 | 12314 | 12315 | AI | 1174 | R |  | Amps
| Current Demand- Circuit 7 | 7 | 6734 |  | 5198 | UINT16 | 12316 | 12317 | AI | 1175 | R |  | Amps
| Current Demand- Circuit 8 | 8 | 6735 |  | 5199 | UINT16 | 12318 | 12319 | AI | 1176 | R |  | Amps
| Current Demand- Circuit 9 | 9 | 6736 |  | 5200 | UINT16 | 12320 | 12321 | AI | 1177 | R |  | Amps
| Current Demand- Circuit 10 | 10 | 6737 |  | 5201 | UINT16 | 12322 | 12323 | AI | 1178 | R |  | Amps
| Current Demand- Circuit 11 | 11 | 6738 |  | 5202 | UINT16 | 12324 | 12325 | AI | 1179 | R |  | Amps
| Current Demand- Circuit 12 | 12 | 6739 |  | 5203 | UINT16 | 12326 | 12327 | AI | 1180 | R |  | Amps
| Current Demand- Circuit 13 | 13 | 6740 |  | 5204 | UINT16 | 12328 | 12329 | AI | 1181 | R |  | Amps
| Current Demand- Circuit 14 | 14 | 6741 |  | 5205 | UINT16 | 12330 | 12331 | AI | 1182 | R |  | Amps
| Current Demand- Circuit 15 | 15 | 6742 |  | 5206 | UINT16 | 12332 | 12333 | AI | 1183 | R |  | Amps
| Current Demand- Circuit 16 | 16 | 6743 |  | 5207 | UINT16 | 12334 | 12335 | AI | 1184 | R |  | Amps
| Current Demand- Circuit 17 | 17 | 6744 |  | 5208 | UINT16 | 12336 | 12337 | AI | 1185 | R |  | Amps
| Current Demand- Circuit 18 | 18 | 6745 |  | 5209 | UINT16 | 12338 | 12339 | AI | 1186 | R |  | Amps
| Current Demand- Circuit 19 | 19 | 6746 |  | 5210 | UINT16 | 12340 | 12341 | AI | 1187 | R |  | Amps
| Current Demand- Circuit 20 | 20 | 6747 |  | 5211 | UINT16 | 12342 | 12343 | AI | 1188 | R |  | Amps
| Current Demand- Circuit 21 | 21 | 6748 |  | 5212 | UINT16 | 12344 | 12345 | AI | 1189 | R |  | Amps
| Current Demand- Circuit 22 | 22 | 6749 |  | 5213 | UINT16 | 12346 | 12347 | AI | 1190 | R |  | Amps
| Current Demand- Circuit 23 | 23 | 6750 |  | 5214 | UINT16 | 12348 | 12349 | AI | 1191 | R |  | Amps
| Current Demand- Circuit 24 | 24 | 6751 |  | 5215 | UINT16 | 12350 | 12351 | AI | 1192 | R |  | Amps
| Current Demand- Circuit 25 | 25 | 6752 |  | 5216 | UINT16 | 12352 | 12353 | AI | 1193 | R |  | Amps
| Current Demand- Circuit 26 | 26 | 6753 |  | 5217 | UINT16 | 12354 | 12355 | AI | 1194 | R |  | Amps
| Current Demand- Circuit 27 | 27 | 6754 |  | 5218 | UINT16 | 12356 | 12357 | AI | 1195 | R |  | Amps
| Current Demand- Circuit 28 | 28 | 6755 |  | 5219 | UINT16 | 12358 | 12359 | AI | 1196 | R |  | Amps
| Current Demand- Circuit 29 | 29 | 6756 |  | 5220 | UINT16 | 12360 | 12361 | AI | 1197 | R |  | Amps
| Current Demand- Circuit 30 | 30 | 6757 |  | 5221 | UINT16 | 12362 | 12363 | AI | 1198 | R |  | Amps
| Current Demand- Circuit 31 | 31 | 6758 |  | 5222 | UINT16 | 12364 | 12365 | AI | 1199 | R |  | Amps
| Current Demand- Circuit 32 | 32 | 6759 |  | 5223 | UINT16 | 12366 | 12367 | AI | 1200 | R |  | Amps
| Current Demand- Circuit 33 | 33 | 6760 |  | 5224 | UINT16 | 12368 | 12369 | AI | 1201 | R |  | Amps
| Current Demand- Circuit 34 | 34 | 6761 |  | 5225 | UINT16 | 12370 | 12371 | AI | 1202 | R |  | Amps
| Current Demand- Circuit 35 | 35 | 6762 |  | 5226 | UINT16 | 12372 | 12373 | AI | 1203 | R |  | Amps
| Current Demand- Circuit 36 | 36 | 6763 |  | 5227 | UINT16 | 12374 | 12375 | AI | 1204 | R |  | Amps
| Current Demand- Circuit 37 | 37 | 6764 |  | 5228 | UINT16 | 12376 | 12377 | AI | 1205 | R |  | Amps
| Current Demand- Circuit 38 | 38 | 6765 |  | 5229 | UINT16 | 12378 | 12379 | AI | 1206 | R |  | Amps
| Current Demand- Circuit 39 | 39 | 6766 |  | 5230 | UINT16 | 12380 | 12381 | AI | 1207 | R |  | Amps
| Current Demand- Circuit 40 | 40 | 6767 |  | 5231 | UINT16 | 12382 | 12383 | AI | 1208 | R |  | Amps
| Current Demand- Circuit 41 | 41 | 6768 |  | 5232 | UINT16 | 12384 | 12385 | AI | 1209 | R |  | Amps
| Current Demand- Circuit 42 | 42 | 6769 |  | 5233 | UINT16 | 12386 | 12387 | AI | 1210 | R |  | Amps
| Current Demand- Circuit 43 | 43 | 6770 |  | 5234 | UINT16 | 12388 | 12389 | AI | 1211 | R |  | Amps
| Current Demand- Circuit 44 | 44 | 6771 |  | 5235 | UINT16 | 12390 | 12391 | AI | 1212 | R |  | Amps
| Current Demand- Circuit 45 | 45 | 6772 |  | 5236 | UINT16 | 12392 | 12393 | AI | 1213 | R |  | Amps
| Current Demand- Circuit 46 | 46 | 6773 |  | 5237 | UINT16 | 12394 | 12395 | AI | 1214 | R |  | Amps
| Current Demand- Circuit 47 | 47 | 6774 |  | 5238 | UINT16 | 12396 | 12397 | AI | 1215 | R |  | Amps
| Current Demand- Circuit 48 | 48 | 6775 |  | 5239 | UINT16 | 12398 | 12399 | AI | 1216 | R |  | Amps
| Current Demand- Circuit 49 | 49 | 6776 |  | 5240 | UINT16 | 12400 | 12401 | AI | 1217 | R |  | Amps
| Current Demand- Circuit 50 | 50 | 6777 |  | 5241 | UINT16 | 12402 | 12403 | AI | 1218 | R |  | Amps
| Current Demand- Circuit 51 | 51 | 6778 |  | 5242 | UINT16 | 12404 | 12405 | AI | 1219 | R |  | Amps
| Current Demand- Circuit 52 | 52 | 6779 |  | 5243 | UINT16 | 12406 | 12407 | AI | 1220 | R |  | Amps
| Current Demand- Circuit 53 | 53 | 6780 |  | 5244 | UINT16 | 12408 | 12409 | AI | 1221 | R |  | Amps
| Current Demand- Circuit 54 | 54 | 6781 |  | 5245 | UINT16 | 12410 | 12411 | AI | 1222 | R |  | Amps
| Current Demand- Circuit 55 | 55 | 6782 |  | 5246 | UINT16 | 12412 | 12413 | AI | 1223 | R |  | Amps
| Current Demand- Circuit 56 | 56 | 6783 |  | 5247 | UINT16 | 12414 | 12415 | AI | 1224 | R |  | Amps
| Current Demand- Circuit 57 | 57 | 6784 |  | 5248 | UINT16 | 12416 | 12417 | AI | 1225 | R |  | Amps
| Current Demand- Circuit 58 | 58 | 6785 |  | 5249 | UINT16 | 12418 | 12419 | AI | 1226 | R |  | Amps
| Current Demand- Circuit 59 | 59 | 6786 |  | 5250 | UINT16 | 12420 | 12421 | AI | 1227 | R |  | Amps
| Current Demand- Circuit 60 | 60 | 6787 |  | 5251 | UINT16 | 12422 | 12423 | AI | 1228 | R |  | Amps
| Current Demand- Circuit 61 | 61 | 6788 |  | 5252 | UINT16 | 12424 | 12425 | AI | 1229 | R |  | Amps
| Current Demand- Circuit 62 | 62 | 6789 |  | 5253 | UINT16 | 12426 | 12427 | AI | 1230 | R |  | Amps
| Current Demand- Circuit 63 | 63 | 6790 |  | 5254 | UINT16 | 12428 | 12429 | AI | 1231 | R |  | Amps
| Current Demand- Circuit 64 | 64 | 6791 |  | 5255 | UINT16 | 12430 | 12431 | AI | 1232 | R |  | Amps
| Current Demand- Circuit 65 | 65 | 6792 |  | 5256 | UINT16 | 12432 | 12433 | AI | 1233 | R |  | Amps
| Current Demand- Circuit 66 | 66 | 6793 |  | 5257 | UINT16 | 12434 | 12435 | AI | 1234 | R |  | Amps
| Current Demand- Circuit 67 | 67 | 6794 |  | 5258 | UINT16 | 12436 | 12437 | AI | 1235 | R |  | Amps
| Current Demand- Circuit 68 | 68 | 6795 |  | 5259 | UINT16 | 12438 | 12439 | AI | 1236 | R |  | Amps
| Current Demand- Circuit 69 | 69 | 6796 |  | 5260 | UINT16 | 12440 | 12441 | AI | 1237 | R |  | Amps
| Current Demand- Circuit 70 | 70 | 6797 |  | 5261 | UINT16 | 12442 | 12443 | AI | 1238 | R |  | Amps
| Current Demand- Circuit 71 | 71 | 6798 |  | 5262 | UINT16 | 12444 | 12445 | AI | 1239 | R |  | Amps
| Current Demand- Circuit 72 | 72 | 6799 |  | 5263 | UINT16 | 12446 | 12447 | AI | 1240 | R |  | Amps
| Current Demand- Circuit 73 | 73 | 6800 |  | 5264 | UINT16 | 12448 | 12449 | AI | 1241 | R |  | Amps
| Current Demand- Circuit 74 | 74 | 6801 |  | 5265 | UINT16 | 12450 | 12451 | AI | 1242 | R |  | Amps
| Current Demand- Circuit 75 | 75 | 6802 |  | 5266 | UINT16 | 12452 | 12453 | AI | 1243 | R |  | Amps
| Current Demand- Circuit 76 | 76 | 6803 |  | 5267 | UINT16 | 12454 | 12455 | AI | 1244 | R |  | Amps
| Current Demand- Circuit 77 | 77 | 6804 |  | 5268 | UINT16 | 12456 | 12457 | AI | 1245 | R |  | Amps
| Current Demand- Circuit 78 | 78 | 6805 |  | 5269 | UINT16 | 12458 | 12459 | AI | 1246 | R |  | Amps
| Current Demand- Circuit 79 | 79 | 6806 |  | 5270 | UINT16 | 12460 | 12461 | AI | 1247 | R |  | Amps
| Current Demand- Circuit 80 | 80 | 6807 |  | 5271 | UINT16 | 12462 | 12463 | AI | 1248 | R |  | Amps
| Current Demand- Circuit 81 | 81 | 6808 |  | 5272 | UINT16 | 12464 | 12465 | AI | 1249 | R |  | Amps
| Current Demand- Circuit 82 | 82 | 6809 |  | 5273 | UINT16 | 12466 | 12467 | AI | 1250 | R |  | Amps
| Current Demand- Circuit 83 | 83 | 6810 |  | 5274 | UINT16 | 12468 | 12469 | AI | 1251 | R |  | Amps
| Current Demand- Circuit 84 | 84 | 6811 |  | 5275 | UINT16 | 12470 | 12471 | AI | 1252 | R |  | Amps
| Current Demand- Circuit 85 | 85 | 6812 |  | 5276 | UINT16 | 12472 | 12473 | AI | 1253 | R |  | Amps
| Current Demand- Circuit 86 | 86 | 6813 |  | 5277 | UINT16 | 12474 | 12475 | AI | 1254 | R |  | Amps
| Current Demand- Circuit 87 | 87 | 6814 |  | 5278 | UINT16 | 12476 | 12477 | AI | 1255 | R |  | Amps
| Current Demand- Circuit 88 | 88 | 6815 |  | 5279 | UINT16 | 12478 | 12479 | AI | 1256 | R |  | Amps
| Current Demand- Circuit 89 | 89 | 6816 |  | 5280 | UINT16 | 12480 | 12481 | AI | 1257 | R |  | Amps
| Current Demand- Circuit 90 | 90 | 6817 |  | 5281 | UINT16 | 12482 | 12483 | AI | 1258 | R |  | Amps
| Current Demand- Circuit 91 | 91 | 6818 |  | 5282 | UINT16 | 12484 | 12485 | AI | 1259 | R |  | Amps
| Current Demand- Circuit 92 | 92 | 6819 |  | 5283 | UINT16 | 12486 | 12487 | AI | 1260 | R |  | Amps
| Current Demand- Circuit 93 | 93 | 6820 |  | 5284 | UINT16 | 12488 | 12489 | AI | 1261 | R |  | Amps
| Current Demand- Circuit 94 | 94 | 6821 |  | 5285 | UINT16 | 12490 | 12491 | AI | 1262 | R |  | Amps
| Current Demand- Circuit 95 | 95 | 6822 |  | 5286 | UINT16 | 12492 | 12493 | AI | 1263 | R |  | Amps
| Current Demand- Circuit 96 | 96 | 6823 |  | 5287 | UINT16 | 12494 | 12495 | AI | 1264 | R |  | Amps
| kW Demand |  | 6824 | 6919 | Power | UINT16 | 12496 | 12687 | AI |  | R |  | kW
| kW Demand- Circuit 1 | 1 | 6824 |  | 5096 | UINT16 | 12496 | 12497 | AI | 1265 | R |  | kW
| kW Demand- Circuit 2 | 2 | 6825 |  | 5097 | UINT16 | 12498 | 12499 | AI | 1266 | R |  | kW
| kW Demand- Circuit 3 | 3 | 6826 |  | 5098 | UINT16 | 12500 | 12501 | AI | 1267 | R |  | kW
| kW Demand- Circuit 4 | 4 | 6827 |  | 5099 | UINT16 | 12502 | 12503 | AI | 1268 | R |  | kW
| kW Demand- Circuit 5 | 5 | 6828 |  | 5100 | UINT16 | 12504 | 12505 | AI | 1269 | R |  | kW
| kW Demand- Circuit 6 | 6 | 6829 |  | 5101 | UINT16 | 12506 | 12507 | AI | 1270 | R |  | kW
| kW Demand- Circuit 7 | 7 | 6830 |  | 5102 | UINT16 | 12508 | 12509 | AI | 1271 | R |  | kW
| kW Demand- Circuit 8 | 8 | 6831 |  | 5103 | UINT16 | 12510 | 12511 | AI | 1272 | R |  | kW
| kW Demand- Circuit 9 | 9 | 6832 |  | 5104 | UINT16 | 12512 | 12513 | AI | 1273 | R |  | kW
| kW Demand- Circuit 10 | 10 | 6833 |  | 5105 | UINT16 | 12514 | 12515 | AI | 1274 | R |  | kW
| kW Demand- Circuit 11 | 11 | 6834 |  | 5106 | UINT16 | 12516 | 12517 | AI | 1275 | R |  | kW
| kW Demand- Circuit 12 | 12 | 6835 |  | 5107 | UINT16 | 12518 | 12519 | AI | 1276 | R |  | kW
| kW Demand- Circuit 13 | 13 | 6836 |  | 5108 | UINT16 | 12520 | 12521 | AI | 1277 | R |  | kW
| kW Demand- Circuit 14 | 14 | 6837 |  | 5109 | UINT16 | 12522 | 12523 | AI | 1278 | R |  | kW
| kW Demand- Circuit 15 | 15 | 6838 |  | 5110 | UINT16 | 12524 | 12525 | AI | 1279 | R |  | kW
| kW Demand- Circuit 16 | 16 | 6839 |  | 5111 | UINT16 | 12526 | 12527 | AI | 1280 | R |  | kW
| kW Demand- Circuit 17 | 17 | 6840 |  | 5112 | UINT16 | 12528 | 12529 | AI | 1281 | R |  | kW
| kW Demand- Circuit 18 | 18 | 6841 |  | 5113 | UINT16 | 12530 | 12531 | AI | 1282 | R |  | kW
| kW Demand- Circuit 19 | 19 | 6842 |  | 5114 | UINT16 | 12532 | 12533 | AI | 1283 | R |  | kW
| kW Demand- Circuit 20 | 20 | 6843 |  | 5115 | UINT16 | 12534 | 12535 | AI | 1284 | R |  | kW
| kW Demand- Circuit 21 | 21 | 6844 |  | 5116 | UINT16 | 12536 | 12537 | AI | 1285 | R |  | kW
| kW Demand- Circuit 22 | 22 | 6845 |  | 5117 | UINT16 | 12538 | 12539 | AI | 1286 | R |  | kW
| kW Demand- Circuit 23 | 23 | 6846 |  | 5118 | UINT16 | 12540 | 12541 | AI | 1287 | R |  | kW
| kW Demand- Circuit 24 | 24 | 6847 |  | 5119 | UINT16 | 12542 | 12543 | AI | 1288 | R |  | kW
| kW Demand- Circuit 25 | 25 | 6848 |  | 5120 | UINT16 | 12544 | 12545 | AI | 1289 | R |  | kW
| kW Demand- Circuit 26 | 26 | 6849 |  | 5121 | UINT16 | 12546 | 12547 | AI | 1290 | R |  | kW
| kW Demand- Circuit 27 | 27 | 6850 |  | 5122 | UINT16 | 12548 | 12549 | AI | 1291 | R |  | kW
| kW Demand- Circuit 28 | 28 | 6851 |  | 5123 | UINT16 | 12550 | 12551 | AI | 1292 | R |  | kW
| kW Demand- Circuit 29 | 29 | 6852 |  | 5124 | UINT16 | 12552 | 12553 | AI | 1293 | R |  | kW
| kW Demand- Circuit 30 | 30 | 6853 |  | 5125 | UINT16 | 12554 | 12555 | AI | 1294 | R |  | kW
| kW Demand- Circuit 31 | 31 | 6854 |  | 5126 | UINT16 | 12556 | 12557 | AI | 1295 | R |  | kW
| kW Demand- Circuit 32 | 32 | 6855 |  | 5127 | UINT16 | 12558 | 12559 | AI | 1296 | R |  | kW
| kW Demand- Circuit 33 | 33 | 6856 |  | 5128 | UINT16 | 12560 | 12561 | AI | 1297 | R |  | kW
| kW Demand- Circuit 34 | 34 | 6857 |  | 5129 | UINT16 | 12562 | 12563 | AI | 1298 | R |  | kW
| kW Demand- Circuit 35 | 35 | 6858 |  | 5130 | UINT16 | 12564 | 12565 | AI | 1299 | R |  | kW
| kW Demand- Circuit 36 | 36 | 6859 |  | 5131 | UINT16 | 12566 | 12567 | AI | 1300 | R |  | kW
| kW Demand- Circuit 37 | 37 | 6860 |  | 5132 | UINT16 | 12568 | 12569 | AI | 1301 | R |  | kW
| kW Demand- Circuit 38 | 38 | 6861 |  | 5133 | UINT16 | 12570 | 12571 | AI | 1302 | R |  | kW
| kW Demand- Circuit 39 | 39 | 6862 |  | 5134 | UINT16 | 12572 | 12573 | AI | 1303 | R |  | kW
| kW Demand- Circuit 40 | 40 | 6863 |  | 5135 | UINT16 | 12574 | 12575 | AI | 1304 | R |  | kW
| kW Demand- Circuit 41 | 41 | 6864 |  | 5136 | UINT16 | 12576 | 12577 | AI | 1305 | R |  | kW
| kW Demand- Circuit 42 | 42 | 6865 |  | 5137 | UINT16 | 12578 | 12579 | AI | 1306 | R |  | kW
| kW Demand- Circuit 43 | 43 | 6866 |  | 5138 | UINT16 | 12580 | 12581 | AI | 1307 | R |  | kW
| kW Demand- Circuit 44 | 44 | 6867 |  | 5139 | UINT16 | 12582 | 12583 | AI | 1308 | R |  | kW
| kW Demand- Circuit 45 | 45 | 6868 |  | 5140 | UINT16 | 12584 | 12585 | AI | 1309 | R |  | kW
| kW Demand- Circuit 46 | 46 | 6869 |  | 5141 | UINT16 | 12586 | 12587 | AI | 1310 | R |  | kW
| kW Demand- Circuit 47 | 47 | 6870 |  | 5142 | UINT16 | 12588 | 12589 | AI | 1311 | R |  | kW
| kW Demand- Circuit 48 | 48 | 6871 |  | 5143 | UINT16 | 12590 | 12591 | AI | 1312 | R |  | kW
| kW Demand- Circuit 49 | 49 | 6872 |  | 5144 | UINT16 | 12592 | 12593 | AI | 1313 | R |  | kW
| kW Demand- Circuit 50 | 50 | 6873 |  | 5145 | UINT16 | 12594 | 12595 | AI | 1314 | R |  | kW
| kW Demand- Circuit 51 | 51 | 6874 |  | 5146 | UINT16 | 12596 | 12597 | AI | 1315 | R |  | kW
| kW Demand- Circuit 52 | 52 | 6875 |  | 5147 | UINT16 | 12598 | 12599 | AI | 1316 | R |  | kW
| kW Demand- Circuit 53 | 53 | 6876 |  | 5148 | UINT16 | 12600 | 12601 | AI | 1317 | R |  | kW
| kW Demand- Circuit 54 | 54 | 6877 |  | 5149 | UINT16 | 12602 | 12603 | AI | 1318 | R |  | kW
| kW Demand- Circuit 55 | 55 | 6878 |  | 5150 | UINT16 | 12604 | 12605 | AI | 1319 | R |  | kW
| kW Demand- Circuit 56 | 56 | 6879 |  | 5151 | UINT16 | 12606 | 12607 | AI | 1320 | R |  | kW
| kW Demand- Circuit 57 | 57 | 6880 |  | 5152 | UINT16 | 12608 | 12609 | AI | 1321 | R |  | kW
| kW Demand- Circuit 58 | 58 | 6881 |  | 5153 | UINT16 | 12610 | 12611 | AI | 1322 | R |  | kW
| kW Demand- Circuit 59 | 59 | 6882 |  | 5154 | UINT16 | 12612 | 12613 | AI | 1323 | R |  | kW
| kW Demand- Circuit 60 | 60 | 6883 |  | 5155 | UINT16 | 12614 | 12615 | AI | 1324 | R |  | kW
| kW Demand- Circuit 61 | 61 | 6884 |  | 5156 | UINT16 | 12616 | 12617 | AI | 1325 | R |  | kW
| kW Demand- Circuit 62 | 62 | 6885 |  | 5157 | UINT16 | 12618 | 12619 | AI | 1326 | R |  | kW
| kW Demand- Circuit 63 | 63 | 6886 |  | 5158 | UINT16 | 12620 | 12621 | AI | 1327 | R |  | kW
| kW Demand- Circuit 64 | 64 | 6887 |  | 5159 | UINT16 | 12622 | 12623 | AI | 1328 | R |  | kW
| kW Demand- Circuit 65 | 65 | 6888 |  | 5160 | UINT16 | 12624 | 12625 | AI | 1329 | R |  | kW
| kW Demand- Circuit 66 | 66 | 6889 |  | 5161 | UINT16 | 12626 | 12627 | AI | 1330 | R |  | kW
| kW Demand- Circuit 67 | 67 | 6890 |  | 5162 | UINT16 | 12628 | 12629 | AI | 1331 | R |  | kW
| kW Demand- Circuit 68 | 68 | 6891 |  | 5163 | UINT16 | 12630 | 12631 | AI | 1332 | R |  | kW
| kW Demand- Circuit 69 | 69 | 6892 |  | 5164 | UINT16 | 12632 | 12633 | AI | 1333 | R |  | kW
| kW Demand- Circuit 70 | 70 | 6893 |  | 5165 | UINT16 | 12634 | 12635 | AI | 1334 | R |  | kW
| kW Demand- Circuit 71 | 71 | 6894 |  | 5166 | UINT16 | 12636 | 12637 | AI | 1335 | R |  | kW
| kW Demand- Circuit 72 | 72 | 6895 |  | 5167 | UINT16 | 12638 | 12639 | AI | 1336 | R |  | kW
| kW Demand- Circuit 73 | 73 | 6896 |  | 5168 | UINT16 | 12640 | 12641 | AI | 1337 | R |  | kW
| kW Demand- Circuit 74 | 74 | 6897 |  | 5169 | UINT16 | 12642 | 12643 | AI | 1338 | R |  | kW
| kW Demand- Circuit 75 | 75 | 6898 |  | 5170 | UINT16 | 12644 | 12645 | AI | 1339 | R |  | kW
| kW Demand- Circuit 76 | 76 | 6899 |  | 5171 | UINT16 | 12646 | 12647 | AI | 1340 | R |  | kW
| kW Demand- Circuit 77 | 77 | 6900 |  | 5172 | UINT16 | 12648 | 12649 | AI | 1341 | R |  | kW
| kW Demand- Circuit 78 | 78 | 6901 |  | 5173 | UINT16 | 12650 | 12651 | AI | 1342 | R |  | kW
| kW Demand- Circuit 79 | 79 | 6902 |  | 5174 | UINT16 | 12652 | 12653 | AI | 1343 | R |  | kW
| kW Demand- Circuit 80 | 80 | 6903 |  | 5175 | UINT16 | 12654 | 12655 | AI | 1344 | R |  | kW
| kW Demand- Circuit 81 | 81 | 6904 |  | 5176 | UINT16 | 12656 | 12657 | AI | 1345 | R |  | kW
| kW Demand- Circuit 82 | 82 | 6905 |  | 5177 | UINT16 | 12658 | 12659 | AI | 1346 | R |  | kW
| kW Demand- Circuit 83 | 83 | 6906 |  | 5178 | UINT16 | 12660 | 12661 | AI | 1347 | R |  | kW
| kW Demand- Circuit 84 | 84 | 6907 |  | 5179 | UINT16 | 12662 | 12663 | AI | 1348 | R |  | kW
| kW Demand- Circuit 85 | 85 | 6908 |  | 5180 | UINT16 | 12664 | 12665 | AI | 1349 | R |  | kW
| kW Demand- Circuit 86 | 86 | 6909 |  | 5181 | UINT16 | 12666 | 12667 | AI | 1350 | R |  | kW
| kW Demand- Circuit 87 | 87 | 6910 |  | 5182 | UINT16 | 12668 | 12669 | AI | 1351 | R |  | kW
| kW Demand- Circuit 88 | 88 | 6911 |  | 5183 | UINT16 | 12670 | 12671 | AI | 1352 | R |  | kW
| kW Demand- Circuit 89 | 89 | 6912 |  | 5184 | UINT16 | 12672 | 12673 | AI | 1353 | R |  | kW
| kW Demand- Circuit 90 | 90 | 6913 |  | 5185 | UINT16 | 12674 | 12675 | AI | 1354 | R |  | kW
| kW Demand- Circuit 91 | 91 | 6914 |  | 5186 | UINT16 | 12676 | 12677 | AI | 1355 | R |  | kW
| kW Demand- Circuit 92 | 92 | 6915 |  | 5187 | UINT16 | 12678 | 12679 | AI | 1356 | R |  | kW
| kW Demand- Circuit 93 | 93 | 6916 |  | 5188 | UINT16 | 12680 | 12681 | AI | 1357 | R |  | kW
| kW Demand- Circuit 94 | 94 | 6917 |  | 5189 | UINT16 | 12682 | 12683 | AI | 1358 | R |  | kW
| kW Demand- Circuit 95 | 95 | 6918 |  | 5190 | UINT16 | 12684 | 12685 | AI | 1359 | R |  | kW
| kW Demand- Circuit 96 | 96 | 6919 |  | 5191 | UINT16 | 12686 | 12687 | AI | 1360 | R |  | kW
| Max Current Demand |  | 6920 | 7015 | Current | UINT16 | 12688 | 12879 | AI |  | R | NV | Amps
| Max Current Demand - Circuit 1 | 1 | 6920 |  | 5192 | UINT16 | 12688 | 12689 | AI | 1361 | R | NV | Amps
| Max Current Demand - Circuit 2 | 2 | 6921 |  | 5193 | UINT16 | 12690 | 12691 | AI | 1362 | R | NV | Amps
| Max Current Demand - Circuit 3 | 3 | 6922 |  | 5194 | UINT16 | 12692 | 12693 | AI | 1363 | R | NV | Amps
| Max Current Demand - Circuit 4 | 4 | 6923 |  | 5195 | UINT16 | 12694 | 12695 | AI | 1364 | R | NV | Amps
| Max Current Demand - Circuit 5 | 5 | 6924 |  | 5196 | UINT16 | 12696 | 12697 | AI | 1365 | R | NV | Amps
| Max Current Demand - Circuit 6 | 6 | 6925 |  | 5197 | UINT16 | 12698 | 12699 | AI | 1366 | R | NV | Amps
| Max Current Demand - Circuit 7 | 7 | 6926 |  | 5198 | UINT16 | 12700 | 12701 | AI | 1367 | R | NV | Amps
| Max Current Demand - Circuit 8 | 8 | 6927 |  | 5199 | UINT16 | 12702 | 12703 | AI | 1368 | R | NV | Amps
| Max Current Demand - Circuit 9 | 9 | 6928 |  | 5200 | UINT16 | 12704 | 12705 | AI | 1369 | R | NV | Amps
| Max Current Demand - Circuit 10 | 10 | 6929 |  | 5201 | UINT16 | 12706 | 12707 | AI | 1370 | R | NV | Amps
| Max Current Demand - Circuit 11 | 11 | 6930 |  | 5202 | UINT16 | 12708 | 12709 | AI | 1371 | R | NV | Amps
| Max Current Demand - Circuit 12 | 12 | 6931 |  | 5203 | UINT16 | 12710 | 12711 | AI | 1372 | R | NV | Amps
| Max Current Demand - Circuit 13 | 13 | 6932 |  | 5204 | UINT16 | 12712 | 12713 | AI | 1373 | R | NV | Amps
| Max Current Demand - Circuit 14 | 14 | 6933 |  | 5205 | UINT16 | 12714 | 12715 | AI | 1374 | R | NV | Amps
| Max Current Demand - Circuit 15 | 15 | 6934 |  | 5206 | UINT16 | 12716 | 12717 | AI | 1375 | R | NV | Amps
| Max Current Demand - Circuit 16 | 16 | 6935 |  | 5207 | UINT16 | 12718 | 12719 | AI | 1376 | R | NV | Amps
| Max Current Demand - Circuit 17 | 17 | 6936 |  | 5208 | UINT16 | 12720 | 12721 | AI | 1377 | R | NV | Amps
| Max Current Demand - Circuit 18 | 18 | 6937 |  | 5209 | UINT16 | 12722 | 12723 | AI | 1378 | R | NV | Amps
| Max Current Demand - Circuit 19 | 19 | 6938 |  | 5210 | UINT16 | 12724 | 12725 | AI | 1379 | R | NV | Amps
| Max Current Demand - Circuit 20 | 20 | 6939 |  | 5211 | UINT16 | 12726 | 12727 | AI | 1380 | R | NV | Amps
| Max Current Demand - Circuit 21 | 21 | 6940 |  | 5212 | UINT16 | 12728 | 12729 | AI | 1381 | R | NV | Amps
| Max Current Demand - Circuit 22 | 22 | 6941 |  | 5213 | UINT16 | 12730 | 12731 | AI | 1382 | R | NV | Amps
| Max Current Demand - Circuit 23 | 23 | 6942 |  | 5214 | UINT16 | 12732 | 12733 | AI | 1383 | R | NV | Amps
| Max Current Demand - Circuit 24 | 24 | 6943 |  | 5215 | UINT16 | 12734 | 12735 | AI | 1384 | R | NV | Amps
| Max Current Demand - Circuit 25 | 25 | 6944 |  | 5216 | UINT16 | 12736 | 12737 | AI | 1385 | R | NV | Amps
| Max Current Demand - Circuit 26 | 26 | 6945 |  | 5217 | UINT16 | 12738 | 12739 | AI | 1386 | R | NV | Amps
| Max Current Demand - Circuit 27 | 27 | 6946 |  | 5218 | UINT16 | 12740 | 12741 | AI | 1387 | R | NV | Amps
| Max Current Demand - Circuit 28 | 28 | 6947 |  | 5219 | UINT16 | 12742 | 12743 | AI | 1388 | R | NV | Amps
| Max Current Demand - Circuit 29 | 29 | 6948 |  | 5220 | UINT16 | 12744 | 12745 | AI | 1389 | R | NV | Amps
| Max Current Demand - Circuit 30 | 30 | 6949 |  | 5221 | UINT16 | 12746 | 12747 | AI | 1390 | R | NV | Amps
| Max Current Demand - Circuit 31 | 31 | 6950 |  | 5222 | UINT16 | 12748 | 12749 | AI | 1391 | R | NV | Amps
| Max Current Demand - Circuit 32 | 32 | 6951 |  | 5223 | UINT16 | 12750 | 12751 | AI | 1392 | R | NV | Amps
| Max Current Demand - Circuit 33 | 33 | 6952 |  | 5224 | UINT16 | 12752 | 12753 | AI | 1393 | R | NV | Amps
| Max Current Demand - Circuit 34 | 34 | 6953 |  | 5225 | UINT16 | 12754 | 12755 | AI | 1394 | R | NV | Amps
| Max Current Demand - Circuit 35 | 35 | 6954 |  | 5226 | UINT16 | 12756 | 12757 | AI | 1395 | R | NV | Amps
| Max Current Demand - Circuit 36 | 36 | 6955 |  | 5227 | UINT16 | 12758 | 12759 | AI | 1396 | R | NV | Amps
| Max Current Demand - Circuit 37 | 37 | 6956 |  | 5228 | UINT16 | 12760 | 12761 | AI | 1397 | R | NV | Amps
| Max Current Demand - Circuit 38 | 38 | 6957 |  | 5229 | UINT16 | 12762 | 12763 | AI | 1398 | R | NV | Amps
| Max Current Demand - Circuit 39 | 39 | 6958 |  | 5230 | UINT16 | 12764 | 12765 | AI | 1399 | R | NV | Amps
| Max Current Demand - Circuit 40 | 40 | 6959 |  | 5231 | UINT16 | 12766 | 12767 | AI | 1400 | R | NV | Amps
| Max Current Demand - Circuit 41 | 41 | 6960 |  | 5232 | UINT16 | 12768 | 12769 | AI | 1401 | R | NV | Amps
| Max Current Demand - Circuit 42 | 42 | 6961 |  | 5233 | UINT16 | 12770 | 12771 | AI | 1402 | R | NV | Amps
| Max Current Demand - Circuit 43 | 43 | 6962 |  | 5234 | UINT16 | 12772 | 12773 | AI | 1403 | R | NV | Amps
| Max Current Demand - Circuit 44 | 44 | 6963 |  | 5235 | UINT16 | 12774 | 12775 | AI | 1404 | R | NV | Amps
| Max Current Demand - Circuit 45 | 45 | 6964 |  | 5236 | UINT16 | 12776 | 12777 | AI | 1405 | R | NV | Amps
| Max Current Demand - Circuit 46 | 46 | 6965 |  | 5237 | UINT16 | 12778 | 12779 | AI | 1406 | R | NV | Amps
| Max Current Demand - Circuit 47 | 47 | 6966 |  | 5238 | UINT16 | 12780 | 12781 | AI | 1407 | R | NV | Amps
| Max Current Demand - Circuit 48 | 48 | 6967 |  | 5239 | UINT16 | 12782 | 12783 | AI | 1408 | R | NV | Amps
| Max Current Demand - Circuit 49 | 49 | 6968 |  | 5240 | UINT16 | 12784 | 12785 | AI | 1409 | R | NV | Amps
| Max Current Demand - Circuit 50 | 50 | 6969 |  | 5241 | UINT16 | 12786 | 12787 | AI | 1410 | R | NV | Amps
| Max Current Demand - Circuit 51 | 51 | 6970 |  | 5242 | UINT16 | 12788 | 12789 | AI | 1411 | R | NV | Amps
| Max Current Demand - Circuit 52 | 52 | 6971 |  | 5243 | UINT16 | 12790 | 12791 | AI | 1412 | R | NV | Amps
| Max Current Demand - Circuit 53 | 53 | 6972 |  | 5244 | UINT16 | 12792 | 12793 | AI | 1413 | R | NV | Amps
| Max Current Demand - Circuit 54 | 54 | 6973 |  | 5245 | UINT16 | 12794 | 12795 | AI | 1414 | R | NV | Amps
| Max Current Demand - Circuit 55 | 55 | 6974 |  | 5246 | UINT16 | 12796 | 12797 | AI | 1415 | R | NV | Amps
| Max Current Demand - Circuit 56 | 56 | 6975 |  | 5247 | UINT16 | 12798 | 12799 | AI | 1416 | R | NV | Amps
| Max Current Demand - Circuit 57 | 57 | 6976 |  | 5248 | UINT16 | 12800 | 12801 | AI | 1417 | R | NV | Amps
| Max Current Demand - Circuit 58 | 58 | 6977 |  | 5249 | UINT16 | 12802 | 12803 | AI | 1418 | R | NV | Amps
| Max Current Demand - Circuit 59 | 59 | 6978 |  | 5250 | UINT16 | 12804 | 12805 | AI | 1419 | R | NV | Amps
| Max Current Demand - Circuit 60 | 60 | 6979 |  | 5251 | UINT16 | 12806 | 12807 | AI | 1420 | R | NV | Amps
| Max Current Demand - Circuit 61 | 61 | 6980 |  | 5252 | UINT16 | 12808 | 12809 | AI | 1421 | R | NV | Amps
| Max Current Demand - Circuit 62 | 62 | 6981 |  | 5253 | UINT16 | 12810 | 12811 | AI | 1422 | R | NV | Amps
| Max Current Demand - Circuit 63 | 63 | 6982 |  | 5254 | UINT16 | 12812 | 12813 | AI | 1423 | R | NV | Amps
| Max Current Demand - Circuit 64 | 64 | 6983 |  | 5255 | UINT16 | 12814 | 12815 | AI | 1424 | R | NV | Amps
| Max Current Demand - Circuit 65 | 65 | 6984 |  | 5256 | UINT16 | 12816 | 12817 | AI | 1425 | R | NV | Amps
| Max Current Demand - Circuit 66 | 66 | 6985 |  | 5257 | UINT16 | 12818 | 12819 | AI | 1426 | R | NV | Amps
| Max Current Demand - Circuit 67 | 67 | 6986 |  | 5258 | UINT16 | 12820 | 12821 | AI | 1427 | R | NV | Amps
| Max Current Demand - Circuit 68 | 68 | 6987 |  | 5259 | UINT16 | 12822 | 12823 | AI | 1428 | R | NV | Amps
| Max Current Demand - Circuit 69 | 69 | 6988 |  | 5260 | UINT16 | 12824 | 12825 | AI | 1429 | R | NV | Amps
| Max Current Demand - Circuit 70 | 70 | 6989 |  | 5261 | UINT16 | 12826 | 12827 | AI | 1430 | R | NV | Amps
| Max Current Demand - Circuit 71 | 71 | 6990 |  | 5262 | UINT16 | 12828 | 12829 | AI | 1431 | R | NV | Amps
| Max Current Demand - Circuit 72 | 72 | 6991 |  | 5263 | UINT16 | 12830 | 12831 | AI | 1432 | R | NV | Amps
| Max Current Demand - Circuit 73 | 73 | 6992 |  | 5264 | UINT16 | 12832 | 12833 | AI | 1433 | R | NV | Amps
| Max Current Demand - Circuit 74 | 74 | 6993 |  | 5265 | UINT16 | 12834 | 12835 | AI | 1434 | R | NV | Amps
| Max Current Demand - Circuit 75 | 75 | 6994 |  | 5266 | UINT16 | 12836 | 12837 | AI | 1435 | R | NV | Amps
| Max Current Demand - Circuit 76 | 76 | 6995 |  | 5267 | UINT16 | 12838 | 12839 | AI | 1436 | R | NV | Amps
| Max Current Demand - Circuit 77 | 77 | 6996 |  | 5268 | UINT16 | 12840 | 12841 | AI | 1437 | R | NV | Amps
| Max Current Demand - Circuit 78 | 78 | 6997 |  | 5269 | UINT16 | 12842 | 12843 | AI | 1438 | R | NV | Amps
| Max Current Demand - Circuit 79 | 79 | 6998 |  | 5270 | UINT16 | 12844 | 12845 | AI | 1439 | R | NV | Amps
| Max Current Demand - Circuit 80 | 80 | 6999 |  | 5271 | UINT16 | 12846 | 12847 | AI | 1440 | R | NV | Amps
| Max Current Demand - Circuit 81 | 81 | 7000 |  | 5272 | UINT16 | 12848 | 12849 | AI | 1441 | R | NV | Amps
| Max Current Demand - Circuit 82 | 82 | 7001 |  | 5273 | UINT16 | 12850 | 12851 | AI | 1442 | R | NV | Amps
| Max Current Demand - Circuit 83 | 83 | 7002 |  | 5274 | UINT16 | 12852 | 12853 | AI | 1443 | R | NV | Amps
| Max Current Demand - Circuit 84 | 84 | 7003 |  | 5275 | UINT16 | 12854 | 12855 | AI | 1444 | R | NV | Amps
| Max Current Demand - Circuit 85 | 85 | 7004 |  | 5276 | UINT16 | 12856 | 12857 | AI | 1445 | R | NV | Amps
| Max Current Demand - Circuit 86 | 86 | 7005 |  | 5277 | UINT16 | 12858 | 12859 | AI | 1446 | R | NV | Amps
| Max Current Demand - Circuit 87 | 87 | 7006 |  | 5278 | UINT16 | 12860 | 12861 | AI | 1447 | R | NV | Amps
| Max Current Demand - Circuit 88 | 88 | 7007 |  | 5279 | UINT16 | 12862 | 12863 | AI | 1448 | R | NV | Amps
| Max Current Demand - Circuit 89 | 89 | 7008 |  | 5280 | UINT16 | 12864 | 12865 | AI | 1449 | R | NV | Amps
| Max Current Demand - Circuit 90 | 90 | 7009 |  | 5281 | UINT16 | 12866 | 12867 | AI | 1450 | R | NV | Amps
| Max Current Demand - Circuit 91 | 91 | 7010 |  | 5282 | UINT16 | 12868 | 12869 | AI | 1451 | R | NV | Amps
| Max Current Demand - Circuit 92 | 92 | 7011 |  | 5283 | UINT16 | 12870 | 12871 | AI | 1452 | R | NV | Amps
| Max Current Demand - Circuit 93 | 93 | 7012 |  | 5284 | UINT16 | 12872 | 12873 | AI | 1453 | R | NV | Amps
| Max Current Demand - Circuit 94 | 94 | 7013 |  | 5285 | UINT16 | 12874 | 12875 | AI | 1454 | R | NV | Amps
| Max Current Demand - Circuit 95 | 95 | 7014 |  | 5286 | UINT16 | 12876 | 12877 | AI | 1455 | R | NV | Amps
| Max Current Demand - Circuit 96 | 96 | 7015 |  | 5287 | UINT16 | 12878 | 12879 | AI | 1456 | R | NV | Amps
| Max kW Demand |  | 7016 | 7111 | Power | UINT16 | 12880 | 13071 | AI |  | R | NV | kW
| Max kW Demand - Circuit 1 | 1 | 7016 |  | 5096 | UINT16 | 12880 | 12881 | AI | 1457 | R | NV | kW
| Max kW Demand - Circuit 2 | 2 | 7017 |  | 5097 | UINT16 | 12882 | 12883 | AI | 1458 | R | NV | kW
| Max kW Demand - Circuit 3 | 3 | 7018 |  | 5098 | UINT16 | 12884 | 12885 | AI | 1459 | R | NV | kW
| Max kW Demand - Circuit 4 | 4 | 7019 |  | 5099 | UINT16 | 12886 | 12887 | AI | 1460 | R | NV | kW
| Max kW Demand - Circuit 5 | 5 | 7020 |  | 5100 | UINT16 | 12888 | 12889 | AI | 1461 | R | NV | kW
| Max kW Demand - Circuit 6 | 6 | 7021 |  | 5101 | UINT16 | 12890 | 12891 | AI | 1462 | R | NV | kW
| Max kW Demand - Circuit 7 | 7 | 7022 |  | 5102 | UINT16 | 12892 | 12893 | AI | 1463 | R | NV | kW
| Max kW Demand - Circuit 8 | 8 | 7023 |  | 5103 | UINT16 | 12894 | 12895 | AI | 1464 | R | NV | kW
| Max kW Demand - Circuit 9 | 9 | 7024 |  | 5104 | UINT16 | 12896 | 12897 | AI | 1465 | R | NV | kW
| Max kW Demand - Circuit 10 | 10 | 7025 |  | 5105 | UINT16 | 12898 | 12899 | AI | 1466 | R | NV | kW
| Max kW Demand - Circuit 11 | 11 | 7026 |  | 5106 | UINT16 | 12900 | 12901 | AI | 1467 | R | NV | kW
| Max kW Demand - Circuit 12 | 12 | 7027 |  | 5107 | UINT16 | 12902 | 12903 | AI | 1468 | R | NV | kW
| Max kW Demand - Circuit 13 | 13 | 7028 |  | 5108 | UINT16 | 12904 | 12905 | AI | 1469 | R | NV | kW
| Max kW Demand - Circuit 14 | 14 | 7029 |  | 5109 | UINT16 | 12906 | 12907 | AI | 1470 | R | NV | kW
| Max kW Demand - Circuit 15 | 15 | 7030 |  | 5110 | UINT16 | 12908 | 12909 | AI | 1471 | R | NV | kW
| Max kW Demand - Circuit 16 | 16 | 7031 |  | 5111 | UINT16 | 12910 | 12911 | AI | 1472 | R | NV | kW
| Max kW Demand - Circuit 17 | 17 | 7032 |  | 5112 | UINT16 | 12912 | 12913 | AI | 1473 | R | NV | kW
| Max kW Demand - Circuit 18 | 18 | 7033 |  | 5113 | UINT16 | 12914 | 12915 | AI | 1474 | R | NV | kW
| Max kW Demand - Circuit 19 | 19 | 7034 |  | 5114 | UINT16 | 12916 | 12917 | AI | 1475 | R | NV | kW
| Max kW Demand - Circuit 20 | 20 | 7035 |  | 5115 | UINT16 | 12918 | 12919 | AI | 1476 | R | NV | kW
| Max kW Demand - Circuit 21 | 21 | 7036 |  | 5116 | UINT16 | 12920 | 12921 | AI | 1477 | R | NV | kW
| Max kW Demand - Circuit 22 | 22 | 7037 |  | 5117 | UINT16 | 12922 | 12923 | AI | 1478 | R | NV | kW
| Max kW Demand - Circuit 23 | 23 | 7038 |  | 5118 | UINT16 | 12924 | 12925 | AI | 1479 | R | NV | kW
| Max kW Demand - Circuit 24 | 24 | 7039 |  | 5119 | UINT16 | 12926 | 12927 | AI | 1480 | R | NV | kW
| Max kW Demand - Circuit 25 | 25 | 7040 |  | 5120 | UINT16 | 12928 | 12929 | AI | 1481 | R | NV | kW
| Max kW Demand - Circuit 26 | 26 | 7041 |  | 5121 | UINT16 | 12930 | 12931 | AI | 1482 | R | NV | kW
| Max kW Demand - Circuit 27 | 27 | 7042 |  | 5122 | UINT16 | 12932 | 12933 | AI | 1483 | R | NV | kW
| Max kW Demand - Circuit 28 | 28 | 7043 |  | 5123 | UINT16 | 12934 | 12935 | AI | 1484 | R | NV | kW
| Max kW Demand - Circuit 29 | 29 | 7044 |  | 5124 | UINT16 | 12936 | 12937 | AI | 1485 | R | NV | kW
| Max kW Demand - Circuit 30 | 30 | 7045 |  | 5125 | UINT16 | 12938 | 12939 | AI | 1486 | R | NV | kW
| Max kW Demand - Circuit 31 | 31 | 7046 |  | 5126 | UINT16 | 12940 | 12941 | AI | 1487 | R | NV | kW
| Max kW Demand - Circuit 32 | 32 | 7047 |  | 5127 | UINT16 | 12942 | 12943 | AI | 1488 | R | NV | kW
| Max kW Demand - Circuit 33 | 33 | 7048 |  | 5128 | UINT16 | 12944 | 12945 | AI | 1489 | R | NV | kW
| Max kW Demand - Circuit 34 | 34 | 7049 |  | 5129 | UINT16 | 12946 | 12947 | AI | 1490 | R | NV | kW
| Max kW Demand - Circuit 35 | 35 | 7050 |  | 5130 | UINT16 | 12948 | 12949 | AI | 1491 | R | NV | kW
| Max kW Demand - Circuit 36 | 36 | 7051 |  | 5131 | UINT16 | 12950 | 12951 | AI | 1492 | R | NV | kW
| Max kW Demand - Circuit 37 | 37 | 7052 |  | 5132 | UINT16 | 12952 | 12953 | AI | 1493 | R | NV | kW
| Max kW Demand - Circuit 38 | 38 | 7053 |  | 5133 | UINT16 | 12954 | 12955 | AI | 1494 | R | NV | kW
| Max kW Demand - Circuit 39 | 39 | 7054 |  | 5134 | UINT16 | 12956 | 12957 | AI | 1495 | R | NV | kW
| Max kW Demand - Circuit 40 | 40 | 7055 |  | 5135 | UINT16 | 12958 | 12959 | AI | 1496 | R | NV | kW
| Max kW Demand - Circuit 41 | 41 | 7056 |  | 5136 | UINT16 | 12960 | 12961 | AI | 1497 | R | NV | kW
| Max kW Demand - Circuit 42 | 42 | 7057 |  | 5137 | UINT16 | 12962 | 12963 | AI | 1498 | R | NV | kW
| Max kW Demand - Circuit 43 | 43 | 7058 |  | 5138 | UINT16 | 12964 | 12965 | AI | 1499 | R | NV | kW
| Max kW Demand - Circuit 44 | 44 | 7059 |  | 5139 | UINT16 | 12966 | 12967 | AI | 1500 | R | NV | kW
| Max kW Demand - Circuit 45 | 45 | 7060 |  | 5140 | UINT16 | 12968 | 12969 | AI | 1501 | R | NV | kW
| Max kW Demand - Circuit 46 | 46 | 7061 |  | 5141 | UINT16 | 12970 | 12971 | AI | 1502 | R | NV | kW
| Max kW Demand - Circuit 47 | 47 | 7062 |  | 5142 | UINT16 | 12972 | 12973 | AI | 1503 | R | NV | kW
| Max kW Demand - Circuit 48 | 48 | 7063 |  | 5143 | UINT16 | 12974 | 12975 | AI | 1504 | R | NV | kW
| Max kW Demand - Circuit 49 | 49 | 7064 |  | 5144 | UINT16 | 12976 | 12977 | AI | 1505 | R | NV | kW
| Max kW Demand - Circuit 50 | 50 | 7065 |  | 5145 | UINT16 | 12978 | 12979 | AI | 1506 | R | NV | kW
| Max kW Demand - Circuit 51 | 51 | 7066 |  | 5146 | UINT16 | 12980 | 12981 | AI | 1507 | R | NV | kW
| Max kW Demand - Circuit 52 | 52 | 7067 |  | 5147 | UINT16 | 12982 | 12983 | AI | 1508 | R | NV | kW
| Max kW Demand - Circuit 53 | 53 | 7068 |  | 5148 | UINT16 | 12984 | 12985 | AI | 1509 | R | NV | kW
| Max kW Demand - Circuit 54 | 54 | 7069 |  | 5149 | UINT16 | 12986 | 12987 | AI | 1510 | R | NV | kW
| Max kW Demand - Circuit 55 | 55 | 7070 |  | 5150 | UINT16 | 12988 | 12989 | AI | 1511 | R | NV | kW
| Max kW Demand - Circuit 56 | 56 | 7071 |  | 5151 | UINT16 | 12990 | 12991 | AI | 1512 | R | NV | kW
| Max kW Demand - Circuit 57 | 57 | 7072 |  | 5152 | UINT16 | 12992 | 12993 | AI | 1513 | R | NV | kW
| Max kW Demand - Circuit 58 | 58 | 7073 |  | 5153 | UINT16 | 12994 | 12995 | AI | 1514 | R | NV | kW
| Max kW Demand - Circuit 59 | 59 | 7074 |  | 5154 | UINT16 | 12996 | 12997 | AI | 1515 | R | NV | kW
| Max kW Demand - Circuit 60 | 60 | 7075 |  | 5155 | UINT16 | 12998 | 12999 | AI | 1516 | R | NV | kW
| Max kW Demand - Circuit 61 | 61 | 7076 |  | 5156 | UINT16 | 13000 | 13001 | AI | 1517 | R | NV | kW
| Max kW Demand - Circuit 62 | 62 | 7077 |  | 5157 | UINT16 | 13002 | 13003 | AI | 1518 | R | NV | kW
| Max kW Demand - Circuit 63 | 63 | 7078 |  | 5158 | UINT16 | 13004 | 13005 | AI | 1519 | R | NV | kW
| Max kW Demand - Circuit 64 | 64 | 7079 |  | 5159 | UINT16 | 13006 | 13007 | AI | 1520 | R | NV | kW
| Max kW Demand - Circuit 65 | 65 | 7080 |  | 5160 | UINT16 | 13008 | 13009 | AI | 1521 | R | NV | kW
| Max kW Demand - Circuit 66 | 66 | 7081 |  | 5161 | UINT16 | 13010 | 13011 | AI | 1522 | R | NV | kW
| Max kW Demand - Circuit 67 | 67 | 7082 |  | 5162 | UINT16 | 13012 | 13013 | AI | 1523 | R | NV | kW
| Max kW Demand - Circuit 68 | 68 | 7083 |  | 5163 | UINT16 | 13014 | 13015 | AI | 1524 | R | NV | kW
| Max kW Demand - Circuit 69 | 69 | 7084 |  | 5164 | UINT16 | 13016 | 13017 | AI | 1525 | R | NV | kW
| Max kW Demand - Circuit 70 | 70 | 7085 |  | 5165 | UINT16 | 13018 | 13019 | AI | 1526 | R | NV | kW
| Max kW Demand - Circuit 71 | 71 | 7086 |  | 5166 | UINT16 | 13020 | 13021 | AI | 1527 | R | NV | kW
| Max kW Demand - Circuit 72 | 72 | 7087 |  | 5167 | UINT16 | 13022 | 13023 | AI | 1528 | R | NV | kW
| Max kW Demand - Circuit 73 | 73 | 7088 |  | 5168 | UINT16 | 13024 | 13025 | AI | 1529 | R | NV | kW
| Max kW Demand - Circuit 74 | 74 | 7089 |  | 5169 | UINT16 | 13026 | 13027 | AI | 1530 | R | NV | kW
| Max kW Demand - Circuit 75 | 75 | 7090 |  | 5170 | UINT16 | 13028 | 13029 | AI | 1531 | R | NV | kW
| Max kW Demand - Circuit 76 | 76 | 7091 |  | 5171 | UINT16 | 13030 | 13031 | AI | 1532 | R | NV | kW
| Max kW Demand - Circuit 77 | 77 | 7092 |  | 5172 | UINT16 | 13032 | 13033 | AI | 1533 | R | NV | kW
| Max kW Demand - Circuit 78 | 78 | 7093 |  | 5173 | UINT16 | 13034 | 13035 | AI | 1534 | R | NV | kW
| Max kW Demand - Circuit 79 | 79 | 7094 |  | 5174 | UINT16 | 13036 | 13037 | AI | 1535 | R | NV | kW
| Max kW Demand - Circuit 80 | 80 | 7095 |  | 5175 | UINT16 | 13038 | 13039 | AI | 1536 | R | NV | kW
| Max kW Demand - Circuit 81 | 81 | 7096 |  | 5176 | UINT16 | 13040 | 13041 | AI | 1537 | R | NV | kW
| Max kW Demand - Circuit 82 | 82 | 7097 |  | 5177 | UINT16 | 13042 | 13043 | AI | 1538 | R | NV | kW
| Max kW Demand - Circuit 83 | 83 | 7098 |  | 5178 | UINT16 | 13044 | 13045 | AI | 1539 | R | NV | kW
| Max kW Demand - Circuit 84 | 84 | 7099 |  | 5179 | UINT16 | 13046 | 13047 | AI | 1540 | R | NV | kW
| Max kW Demand - Circuit 85 | 85 | 7100 |  | 5180 | UINT16 | 13048 | 13049 | AI | 1541 | R | NV | kW
| Max kW Demand - Circuit 86 | 86 | 7101 |  | 5181 | UINT16 | 13050 | 13051 | AI | 1542 | R | NV | kW
| Max kW Demand - Circuit 87 | 87 | 7102 |  | 5182 | UINT16 | 13052 | 13053 | AI | 1543 | R | NV | kW
| Max kW Demand - Circuit 88 | 88 | 7103 |  | 5183 | UINT16 | 13054 | 13055 | AI | 1544 | R | NV | kW
| Max kW Demand - Circuit 89 | 89 | 7104 |  | 5184 | UINT16 | 13056 | 13057 | AI | 1545 | R | NV | kW
| Max kW Demand - Circuit 90 | 90 | 7105 |  | 5185 | UINT16 | 13058 | 13059 | AI | 1546 | R | NV | kW
| Max kW Demand - Circuit 91 | 91 | 7106 |  | 5186 | UINT16 | 13060 | 13061 | AI | 1547 | R | NV | kW
| Max kW Demand - Circuit 92 | 92 | 7107 |  | 5187 | UINT16 | 13062 | 13063 | AI | 1548 | R | NV | kW
| Max kW Demand - Circuit 93 | 93 | 7108 |  | 5188 | UINT16 | 13064 | 13065 | AI | 1549 | R | NV | kW
| Max kW Demand - Circuit 94 | 94 | 7109 |  | 5189 | UINT16 | 13066 | 13067 | AI | 1550 | R | NV | kW
| Max kW Demand - Circuit 95 | 95 | 7110 |  | 5190 | UINT16 | 13068 | 13069 | AI | 1551 | R | NV | kW
| Max kW Demand - Circuit 96 | 96 | 7111 |  | 5191 | UINT16 | 13070 | 13071 | AI | 1552 | R | NV | kW
| KWH Snapshot |  | 7112 | 7303 | Energy | UINT32 | 13072 | 13263 | AI |  | R |  | kWh
| KWH Snapshot - Circuit 1 | 1 | 7112 | 7113 | 5000 |  | 13072 | 13073 | AI | 1553 | R |  | kWh
| KWH Snapshot - Circuit 2 | 2 | 7114 | 7115 | 5001 |  | 13074 | 13075 | AI | 1554 | R |  | kWh
| KWH Snapshot - Circuit 3 | 3 | 7116 | 7117 | 5002 |  | 13076 | 13077 | AI | 1555 | R |  | kWh
| KWH Snapshot - Circuit 4 | 4 | 7118 | 7119 | 5003 |  | 13078 | 13079 | AI | 1556 | R |  | kWh
| KWH Snapshot - Circuit 5 | 5 | 7120 | 7121 | 5004 |  | 13080 | 13081 | AI | 1557 | R |  | kWh
| KWH Snapshot - Circuit 6 | 6 | 7122 | 7123 | 5005 |  | 13082 | 13083 | AI | 1558 | R |  | kWh
| KWH Snapshot - Circuit 7 | 7 | 7124 | 7125 | 5006 |  | 13084 | 13085 | AI | 1559 | R |  | kWh
| KWH Snapshot - Circuit 8 | 8 | 7126 | 7127 | 5007 |  | 13086 | 13087 | AI | 1560 | R |  | kWh
| KWH Snapshot - Circuit 9 | 9 | 7128 | 7129 | 5008 |  | 13088 | 13089 | AI | 1561 | R |  | kWh
| KWH Snapshot - Circuit 10 | 10 | 7130 | 7131 | 5009 |  | 13090 | 13091 | AI | 1562 | R |  | kWh
| KWH Snapshot - Circuit 11 | 11 | 7132 | 7133 | 5010 |  | 13092 | 13093 | AI | 1563 | R |  | kWh
| KWH Snapshot - Circuit 12 | 12 | 7134 | 7135 | 5011 |  | 13094 | 13095 | AI | 1564 | R |  | kWh
| KWH Snapshot - Circuit 13 | 13 | 7136 | 7137 | 5012 |  | 13096 | 13097 | AI | 1565 | R |  | kWh
| KWH Snapshot - Circuit 14 | 14 | 7138 | 7139 | 5013 |  | 13098 | 13099 | AI | 1566 | R |  | kWh
| KWH Snapshot - Circuit 15 | 15 | 7140 | 7141 | 5014 |  | 13100 | 13101 | AI | 1567 | R |  | kWh
| KWH Snapshot - Circuit 16 | 16 | 7142 | 7143 | 5015 |  | 13102 | 13103 | AI | 1568 | R |  | kWh
| KWH Snapshot - Circuit 17 | 17 | 7144 | 7145 | 5016 |  | 13104 | 13105 | AI | 1569 | R |  | kWh
| KWH Snapshot - Circuit 18 | 18 | 7146 | 7147 | 5017 |  | 13106 | 13107 | AI | 1570 | R |  | kWh
| KWH Snapshot - Circuit 19 | 19 | 7148 | 7149 | 5018 |  | 13108 | 13109 | AI | 1571 | R |  | kWh
| KWH Snapshot - Circuit 20 | 20 | 7150 | 7151 | 5019 |  | 13110 | 13111 | AI | 1572 | R |  | kWh
| KWH Snapshot - Circuit 21 | 21 | 7152 | 7153 | 5020 |  | 13112 | 13113 | AI | 1573 | R |  | kWh
| KWH Snapshot - Circuit 22 | 22 | 7154 | 7155 | 5021 |  | 13114 | 13115 | AI | 1574 | R |  | kWh
| KWH Snapshot - Circuit 23 | 23 | 7156 | 7157 | 5022 |  | 13116 | 13117 | AI | 1575 | R |  | kWh
| KWH Snapshot - Circuit 24 | 24 | 7158 | 7159 | 5023 |  | 13118 | 13119 | AI | 1576 | R |  | kWh
| KWH Snapshot - Circuit 25 | 25 | 7160 | 7161 | 5024 |  | 13120 | 13121 | AI | 1577 | R |  | kWh
| KWH Snapshot - Circuit 26 | 26 | 7162 | 7163 | 5025 |  | 13122 | 13123 | AI | 1578 | R |  | kWh
| KWH Snapshot - Circuit 27 | 27 | 7164 | 7165 | 5026 |  | 13124 | 13125 | AI | 1579 | R |  | kWh
| KWH Snapshot - Circuit 28 | 28 | 7166 | 7167 | 5027 |  | 13126 | 13127 | AI | 1580 | R |  | kWh
| KWH Snapshot - Circuit 29 | 29 | 7168 | 7169 | 5028 |  | 13128 | 13129 | AI | 1581 | R |  | kWh
| KWH Snapshot - Circuit 30 | 30 | 7170 | 7171 | 5029 |  | 13130 | 13131 | AI | 1582 | R |  | kWh
| KWH Snapshot - Circuit 31 | 31 | 7172 | 7173 | 5030 |  | 13132 | 13133 | AI | 1583 | R |  | kWh
| KWH Snapshot - Circuit 32 | 32 | 7174 | 7175 | 5031 |  | 13134 | 13135 | AI | 1584 | R |  | kWh
| KWH Snapshot - Circuit 33 | 33 | 7176 | 7177 | 5032 |  | 13136 | 13137 | AI | 1585 | R |  | kWh
| KWH Snapshot - Circuit 34 | 34 | 7178 | 7179 | 5033 |  | 13138 | 13139 | AI | 1586 | R |  | kWh
| KWH Snapshot - Circuit 35 | 35 | 7180 | 7181 | 5034 |  | 13140 | 13141 | AI | 1587 | R |  | kWh
| KWH Snapshot - Circuit 36 | 36 | 7182 | 7183 | 5035 |  | 13142 | 13143 | AI | 1588 | R |  | kWh
| KWH Snapshot - Circuit 37 | 37 | 7184 | 7185 | 5036 |  | 13144 | 13145 | AI | 1589 | R |  | kWh
| KWH Snapshot - Circuit 38 | 38 | 7186 | 7187 | 5037 |  | 13146 | 13147 | AI | 1590 | R |  | kWh
| KWH Snapshot - Circuit 39 | 39 | 7188 | 7189 | 5038 |  | 13148 | 13149 | AI | 1591 | R |  | kWh
| KWH Snapshot - Circuit 40 | 40 | 7190 | 7191 | 5039 |  | 13150 | 13151 | AI | 1592 | R |  | kWh
| KWH Snapshot - Circuit 41 | 41 | 7192 | 7193 | 5040 |  | 13152 | 13153 | AI | 1593 | R |  | kWh
| KWH Snapshot - Circuit 42 | 42 | 7194 | 7195 | 5041 |  | 13154 | 13155 | AI | 1594 | R |  | kWh
| KWH Snapshot - Circuit 43 | 43 | 7196 | 7197 | 5042 |  | 13156 | 13157 | AI | 1595 | R |  | kWh
| KWH Snapshot - Circuit 44 | 44 | 7198 | 7199 | 5043 |  | 13158 | 13159 | AI | 1596 | R |  | kWh
| KWH Snapshot - Circuit 45 | 45 | 7200 | 7201 | 5044 |  | 13160 | 13161 | AI | 1597 | R |  | kWh
| KWH Snapshot - Circuit 46 | 46 | 7202 | 7203 | 5045 |  | 13162 | 13163 | AI | 1598 | R |  | kWh
| KWH Snapshot - Circuit 47 | 47 | 7204 | 7205 | 5046 |  | 13164 | 13165 | AI | 1599 | R |  | kWh
| KWH Snapshot - Circuit 48 | 48 | 7206 | 7207 | 5047 |  | 13166 | 13167 | AI | 1600 | R |  | kWh
| KWH Snapshot - Circuit 49 | 49 | 7208 | 7209 | 5048 |  | 13168 | 13169 | AI | 1601 | R |  | kWh
| KWH Snapshot - Circuit 50 | 50 | 7210 | 7211 | 5049 |  | 13170 | 13171 | AI | 1602 | R |  | kWh
| KWH Snapshot - Circuit 51 | 51 | 7212 | 7213 | 5050 |  | 13172 | 13173 | AI | 1603 | R |  | kWh
| KWH Snapshot - Circuit 52 | 52 | 7214 | 7215 | 5051 |  | 13174 | 13175 | AI | 1604 | R |  | kWh
| KWH Snapshot - Circuit 53 | 53 | 7216 | 7217 | 5052 |  | 13176 | 13177 | AI | 1605 | R |  | kWh
| KWH Snapshot - Circuit 54 | 54 | 7218 | 7219 | 5053 |  | 13178 | 13179 | AI | 1606 | R |  | kWh
| KWH Snapshot - Circuit 55 | 55 | 7220 | 7221 | 5054 |  | 13180 | 13181 | AI | 1607 | R |  | kWh
| KWH Snapshot - Circuit 56 | 56 | 7222 | 7223 | 5055 |  | 13182 | 13183 | AI | 1608 | R |  | kWh
| KWH Snapshot - Circuit 57 | 57 | 7224 | 7225 | 5056 |  | 13184 | 13185 | AI | 1609 | R |  | kWh
| KWH Snapshot - Circuit 58 | 58 | 7226 | 7227 | 5057 |  | 13186 | 13187 | AI | 1610 | R |  | kWh
| KWH Snapshot - Circuit 59 | 59 | 7228 | 7229 | 5058 |  | 13188 | 13189 | AI | 1611 | R |  | kWh
| KWH Snapshot - Circuit 60 | 60 | 7230 | 7231 | 5059 |  | 13190 | 13191 | AI | 1612 | R |  | kWh
| KWH Snapshot - Circuit 61 | 61 | 7232 | 7233 | 5060 |  | 13192 | 13193 | AI | 1613 | R |  | kWh
| KWH Snapshot - Circuit 62 | 62 | 7234 | 7235 | 5061 |  | 13194 | 13195 | AI | 1614 | R |  | kWh
| KWH Snapshot - Circuit 63 | 63 | 7236 | 7237 | 5062 |  | 13196 | 13197 | AI | 1615 | R |  | kWh
| KWH Snapshot - Circuit 64 | 64 | 7238 | 7239 | 5063 |  | 13198 | 13199 | AI | 1616 | R |  | kWh
| KWH Snapshot - Circuit 65 | 65 | 7240 | 7241 | 5064 |  | 13200 | 13201 | AI | 1617 | R |  | kWh
| KWH Snapshot - Circuit 66 | 66 | 7242 | 7243 | 5065 |  | 13202 | 13203 | AI | 1618 | R |  | kWh
| KWH Snapshot - Circuit 67 | 67 | 7244 | 7245 | 5066 |  | 13204 | 13205 | AI | 1619 | R |  | kWh
| KWH Snapshot - Circuit 68 | 68 | 7246 | 7247 | 5067 |  | 13206 | 13207 | AI | 1620 | R |  | kWh
| KWH Snapshot - Circuit 69 | 69 | 7248 | 7249 | 5068 |  | 13208 | 13209 | AI | 1621 | R |  | kWh
| KWH Snapshot - Circuit 70 | 70 | 7250 | 7251 | 5069 |  | 13210 | 13211 | AI | 1622 | R |  | kWh
| KWH Snapshot - Circuit 71 | 71 | 7252 | 7253 | 5070 |  | 13212 | 13213 | AI | 1623 | R |  | kWh
| KWH Snapshot - Circuit 72 | 72 | 7254 | 7255 | 5071 |  | 13214 | 13215 | AI | 1624 | R |  | kWh
| KWH Snapshot - Circuit 73 | 73 | 7256 | 7257 | 5072 |  | 13216 | 13217 | AI | 1625 | R |  | kWh
| KWH Snapshot - Circuit 74 | 74 | 7258 | 7259 | 5073 |  | 13218 | 13219 | AI | 1626 | R |  | kWh
| KWH Snapshot - Circuit 75 | 75 | 7260 | 7261 | 5074 |  | 13220 | 13221 | AI | 1627 | R |  | kWh
| KWH Snapshot - Circuit 76 | 76 | 7262 | 7263 | 5075 |  | 13222 | 13223 | AI | 1628 | R |  | kWh
| KWH Snapshot - Circuit 77 | 77 | 7264 | 7265 | 5076 |  | 13224 | 13225 | AI | 1629 | R |  | kWh
| KWH Snapshot - Circuit 78 | 78 | 7266 | 7267 | 5077 |  | 13226 | 13227 | AI | 1630 | R |  | kWh
| KWH Snapshot - Circuit 79 | 79 | 7268 | 7269 | 5078 |  | 13228 | 13229 | AI | 1631 | R |  | kWh
| KWH Snapshot - Circuit 80 | 80 | 7270 | 7271 | 5079 |  | 13230 | 13231 | AI | 1632 | R |  | kWh
| KWH Snapshot - Circuit 81 | 81 | 7272 | 7273 | 5080 |  | 13232 | 13233 | AI | 1633 | R |  | kWh
| KWH Snapshot - Circuit 82 | 82 | 7274 | 7275 | 5081 |  | 13234 | 13235 | AI | 1634 | R |  | kWh
| KWH Snapshot - Circuit 83 | 83 | 7276 | 7277 | 5082 |  | 13236 | 13237 | AI | 1635 | R |  | kWh
| KWH Snapshot - Circuit 84 | 84 | 7278 | 7279 | 5083 |  | 13238 | 13239 | AI | 1636 | R |  | kWh
| KWH Snapshot - Circuit 85 | 85 | 7280 | 7281 | 5084 |  | 13240 | 13241 | AI | 1637 | R |  | kWh
| KWH Snapshot - Circuit 86 | 86 | 7282 | 7283 | 5085 |  | 13242 | 13243 | AI | 1638 | R |  | kWh
| KWH Snapshot - Circuit 87 | 87 | 7284 | 7285 | 5086 |  | 13244 | 13245 | AI | 1639 | R |  | kWh
| KWH Snapshot - Circuit 88 | 88 | 7286 | 7287 | 5087 |  | 13246 | 13247 | AI | 1640 | R |  | kWh
| KWH Snapshot - Circuit 89 | 89 | 7288 | 7289 | 5088 |  | 13248 | 13249 | AI | 1641 | R |  | kWh
| KWH Snapshot - Circuit 90 | 90 | 7290 | 7291 | 5089 |  | 13250 | 13251 | AI | 1642 | R |  | kWh
| KWH Snapshot - Circuit 91 | 91 | 7292 | 7293 | 5090 |  | 13252 | 13253 | AI | 1643 | R |  | kWh
| KWH Snapshot - Circuit 92 | 92 | 7294 | 7295 | 5091 |  | 13254 | 13255 | AI | 1644 | R |  | kWh
| KWH Snapshot - Circuit 93 | 93 | 7296 | 7297 | 5092 |  | 13256 | 13257 | AI | 1645 | R |  | kWh
| KWH Snapshot - Circuit 94 | 94 | 7298 | 7299 | 5093 |  | 13258 | 13259 | AI | 1646 | R |  | kWh
| KWH Snapshot - Circuit 95 | 95 | 7300 | 7301 | 5094 |  | 13260 | 13261 | AI | 1647 | R |  | kWh
| KWH Snapshot - Circuit 96 | 96 | 7302 | 7303 | 5095 |  | 13262 | 13263 | AI | 1648 | R |  | kWh
| Crest Factor |  | 7304 | 7399 | -3 | UINT16 | 13264 | 13455 | AI |  | R
| Crest Factor - Circuit 1 | 1 | 7304 |  | -3 | UINT16 | 13264 | 13265 | AI | 1649 | R
| Crest Factor - Circuit 2 | 2 | 7305 |  | -3 | UINT16 | 13266 | 13267 | AI | 1650 | R
| Crest Factor - Circuit 3 | 3 | 7306 |  | -3 | UINT16 | 13268 | 13269 | AI | 1651 | R
| Crest Factor - Circuit 4 | 4 | 7307 |  | -3 | UINT16 | 13270 | 13271 | AI | 1652 | R
| Crest Factor - Circuit 5 | 5 | 7308 |  | -3 | UINT16 | 13272 | 13273 | AI | 1653 | R
| Crest Factor - Circuit 6 | 6 | 7309 |  | -3 | UINT16 | 13274 | 13275 | AI | 1654 | R
| Crest Factor - Circuit 7 | 7 | 7310 |  | -3 | UINT16 | 13276 | 13277 | AI | 1655 | R
| Crest Factor - Circuit 8 | 8 | 7311 |  | -3 | UINT16 | 13278 | 13279 | AI | 1656 | R
| Crest Factor - Circuit 9 | 9 | 7312 |  | -3 | UINT16 | 13280 | 13281 | AI | 1657 | R
| Crest Factor - Circuit 10 | 10 | 7313 |  | -3 | UINT16 | 13282 | 13283 | AI | 1658 | R
| Crest Factor - Circuit 11 | 11 | 7314 |  | -3 | UINT16 | 13284 | 13285 | AI | 1659 | R
| Crest Factor - Circuit 12 | 12 | 7315 |  | -3 | UINT16 | 13286 | 13287 | AI | 1660 | R
| Crest Factor - Circuit 13 | 13 | 7316 |  | -3 | UINT16 | 13288 | 13289 | AI | 1661 | R
| Crest Factor - Circuit 14 | 14 | 7317 |  | -3 | UINT16 | 13290 | 13291 | AI | 1662 | R
| Crest Factor - Circuit 15 | 15 | 7318 |  | -3 | UINT16 | 13292 | 13293 | AI | 1663 | R
| Crest Factor - Circuit 16 | 16 | 7319 |  | -3 | UINT16 | 13294 | 13295 | AI | 1664 | R
| Crest Factor - Circuit 17 | 17 | 7320 |  | -3 | UINT16 | 13296 | 13297 | AI | 1665 | R
| Crest Factor - Circuit 18 | 18 | 7321 |  | -3 | UINT16 | 13298 | 13299 | AI | 1666 | R
| Crest Factor - Circuit 19 | 19 | 7322 |  | -3 | UINT16 | 13300 | 13301 | AI | 1667 | R
| Crest Factor - Circuit 20 | 20 | 7323 |  | -3 | UINT16 | 13302 | 13303 | AI | 1668 | R
| Crest Factor - Circuit 21 | 21 | 7324 |  | -3 | UINT16 | 13304 | 13305 | AI | 1669 | R
| Crest Factor - Circuit 22 | 22 | 7325 |  | -3 | UINT16 | 13306 | 13307 | AI | 1670 | R
| Crest Factor - Circuit 23 | 23 | 7326 |  | -3 | UINT16 | 13308 | 13309 | AI | 1671 | R
| Crest Factor - Circuit 24 | 24 | 7327 |  | -3 | UINT16 | 13310 | 13311 | AI | 1672 | R
| Crest Factor - Circuit 25 | 25 | 7328 |  | -3 | UINT16 | 13312 | 13313 | AI | 1673 | R
| Crest Factor - Circuit 26 | 26 | 7329 |  | -3 | UINT16 | 13314 | 13315 | AI | 1674 | R
| Crest Factor - Circuit 27 | 27 | 7330 |  | -3 | UINT16 | 13316 | 13317 | AI | 1675 | R
| Crest Factor - Circuit 28 | 28 | 7331 |  | -3 | UINT16 | 13318 | 13319 | AI | 1676 | R
| Crest Factor - Circuit 29 | 29 | 7332 |  | -3 | UINT16 | 13320 | 13321 | AI | 1677 | R
| Crest Factor - Circuit 30 | 30 | 7333 |  | -3 | UINT16 | 13322 | 13323 | AI | 1678 | R
| Crest Factor - Circuit 31 | 31 | 7334 |  | -3 | UINT16 | 13324 | 13325 | AI | 1679 | R
| Crest Factor - Circuit 32 | 32 | 7335 |  | -3 | UINT16 | 13326 | 13327 | AI | 1680 | R
| Crest Factor - Circuit 33 | 33 | 7336 |  | -3 | UINT16 | 13328 | 13329 | AI | 1681 | R
| Crest Factor - Circuit 34 | 34 | 7337 |  | -3 | UINT16 | 13330 | 13331 | AI | 1682 | R
| Crest Factor - Circuit 35 | 35 | 7338 |  | -3 | UINT16 | 13332 | 13333 | AI | 1683 | R
| Crest Factor - Circuit 36 | 36 | 7339 |  | -3 | UINT16 | 13334 | 13335 | AI | 1684 | R
| Crest Factor - Circuit 37 | 37 | 7340 |  | -3 | UINT16 | 13336 | 13337 | AI | 1685 | R
| Crest Factor - Circuit 38 | 38 | 7341 |  | -3 | UINT16 | 13338 | 13339 | AI | 1686 | R
| Crest Factor - Circuit 39 | 39 | 7342 |  | -3 | UINT16 | 13340 | 13341 | AI | 1687 | R
| Crest Factor - Circuit 40 | 40 | 7343 |  | -3 | UINT16 | 13342 | 13343 | AI | 1688 | R
| Crest Factor - Circuit 41 | 41 | 7344 |  | -3 | UINT16 | 13344 | 13345 | AI | 1689 | R
| Crest Factor - Circuit 42 | 42 | 7345 |  | -3 | UINT16 | 13346 | 13347 | AI | 1690 | R
| Crest Factor - Circuit 43 | 43 | 7346 |  | -3 | UINT16 | 13348 | 13349 | AI | 1691 | R
| Crest Factor - Circuit 44 | 44 | 7347 |  | -3 | UINT16 | 13350 | 13351 | AI | 1692 | R
| Crest Factor - Circuit 45 | 45 | 7348 |  | -3 | UINT16 | 13352 | 13353 | AI | 1693 | R
| Crest Factor - Circuit 46 | 46 | 7349 |  | -3 | UINT16 | 13354 | 13355 | AI | 1694 | R
| Crest Factor - Circuit 47 | 47 | 7350 |  | -3 | UINT16 | 13356 | 13357 | AI | 1695 | R
| Crest Factor - Circuit 48 | 48 | 7351 |  | -3 | UINT16 | 13358 | 13359 | AI | 1696 | R
| Crest Factor - Circuit 49 | 49 | 7352 |  | -3 | UINT16 | 13360 | 13361 | AI | 1697 | R
| Crest Factor - Circuit 50 | 50 | 7353 |  | -3 | UINT16 | 13362 | 13363 | AI | 1698 | R
| Crest Factor - Circuit 51 | 51 | 7354 |  | -3 | UINT16 | 13364 | 13365 | AI | 1699 | R
| Crest Factor - Circuit 52 | 52 | 7355 |  | -3 | UINT16 | 13366 | 13367 | AI | 1700 | R
| Crest Factor - Circuit 53 | 53 | 7356 |  | -3 | UINT16 | 13368 | 13369 | AI | 1701 | R
| Crest Factor - Circuit 54 | 54 | 7357 |  | -3 | UINT16 | 13370 | 13371 | AI | 1702 | R
| Crest Factor - Circuit 55 | 55 | 7358 |  | -3 | UINT16 | 13372 | 13373 | AI | 1703 | R
| Crest Factor - Circuit 56 | 56 | 7359 |  | -3 | UINT16 | 13374 | 13375 | AI | 1704 | R
| Crest Factor - Circuit 57 | 57 | 7360 |  | -3 | UINT16 | 13376 | 13377 | AI | 1705 | R
| Crest Factor - Circuit 58 | 58 | 7361 |  | -3 | UINT16 | 13378 | 13379 | AI | 1706 | R
| Crest Factor - Circuit 59 | 59 | 7362 |  | -3 | UINT16 | 13380 | 13381 | AI | 1707 | R
| Crest Factor - Circuit 60 | 60 | 7363 |  | -3 | UINT16 | 13382 | 13383 | AI | 1708 | R
| Crest Factor - Circuit 61 | 61 | 7364 |  | -3 | UINT16 | 13384 | 13385 | AI | 1709 | R
| Crest Factor - Circuit 62 | 62 | 7365 |  | -3 | UINT16 | 13386 | 13387 | AI | 1710 | R
| Crest Factor - Circuit 63 | 63 | 7366 |  | -3 | UINT16 | 13388 | 13389 | AI | 1711 | R
| Crest Factor - Circuit 64 | 64 | 7367 |  | -3 | UINT16 | 13390 | 13391 | AI | 1712 | R
| Crest Factor - Circuit 65 | 65 | 7368 |  | -3 | UINT16 | 13392 | 13393 | AI | 1713 | R
| Crest Factor - Circuit 66 | 66 | 7369 |  | -3 | UINT16 | 13394 | 13395 | AI | 1714 | R
| Crest Factor - Circuit 67 | 67 | 7370 |  | -3 | UINT16 | 13396 | 13397 | AI | 1715 | R
| Crest Factor - Circuit 68 | 68 | 7371 |  | -3 | UINT16 | 13398 | 13399 | AI | 1716 | R
| Crest Factor - Circuit 69 | 69 | 7372 |  | -3 | UINT16 | 13400 | 13401 | AI | 1717 | R
| Crest Factor - Circuit 70 | 70 | 7373 |  | -3 | UINT16 | 13402 | 13403 | AI | 1718 | R
| Crest Factor - Circuit 71 | 71 | 7374 |  | -3 | UINT16 | 13404 | 13405 | AI | 1719 | R
| Crest Factor - Circuit 72 | 72 | 7375 |  | -3 | UINT16 | 13406 | 13407 | AI | 1720 | R
| Crest Factor - Circuit 73 | 73 | 7376 |  | -3 | UINT16 | 13408 | 13409 | AI | 1721 | R
| Crest Factor - Circuit 74 | 74 | 7377 |  | -3 | UINT16 | 13410 | 13411 | AI | 1722 | R
| Crest Factor - Circuit 75 | 75 | 7378 |  | -3 | UINT16 | 13412 | 13413 | AI | 1723 | R
| Crest Factor - Circuit 76 | 76 | 7379 |  | -3 | UINT16 | 13414 | 13415 | AI | 1724 | R
| Crest Factor - Circuit 77 | 77 | 7380 |  | -3 | UINT16 | 13416 | 13417 | AI | 1725 | R
| Crest Factor - Circuit 78 | 78 | 7381 |  | -3 | UINT16 | 13418 | 13419 | AI | 1726 | R
| Crest Factor - Circuit 79 | 79 | 7382 |  | -3 | UINT16 | 13420 | 13421 | AI | 1727 | R
| Crest Factor - Circuit 80 | 80 | 7383 |  | -3 | UINT16 | 13422 | 13423 | AI | 1728 | R
| Crest Factor - Circuit 81 | 81 | 7384 |  | -3 | UINT16 | 13424 | 13425 | AI | 1729 | R
| Crest Factor - Circuit 82 | 82 | 7385 |  | -3 | UINT16 | 13426 | 13427 | AI | 1730 | R
| Crest Factor - Circuit 83 | 83 | 7386 |  | -3 | UINT16 | 13428 | 13429 | AI | 1731 | R
| Crest Factor - Circuit 84 | 84 | 7387 |  | -3 | UINT16 | 13430 | 13431 | AI | 1732 | R
| Crest Factor - Circuit 85 | 85 | 7388 |  | -3 | UINT16 | 13432 | 13433 | AI | 1733 | R
| Crest Factor - Circuit 86 | 86 | 7389 |  | -3 | UINT16 | 13434 | 13435 | AI | 1734 | R
| Crest Factor - Circuit 87 | 87 | 7390 |  | -3 | UINT16 | 13436 | 13437 | AI | 1735 | R
| Crest Factor - Circuit 88 | 88 | 7391 |  | -3 | UINT16 | 13438 | 13439 | AI | 1736 | R
| Crest Factor - Circuit 89 | 89 | 7392 |  | -3 | UINT16 | 13440 | 13441 | AI | 1737 | R
| Crest Factor - Circuit 90 | 90 | 7393 |  | -3 | UINT16 | 13442 | 13443 | AI | 1738 | R
| Crest Factor - Circuit 91 | 91 | 7394 |  | -3 | UINT16 | 13444 | 13445 | AI | 1739 | R
| Crest Factor - Circuit 92 | 92 | 7395 |  | -3 | UINT16 | 13446 | 13447 | AI | 1740 | R
| Crest Factor - Circuit 93 | 93 | 7396 |  | -3 | UINT16 | 13448 | 13449 | AI | 1741 | R
| Crest Factor - Circuit 94 | 94 | 7397 |  | -3 | UINT16 | 13450 | 13451 | AI | 1742 | R
| Crest Factor - Circuit 95 | 95 | 7398 |  | -3 | UINT16 | 13452 | 13453 | AI | 1743 | R
| Crest Factor - Circuit 96 | 96 | 7399 |  | -3 | UINT16 | 13454 | 13455 | AI | 1744 | R
| Temperature |  | 7400 | 7495 | -2 | INT16 | 13456 | 13647 |  |  | R |  |  |  | Not Yet Supported
| Temperature - Circuit 1 | 1 | 7400 |  | -2 | UINT16 | 13456 | 13457 |  |  | R
| Temperature - Circuit 2 | 2 | 7401 |  | -2 | UINT16 | 13458 | 13459 |  |  | R
| Temperature - Circuit 3 | 3 | 7402 |  | -2 | UINT16 | 13460 | 13461 |  |  | R
| Temperature - Circuit 4 | 4 | 7403 |  | -2 | UINT16 | 13462 | 13463 |  |  | R
| Temperature - Circuit 5 | 5 | 7404 |  | -2 | UINT16 | 13464 | 13465 |  |  | R
| Temperature - Circuit 6 | 6 | 7405 |  | -2 | UINT16 | 13466 | 13467 |  |  | R
| Temperature - Circuit 7 | 7 | 7406 |  | -2 | UINT16 | 13468 | 13469 |  |  | R
| Temperature - Circuit 8 | 8 | 7407 |  | -2 | UINT16 | 13470 | 13471 |  |  | R
| Temperature - Circuit 9 | 9 | 7408 |  | -2 | UINT16 | 13472 | 13473 |  |  | R
| Temperature - Circuit 10 | 10 | 7409 |  | -2 | UINT16 | 13474 | 13475 |  |  | R
| Temperature - Circuit 11 | 11 | 7410 |  | -2 | UINT16 | 13476 | 13477 |  |  | R
| Temperature - Circuit 12 | 12 | 7411 |  | -2 | UINT16 | 13478 | 13479 |  |  | R
| Temperature - Circuit 13 | 13 | 7412 |  | -2 | UINT16 | 13480 | 13481 |  |  | R
| Temperature - Circuit 14 | 14 | 7413 |  | -2 | UINT16 | 13482 | 13483 |  |  | R
| Temperature - Circuit 15 | 15 | 7414 |  | -2 | UINT16 | 13484 | 13485 |  |  | R
| Temperature - Circuit 16 | 16 | 7415 |  | -2 | UINT16 | 13486 | 13487 |  |  | R
| Temperature - Circuit 17 | 17 | 7416 |  | -2 | UINT16 | 13488 | 13489 |  |  | R
| Temperature - Circuit 18 | 18 | 7417 |  | -2 | UINT16 | 13490 | 13491 |  |  | R
| Temperature - Circuit 19 | 19 | 7418 |  | -2 | UINT16 | 13492 | 13493 |  |  | R
| Temperature - Circuit 20 | 20 | 7419 |  | -2 | UINT16 | 13494 | 13495 |  |  | R
| Temperature - Circuit 21 | 21 | 7420 |  | -2 | UINT16 | 13496 | 13497 |  |  | R
| Temperature - Circuit 22 | 22 | 7421 |  | -2 | UINT16 | 13498 | 13499 |  |  | R
| Temperature - Circuit 23 | 23 | 7422 |  | -2 | UINT16 | 13500 | 13501 |  |  | R
| Temperature - Circuit 24 | 24 | 7423 |  | -2 | UINT16 | 13502 | 13503 |  |  | R
| Temperature - Circuit 25 | 25 | 7424 |  | -2 | UINT16 | 13504 | 13505 |  |  | R
| Temperature - Circuit 26 | 26 | 7425 |  | -2 | UINT16 | 13506 | 13507 |  |  | R
| Temperature - Circuit 27 | 27 | 7426 |  | -2 | UINT16 | 13508 | 13509 |  |  | R
| Temperature - Circuit 28 | 28 | 7427 |  | -2 | UINT16 | 13510 | 13511 |  |  | R
| Temperature - Circuit 29 | 29 | 7428 |  | -2 | UINT16 | 13512 | 13513 |  |  | R
| Temperature - Circuit 30 | 30 | 7429 |  | -2 | UINT16 | 13514 | 13515 |  |  | R
| Temperature - Circuit 31 | 31 | 7430 |  | -2 | UINT16 | 13516 | 13517 |  |  | R
| Temperature - Circuit 32 | 32 | 7431 |  | -2 | UINT16 | 13518 | 13519 |  |  | R
| Temperature - Circuit 33 | 33 | 7432 |  | -2 | UINT16 | 13520 | 13521 |  |  | R
| Temperature - Circuit 34 | 34 | 7433 |  | -2 | UINT16 | 13522 | 13523 |  |  | R
| Temperature - Circuit 35 | 35 | 7434 |  | -2 | UINT16 | 13524 | 13525 |  |  | R
| Temperature - Circuit 36 | 36 | 7435 |  | -2 | UINT16 | 13526 | 13527 |  |  | R
| Temperature - Circuit 37 | 37 | 7436 |  | -2 | UINT16 | 13528 | 13529 |  |  | R
| Temperature - Circuit 38 | 38 | 7437 |  | -2 | UINT16 | 13530 | 13531 |  |  | R
| Temperature - Circuit 39 | 39 | 7438 |  | -2 | UINT16 | 13532 | 13533 |  |  | R
| Temperature - Circuit 40 | 40 | 7439 |  | -2 | UINT16 | 13534 | 13535 |  |  | R
| Temperature - Circuit 41 | 41 | 7440 |  | -2 | UINT16 | 13536 | 13537 |  |  | R
| Temperature - Circuit 42 | 42 | 7441 |  | -2 | UINT16 | 13538 | 13539 |  |  | R
| Temperature - Circuit 43 | 43 | 7442 |  | -2 | UINT16 | 13540 | 13541 |  |  | R
| Temperature - Circuit 44 | 44 | 7443 |  | -2 | UINT16 | 13542 | 13543 |  |  | R
| Temperature - Circuit 45 | 45 | 7444 |  | -2 | UINT16 | 13544 | 13545 |  |  | R
| Temperature - Circuit 46 | 46 | 7445 |  | -2 | UINT16 | 13546 | 13547 |  |  | R
| Temperature - Circuit 47 | 47 | 7446 |  | -2 | UINT16 | 13548 | 13549 |  |  | R
| Temperature - Circuit 48 | 48 | 7447 |  | -2 | UINT16 | 13550 | 13551 |  |  | R
| Temperature - Circuit 49 | 49 | 7448 |  | -2 | UINT16 | 13552 | 13553 |  |  | R
| Temperature - Circuit 50 | 50 | 7449 |  | -2 | UINT16 | 13554 | 13555 |  |  | R
| Temperature - Circuit 51 | 51 | 7450 |  | -2 | UINT16 | 13556 | 13557 |  |  | R
| Temperature - Circuit 52 | 52 | 7451 |  | -2 | UINT16 | 13558 | 13559 |  |  | R
| Temperature - Circuit 53 | 53 | 7452 |  | -2 | UINT16 | 13560 | 13561 |  |  | R
| Temperature - Circuit 54 | 54 | 7453 |  | -2 | UINT16 | 13562 | 13563 |  |  | R
| Temperature - Circuit 55 | 55 | 7454 |  | -2 | UINT16 | 13564 | 13565 |  |  | R
| Temperature - Circuit 56 | 56 | 7455 |  | -2 | UINT16 | 13566 | 13567 |  |  | R
| Temperature - Circuit 57 | 57 | 7456 |  | -2 | UINT16 | 13568 | 13569 |  |  | R
| Temperature - Circuit 58 | 58 | 7457 |  | -2 | UINT16 | 13570 | 13571 |  |  | R
| Temperature - Circuit 59 | 59 | 7458 |  | -2 | UINT16 | 13572 | 13573 |  |  | R
| Temperature - Circuit 60 | 60 | 7459 |  | -2 | UINT16 | 13574 | 13575 |  |  | R
| Temperature - Circuit 61 | 61 | 7460 |  | -2 | UINT16 | 13576 | 13577 |  |  | R
| Temperature - Circuit 62 | 62 | 7461 |  | -2 | UINT16 | 13578 | 13579 |  |  | R
| Temperature - Circuit 63 | 63 | 7462 |  | -2 | UINT16 | 13580 | 13581 |  |  | R
| Temperature - Circuit 64 | 64 | 7463 |  | -2 | UINT16 | 13582 | 13583 |  |  | R
| Temperature - Circuit 65 | 65 | 7464 |  | -2 | UINT16 | 13584 | 13585 |  |  | R
| Temperature - Circuit 66 | 66 | 7465 |  | -2 | UINT16 | 13586 | 13587 |  |  | R
| Temperature - Circuit 67 | 67 | 7466 |  | -2 | UINT16 | 13588 | 13589 |  |  | R
| Temperature - Circuit 68 | 68 | 7467 |  | -2 | UINT16 | 13590 | 13591 |  |  | R
| Temperature - Circuit 69 | 69 | 7468 |  | -2 | UINT16 | 13592 | 13593 |  |  | R
| Temperature - Circuit 70 | 70 | 7469 |  | -2 | UINT16 | 13594 | 13595 |  |  | R
| Temperature - Circuit 71 | 71 | 7470 |  | -2 | UINT16 | 13596 | 13597 |  |  | R
| Temperature - Circuit 72 | 72 | 7471 |  | -2 | UINT16 | 13598 | 13599 |  |  | R
| Temperature - Circuit 73 | 73 | 7472 |  | -2 | UINT16 | 13600 | 13601 |  |  | R
| Temperature - Circuit 74 | 74 | 7473 |  | -2 | UINT16 | 13602 | 13603 |  |  | R
| Temperature - Circuit 75 | 75 | 7474 |  | -2 | UINT16 | 13604 | 13605 |  |  | R
| Temperature - Circuit 76 | 76 | 7475 |  | -2 | UINT16 | 13606 | 13607 |  |  | R
| Temperature - Circuit 77 | 77 | 7476 |  | -2 | UINT16 | 13608 | 13609 |  |  | R
| Temperature - Circuit 78 | 78 | 7477 |  | -2 | UINT16 | 13610 | 13611 |  |  | R
| Temperature - Circuit 79 | 79 | 7478 |  | -2 | UINT16 | 13612 | 13613 |  |  | R
| Temperature - Circuit 80 | 80 | 7479 |  | -2 | UINT16 | 13614 | 13615 |  |  | R
| Temperature - Circuit 81 | 81 | 7480 |  | -2 | UINT16 | 13616 | 13617 |  |  | R
| Temperature - Circuit 82 | 82 | 7481 |  | -2 | UINT16 | 13618 | 13619 |  |  | R
| Temperature - Circuit 83 | 83 | 7482 |  | -2 | UINT16 | 13620 | 13621 |  |  | R
| Temperature - Circuit 84 | 84 | 7483 |  | -2 | UINT16 | 13622 | 13623 |  |  | R
| Temperature - Circuit 85 | 85 | 7484 |  | -2 | UINT16 | 13624 | 13625 |  |  | R
| Temperature - Circuit 86 | 86 | 7485 |  | -2 | UINT16 | 13626 | 13627 |  |  | R
| Temperature - Circuit 87 | 87 | 7486 |  | -2 | UINT16 | 13628 | 13629 |  |  | R
| Temperature - Circuit 88 | 88 | 7487 |  | -2 | UINT16 | 13630 | 13631 |  |  | R
| Temperature - Circuit 89 | 89 | 7488 |  | -2 | UINT16 | 13632 | 13633 |  |  | R
| Temperature - Circuit 90 | 90 | 7489 |  | -2 | UINT16 | 13634 | 13635 |  |  | R
| Temperature - Circuit 91 | 91 | 7490 |  | -2 | UINT16 | 13636 | 13637 |  |  | R
| Temperature - Circuit 92 | 92 | 7491 |  | -2 | UINT16 | 13638 | 13639 |  |  | R
| Temperature - Circuit 93 | 93 | 7492 |  | -2 | UINT16 | 13640 | 13641 |  |  | R
| Temperature - Circuit 94 | 94 | 7493 |  | -2 | UINT16 | 13642 | 13643 |  |  | R
| Temperature - Circuit 95 | 95 | 7494 |  | -2 | UINT16 | 13644 | 13645 |  |  | R
| Temperature - Circuit 96 | 96 | 7495 |  | -2 | UINT16 | 13646 | 13647 |  |  | R
True Meter | True Meter #1 | 1 | 15000 | 15276 |  |  | 15060 | 15485 | [6 empty] | Add 500 for next Circuit
Meter Configuration | [14 empty] | Integers have not yet been implemented for True Circuits
| # of Channels Assigned |  | 15000
| Assigned Branch |  | 15001 | 15003 | [6 empty] | R | NV |  |  | Read Only Registers (Use Meter Configuration registers to configure)
| Assigned Branch to Channel 1 |  | 15001 | [7 empty] | R | NV
| Assigned Branch to Channel 2 |  | 15002 | [7 empty] | R | NV
| Assigned Branch to Channel 3 |  | 15003 | [7 empty] | R | NV
| CT Size |  | 15004 | 15006 | [6 empty] | R | NV | Amps |  | Read Only Registers (Use Meter Configuration registers to configure)
| CT Size - Assigned Channel 1 |  | 15004 | [7 empty] | R | NV | Amps
| CT Size - Assigned Channel 2 |  | 15005 | [7 empty] | R | NV | Amps
| CT Size - Assigned Channel 3 |  | 15006 | [7 empty] | R | NV | Amps
| Breaker Size |  | 15007 | 15009 | [6 empty] | R | NV | Amps |  | Read Only Registers (Use Meter Configuration registers to configure)
| Breaker Size - Assigned Channel 1 |  | 15007 | [7 empty] | R | NV | Amps
| Breaker Size - Assigned Channel 2 |  | 15008 | [7 empty] | R | NV | Amps
| Breaker Size - Assigned Channel 3 |  | 15009 | [7 empty] | R | NV | Amps
| Voltage Phase |  | 15010 | 15012 | [6 empty] | R | NV |  |  | Read Only Registers (Use Meter Configuration registers to configure)
| Voltage Phase - Assigned Channel 1 |  | 15010 | [7 empty] | R | NV
| Voltage Phase - Assigned Channel 2 |  | 15011 | [7 empty] | R | NV
| Voltage Phase - Assigned Channel 3 |  | 15012 | [7 empty] | R | NV
| Reset/Command All Phases |  | 15013 | [11 empty] | Configuration registers have not yet been implemented for True Circuits
| Reset/Command |  | 15014 | 15016
| Reset/Command - Assigned Channel 1 |  | 15014
| Reset/Command - Assigned Channel 2 |  | 15015
| Reset/Command - Assigned Channel 3 |  | 15016
| CT Type/Compensation |  | 15017 | 15019 | [10 empty] | Configuration registers have not yet been implemented for True Circuits
| CT Type/Compensation - Assigned Channel 1 |  | 15017
| CT Type/Compensation - Assigned Channel 2 |  | 15018
| CT Type/Compensation - Assigned Channel 3 |  | 15019
| Meter Name - 40 Characters (20 Register) |  | 15020 | 15039
Voltage
| Frequency |  | 15040 |  |  |  | 15060 | 15061
| Voltage LN |  | 15041 | 15044 |  |  | 15062 | 15069
| Voltage LN - Average of Assigned Channels |  | 15041 |  |  |  | 15062 | 15063
| Voltage LN - Assigned Channel 1 |  | 15042 |  |  |  | 15064 | 15065
| Voltage LN - Assigned Channel 2 |  | 15043 |  |  |  | 15066 | 15067
| Voltage LN - Assigned Channel 3 |  | 15044 |  |  |  | 15068 | 15069
| Voltage LN THD |  | 15045 | 15048 |  |  | 15070 | 15077
| Voltage LN THD - Average of Assigned Channels |  | 15045 |  |  |  | 15070 | 15071
| Voltage LN THD - Assigned Channel 1 |  | 15046 |  |  |  | 15072 | 15073
| Voltage LN THD - Assigned Channel 2 |  | 15047 |  |  |  | 15074 | 15075
| Voltage LN THD - Assigned Channel 3 |  | 15048 |  |  |  | 15076 | 15077
True Meter #1 Total/Average |  |  | 15100
| Energy Scale |  | 15100
| Power Scale |  | 15101
| Current Scale |  | 15102
| Voltage Scale |  | 15103
| Alarm Status |  | 15104
| kWh |  | 15105 | 15106 |  |  | 15300 | 15301
| kVARh |  | 15107 | 15108 |  |  | 15302 | 15303
| kVAh |  | 15109 | 15110 |  |  | 15304 | 15305
| kW |  | 15111 |  |  |  | 15306 | 15307
| kVAR |  | 15112 |  |  |  | 15308 | 15309
| kVA |  | 15113 |  |  |  | 15310 | 15311
| Current |  | 15114 |  |  |  | 15312 | 15313
| Power Factor |  | 15115 |  |  |  | 15314 | 15315
| Reservered |  | 15116 |  |  |  | 15316 | 15317
| Current THD Average |  | 15117 |  |  |  | 15318 | 15319
| Max Current |  | 15118 |  |  |  | 15320 | 15321
| Max kW |  | 15119 |  |  |  | 15322 | 15323
| Current Demand |  | 15120 |  |  |  | 15324 | 15325
| kW Demand |  | 15121 |  |  |  | 15326 | 15327
| Max Current Demand |  | 15122 |  |  |  | 15328 | 15329
| Max kW Demand |  | 15123 |  |  |  | 15330 | 15331
| KWH Snapshot |  | 15124 | 15125 |  |  | 15332 | 15333
| Crest Factor |  | 15126 |  |  |  | 15334 | 15335
True Meter #1 Channel 1
| Energy Scale |  | 15150
| Power Scale |  | 15151
| Current Scale |  | 15152
| Voltage Scale |  | 15153
| Alarm Status |  | 15154
| kWh |  | 15155 | 15156 |  |  | 15350 | 15351
| kVARh |  | 15157 | 15158 |  |  | 15352 | 15353
| kVAh |  | 15159 | 15160 |  |  | 15354 | 15355
| kW |  | 15161 |  |  |  | 15356 | 15357
| kVAR |  | 15162 |  |  |  | 15358 | 15359
| kVA |  | 15163 |  |  |  | 15360 | 15361
| Current |  | 15164 |  |  |  | 15362 | 15363
| Power Factor |  | 15165 |  |  |  | 15364 | 15365
| Current Angle |  | 15166 |  |  |  | 15366 | 15367
| Percent THD |  | 15167 |  |  |  | 15368 | 15369
| Max Current |  | 15168 |  |  |  | 15370 | 15371
| Max kW |  | 15169 |  |  |  | 15372 | 15373
| Current Demand |  | 15170 |  |  |  | 15374 | 15375
| kW Demand |  | 15171 |  |  |  | 15376 | 15377
| Max Current Demand |  | 15172 |  |  |  | 15378 | 15379
| Max kW Demand |  | 15173 |  |  |  | 15380 | 15381
| KWH Snapshot |  | 15174 | 15175 |  |  | 15382 | 15383
| Crest Factor |  | 15176 |  |  |  | 15384 | 15385
True Meter #1 Channel 2
| Energy Scale |  | 15200
| Power Scale |  | 15201
| Current Scale |  | 15202
| Voltage Scale |  | 15203
| Alarm Status |  | 15204
| kWh |  | 15205 | 15206 |  |  | 15400 | 15401
| kVARh |  | 15207 | 15208 |  |  | 15402 | 15403
| kVAh |  | 15209 | 15210 |  |  | 15404 | 15405
| kW |  | 15211 |  |  |  | 15406 | 15407
| kVAR |  | 15212 |  |  |  | 15408 | 15409
| kVA |  | 15213 |  |  |  | 15410 | 15411
| Current |  | 15214 |  |  |  | 15412 | 15413
| Power Factor |  | 15215 |  |  |  | 15414 | 15415
| Current Angle |  | 15216 |  |  |  | 15416 | 15417
| Percent THD |  | 15217 |  |  |  | 15418 | 15419
| Max Current |  | 15218 |  |  |  | 15420 | 15421
| Max kW |  | 15219 |  |  |  | 15422 | 15423
| Current Demand |  | 15220 |  |  |  | 15424 | 15425
| kW Demand |  | 15221 |  |  |  | 15426 | 15427
| Max Current Demand |  | 15222 |  |  |  | 15428 | 15429
| Max kW Demand |  | 15223 |  |  |  | 15430 | 15431
| KWH Snapshot |  | 15224 | 15225 |  |  | 15432 | 15433
| Crest Factor |  | 15226 |  |  |  | 15434 | 15435
True Meter #1 Channel 3
| Energy Scale |  | 15250
| Power Scale |  | 15251
| Current Scale |  | 15252
| Voltage Scale |  | 15253
| Alarm Status |  | 15254
| kWh |  | 15255 | 15256 |  |  | 15450 | 15451
| kVARh |  | 15257 | 15258 |  |  | 15452 | 15453
| kVAh |  | 15259 | 15260 |  |  | 15454 | 15455
| kW |  | 15261 |  |  |  | 15456 | 15457
| kVAR |  | 15262 |  |  |  | 15458 | 15459
| kVA |  | 15263 |  |  |  | 15460 | 15461
| Current |  | 15264 |  |  |  | 15462 | 15463
| Power Factor |  | 15265 |  |  |  | 15464 | 15465
| Current Angle |  | 15266 |  |  |  | 15466 | 15467
| Percent THD |  | 15267 |  |  |  | 15468 | 15469
| Max Current |  | 15268 |  |  |  | 15470 | 15471
| Max kW |  | 15269 |  |  |  | 15472 | 15473
| Current Demand |  | 15270 |  |  |  | 15474 | 15475
| kW Demand |  | 15271 |  |  |  | 15476 | 15477
| Max Current Demand |  | 15272 |  |  |  | 15478 | 15479
| Max kW Demand |  | 15273 |  |  |  | 15480 | 15481
| KWH Snapshot |  | 15274 | 15275 |  |  | 15482 | 15483
| Crest Factor |  | 15276 |  |  |  | 15484 | 15485
| True Meter #2 | 2 | 15500 |  |  |  |  | 15999 | [6 empty] | Meter #2 = (Meter #1 + 500)
| True Meter #3 | 3 | 16000 |  |  |  |  | 16499 | [6 empty] | Meter #3 = (Meter #2 + 500)
| True Meter #4 | 4 | 16500 |  |  |  |  | 16999
| True Meter #5 | 5 | 17000 |  |  |  |  | 17499
| True Meter #6 | 6 | 17500 |  |  |  |  | 17999
| True Meter #7 | 7 | 18000 |  |  |  |  | 18499
| True Meter #8 | 8 | 18500 |  |  |  |  | 18999
| True Meter #9 | 9 | 19000 |  |  |  |  | 19499
| True Meter #10 | 10 | 19500 |  |  |  |  | 19999
| True Meter #11 | 11 | 20000 |  |  |  |  | 20499
| True Meter #12 | 12 | 20500 |  |  |  |  | 20999
| True Meter #13 | 13 | 21000 |  |  |  |  | 21499
| True Meter #14 | 14 | 21500 |  |  |  |  | 21999
| True Meter #15 | 15 | 22000 |  |  |  |  | 22499
| True Meter #16 | 16 | 22500 |  |  |  |  | 22999
| True Meter #17 | 17 | 23000 |  |  |  |  | 23499
| True Meter #18 | 18 | 23500 |  |  |  |  | 23999
| True Meter #19 | 19 | 24000 |  |  |  |  | 24499
| True Meter #20 | 20 | 24500 |  |  |  |  | 24999
| True Meter #21 | 21 | 25000 |  |  |  |  | 25499
| True Meter #22 | 22 | 25500 |  |  |  |  | 25999
| True Meter #23 | 23 | 26000 |  |  |  |  | 26499
| True Meter #24 | 24 | 26500 |  |  |  |  | 26999
| True Meter #25 | 25 | 27000 |  |  |  |  | 27499
| True Meter #26 | 26 | 27500 |  |  |  |  | 27999
| True Meter #27 | 27 | 28000 |  |  |  |  | 28499
| True Meter #28 | 28 | 28500 |  |  |  |  | 28999
| True Meter #29 | 29 | 29000 |  |  |  |  | 29499
| True Meter #30 | 30 | 29500 |  |  |  |  | 29999
| True Meter #31 | 31 | 30000 |  |  |  |  | 30499
| True Meter #32 | 32 | 30500 |  |  |  |  | 30999
| True Meter #33 | 33 | 31000 |  |  |  |  | 31499
| True Meter #34 | 34 | 31500 |  |  |  |  | 31999
| True Meter #35 | 35 | 32000 |  |  |  |  | 32499
| True Meter #36 | 36 | 32500 |  |  |  |  | 32999
| True Meter #37 | 37 | 33000 |  |  |  |  | 33499
| True Meter #38 | 38 | 33500 |  |  |  |  | 33999
| True Meter #39 | 39 | 34000 |  |  |  |  | 34499
| True Meter #40 | 40 | 34500 |  |  |  |  | 34999
| True Meter #41 | 41 | 35000 |  |  |  |  | 35499
| True Meter #42 | 42 | 35500 |  |  |  |  | 35999
| True Meter #43 | 43 | 36000 |  |  |  |  | 36499
| True Meter #44 | 44 | 36500 |  |  |  |  | 36999
| True Meter #45 | 45 | 37000 |  |  |  |  | 37499
| True Meter #46 | 46 | 37500 |  |  |  |  | 37999
| True Meter #47 | 47 | 38000 |  |  |  |  | 38499
| True Meter #48 | 48 | 38500 |  |  |  |  | 38999
| True Meter #49 | 49 | 39000 |  |  |  |  | 39499
| True Meter #50 | 50 | 39500 |  |  |  |  | 39999
| True Meter #51 | 51 | 40000 |  |  |  |  | 40499
| True Meter #52 | 52 | 40500 |  |  |  |  | 40999
| True Meter #53 | 53 | 41000 |  |  |  |  | 41499
| True Meter #54 | 54 | 41500 |  |  |  |  | 41999
| True Meter #55 | 55 | 42000 |  |  |  |  | 42499
| True Meter #56 | 56 | 42500 |  |  |  |  | 42999
| True Meter #57 | 57 | 43000 |  |  |  |  | 43499
| True Meter #58 | 58 | 43500 |  |  |  |  | 43999
| True Meter #59 | 59 | 44000 |  |  |  |  | 44499
| True Meter #60 | 60 | 44500 |  |  |  |  | 44999
| True Meter #61 | 61 | 45000 |  |  |  |  | 45499
| True Meter #62 | 62 | 45500 |  |  |  |  | 45999
| True Meter #63 | 63 | 46000 |  |  |  |  | 46499
| True Meter #64 | 64 | 46500 |  |  |  |  | 46999
| True Meter #65 | 65 | 47000 |  |  |  |  | 47499
| True Meter #66 | 66 | 47500 |  |  |  |  | 47999
| True Meter #67 | 67 | 48000 |  |  |  |  | 48499
| True Meter #68 | 68 | 48500 |  |  |  |  | 48999
| True Meter #69 | 69 | 49000 |  |  |  |  | 49499
| True Meter #70 | 70 | 49500 |  |  |  |  | 49999
| True Meter #71 | 71 | 50000 |  |  |  |  | 50499
| True Meter #72 | 72 | 50500 |  |  |  |  | 50999
| True Meter #73 | 73 | 51000 |  |  |  |  | 51499
| True Meter #74 | 74 | 51500 |  |  |  |  | 51999
| True Meter #75 | 75 | 52000 |  |  |  |  | 52499
| True Meter #76 | 76 | 52500 |  |  |  |  | 52999
| True Meter #77 | 77 | 53000 |  |  |  |  | 53499
| True Meter #78 | 78 | 53500 |  |  |  |  | 53999
| True Meter #79 | 79 | 54000 |  |  |  |  | 54499
| True Meter #80 | 80 | 54500 |  |  |  |  | 54999
| True Meter #81 | 81 | 55000 |  |  |  |  | 55499
| True Meter #82 | 82 | 55500 |  |  |  |  | 55999
| True Meter #83 | 83 | 56000 |  |  |  |  | 56499
| True Meter #84 | 84 | 56500 |  |  |  |  | 56999
| True Meter #85 | 85 | 57000 |  |  |  |  | 57499
| True Meter #86 | 86 | 57500 |  |  |  |  | 57999
| True Meter #87 | 87 | 58000 |  |  |  |  | 58499
| True Meter #88 | 88 | 58500 |  |  |  |  | 58999
| True Meter #89 | 89 | 59000 |  |  |  |  | 59499
| True Meter #90 | 90 | 59500 |  |  |  |  | 59999
| True Meter #91 | 91 | 60000 |  |  |  |  | 60499
| True Meter #92 | 92 | 60500 |  |  |  |  | 60999
| True Meter #93 | 93 | 61000 |  |  |  |  | 61499
| True Meter #94 | 94 | 61500 |  |  |  |  | 61999
| True Meter #95 | 95 | 62000 |  |  |  |  | 62499
| True Meter #96 | 96 | 62500 |  |  |  |  | 62999

## Change Log
Revision | Date | Changes | Notes:
A |  | Initial Release | Changes from previous version are highlighted with light gray shading
B | 2019-07-01 | Added Device Name (Reg 61-76) and changed register count for Brand Name (Reg 29-44) and Model Name (Reg 45-60)
Removed Voltage Presence registers (Reg 1307-1402)
|  | Added Alarm Status summary registers (Reg 1403-1498) | Yellow text indicates features which are not yet supported
Added Smart Port/Panel configuration registers (Reg 1800-1997)
Added Percent THD Average (Reg 4810/4918-4919) Moved L1, L2, L3 THD and L1, L2, L3 Angle (Reg 4810-4816/4918-4931)
Added Dynamic Smart Port Map (Reg 3000-3999)
Added Smart Port to Circuit Configuration (Reg 776-871)
Added CT Compensation Enabled (Reg 149)
C | 2019-07-22 | IP Address, Netmask and Default Gateway are Writable (Reg 126-131)
NTP, DNS and SMTP are not Writable (Reg 132-139)
RS485 Baud rate can be set using the pointmap (Reg 140-141)
Added Device Reboot to Reset/Commnad (Reg 192)
Added Support for BACnet
Added Units Column
Enabled Uptime (Reg 7-8)
Enabled Crest Factor Registers
Enabled CT Size, Breaker Size, Voltage Phase in True Meter (Read Only)