## Pointmap
|  |  | Modbus Register |  |  |  | Bacnet Object
|  |  | Integer |  | Float
| Description | Channel | Start (MSW) | End (LSW) | MSW | LSW | Object Type | Instance # | R/W | NV | Range | Default | Notes
Meter Information
| Serial Number |  | 1 | 2
| Bootloader Version |  | 3
| Firmware Version |  | 4
| Product ID |  | 5
| Power Up Counter |  | 6
| Device Health |  | 7
| Smart Port ID #1 |  | 8 | [9 empty] | 0 = Nothing Connected 1 = CT Card 2 = CT Strip …
| Smart Port ID #2 |  | 9
| Smart Port ID #3 |  | 10
| Smart Port ID #4 |  | 11
| Smart Port #1 Serial Number |  | 12 | 13
| Smart Port #2 Serial Number |  | 14 | 15
| Smart Port #3 Serial Number |  | 16 | 17
| Smart Port #4 Serial Number |  | 18 | 19
| Smart Port #1 Firmware Version |  | 20
| Smart Port #2 Firmware Version |  | 21
| Smart Port #3 Firmware Version |  | 22
| Smart Port #4 Firmware Version |  | 23
| MAC Address (Bit 33-48) |  | 24
| MAC Address (Bit 17-32) |  | 25
| MAC Address (Bit 1-16) |  | 26
| Brand Name (16 Registers) |  | 27 | 42
| Model Name (32 Register) |  | 43 | 74
Meter Configuration
| Demand # of Sub-Intervals |  | 100
| Demand Sub-Interval Length |  | 101
| Demand Time Stamp (Year) |  | 102
| Demand Time Stamp (Month) |  | 103
| Demand Time Stamp (Day) |  | 104
| Demand Time Stamp (Weekday) |  | 105
| Demand Time Stamp (Hour) |  | 106
| Demand Time Stamp (Minute) |  | 107
| Demand Time Stamp (Second) |  | 108
| Real Time Clock (Year) |  | 340
| Real Time Clock (Month) |  | 341
| Real Time Clock (Day) |  | 342
| Real Time Clock (Weekday) |  | 343
| Real Time Clock (Hour) |  | 344
| Real Time Clock (Min) |  | 345
| Real Time Clock (Second) |  | 346
| Digital Output #1 |  | 347
| Digital Output #2 |  | 348
| Digital Input #1 State |  | 349
| Digital Input #2 State |  | 350
| Digital Input #1 Counter |  | 351
| Digital Input #1 Counter |  | 352
| Modbus Address |  | 353
| Modbus TCP Port |  | 354
| IP Address |  | 355 | 356
| Gateway |  | 357 | 358
| NTP |  | 359 | 360
| DNS 1 |  | 361 | 362
| DNS 2 |  | 363 | 364
| SMTP |  | 365 | 366
| Baudrate |  | 367 | 368
| Parity |  | 369
| Stop Bits |  | 370
| Dip Switch Enabled |  | 371
| Dips Switch Value |  | 372
| RS485 Gateway Passthrough Enabled |  | 373
Circuit Configuration
| CT Size |  | 400 | 495
| CT Size - Channel 1 | 1 | 400 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 2 | 2 | 401 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 3 | 3 | 402 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 4 | 4 | 403 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 5 | 5 | 404 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 6 | 6 | 405 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 7 | 7 | 406 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 8 | 8 | 407 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 9 | 9 | 408 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 10 | 10 | 409 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 11 | 11 | 410 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 12 | 12 | 411 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 13 | 13 | 412 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 14 | 14 | 413 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 15 | 15 | 414 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 16 | 16 | 415 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 17 | 17 | 416 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 18 | 18 | 417 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 19 | 19 | 418 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 20 | 20 | 419 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 21 | 21 | 420 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 22 | 22 | 421 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 23 | 23 | 422 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 24 | 24 | 423 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 25 | 25 | 424 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 26 | 26 | 425 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 27 | 27 | 426 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 28 | 28 | 427 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 29 | 29 | 428 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 30 | 30 | 429 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 31 | 31 | 430 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 32 | 32 | 431 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 33 | 33 | 432 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 34 | 34 | 433 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 35 | 35 | 434 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 36 | 36 | 435 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 37 | 37 | 436 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 38 | 38 | 437 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 39 | 39 | 438 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 40 | 40 | 439 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 41 | 41 | 440 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 42 | 42 | 441 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 43 | 43 | 442 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 44 | 44 | 443 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 45 | 45 | 444 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 46 | 46 | 445 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 47 | 47 | 446 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 48 | 48 | 447 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 49 | 49 | 448 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 50 | 50 | 449 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 51 | 51 | 450 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 52 | 52 | 451 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 53 | 53 | 452 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 54 | 54 | 453 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 55 | 55 | 454 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 56 | 56 | 455 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 57 | 57 | 456 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 58 | 58 | 457 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 59 | 59 | 458 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 60 | 60 | 459 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 61 | 61 | 460 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 62 | 62 | 461 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 63 | 63 | 462 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 64 | 64 | 463 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 65 | 65 | 464 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 66 | 66 | 465 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 67 | 67 | 466 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 68 | 68 | 467 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 69 | 69 | 468 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 70 | 70 | 469 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 71 | 71 | 470 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 72 | 72 | 471 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 73 | 73 | 472 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 74 | 74 | 473 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 75 | 75 | 474 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 76 | 76 | 475 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 77 | 77 | 476 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 78 | 78 | 477 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 79 | 79 | 478 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 80 | 80 | 479 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 81 | 81 | 480 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 82 | 82 | 481 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 83 | 83 | 482 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 84 | 84 | 483 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 85 | 85 | 484 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 86 | 86 | 485 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 87 | 87 | 486 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 88 | 88 | 487 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 89 | 89 | 488 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 90 | 90 | 489 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 91 | 91 | 490 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 92 | 92 | 491 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 93 | 93 | 492 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 94 | 94 | 493 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 95 | 95 | 494 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 96 | 96 | 495 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size |  | 500 | 595
| Breaker Size - Channel 1 | 1 | 500 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 2 | 2 | 501 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 3 | 3 | 502 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 4 | 4 | 503 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 5 | 5 | 504 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 6 | 6 | 505 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 7 | 7 | 506 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 8 | 8 | 507 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 9 | 9 | 508 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 10 | 10 | 509 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 11 | 11 | 510 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 12 | 12 | 511 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 13 | 13 | 512 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 14 | 14 | 513 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 15 | 15 | 514 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 16 | 16 | 515 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 17 | 17 | 516 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 18 | 18 | 517 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 19 | 19 | 518 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 20 | 20 | 519 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 21 | 21 | 520 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 22 | 22 | 521 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 23 | 23 | 522 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 24 | 24 | 523 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 25 | 25 | 524 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 26 | 26 | 525 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 27 | 27 | 526 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 28 | 28 | 527 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 29 | 29 | 528 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 30 | 30 | 529 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 31 | 31 | 530 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 32 | 32 | 531 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 33 | 33 | 532 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 34 | 34 | 533 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 35 | 35 | 534 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 36 | 36 | 535 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 37 | 37 | 536 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 38 | 38 | 537 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 39 | 39 | 538 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 40 | 40 | 539 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 41 | 41 | 540 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 42 | 42 | 541 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 43 | 43 | 542 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 44 | 44 | 543 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 45 | 45 | 544 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 46 | 46 | 545 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 47 | 47 | 546 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 48 | 48 | 547 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 49 | 49 | 548 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 50 | 50 | 549 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 51 | 51 | 550 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 52 | 52 | 551 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 53 | 53 | 552 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 54 | 54 | 553 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 55 | 55 | 554 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 56 | 56 | 555 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 57 | 57 | 556 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 58 | 58 | 557 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 59 | 59 | 558 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 60 | 60 | 559 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 61 | 61 | 560 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 62 | 62 | 561 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 63 | 63 | 562 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 64 | 64 | 563 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 65 | 65 | 564 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 66 | 66 | 565 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 67 | 67 | 566 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 68 | 68 | 567 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 69 | 69 | 568 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 70 | 70 | 569 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 71 | 71 | 570 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 72 | 72 | 571 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 73 | 73 | 572 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 74 | 74 | 573 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 75 | 75 | 574 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 76 | 76 | 575 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 77 | 77 | 576 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 78 | 78 | 577 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 79 | 79 | 578 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 80 | 80 | 579 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 81 | 81 | 580 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 82 | 82 | 581 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 83 | 83 | 582 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 84 | 84 | 583 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 85 | 85 | 584 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 86 | 86 | 585 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 87 | 87 | 586 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 88 | 88 | 587 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 89 | 89 | 588 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 90 | 90 | 589 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 91 | 91 | 590 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 92 | 92 | 591 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 93 | 93 | 592 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 94 | 94 | 593 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 95 | 95 | 594 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 96 | 96 | 595 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase |  | 600 | 695
| Voltage Phase - Channel 1 | 1 | 600 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 2 | 2 | 601 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 3 | 3 | 602 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 4 | 4 | 603 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 5 | 5 | 604 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 6 | 6 | 605 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 7 | 7 | 606 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 8 | 8 | 607 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 9 | 9 | 608 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 10 | 10 | 609 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 11 | 11 | 610 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 12 | 12 | 611 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 13 | 13 | 612 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 14 | 14 | 613 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 15 | 15 | 614 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 16 | 16 | 615 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 17 | 17 | 616 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 18 | 18 | 617 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 19 | 19 | 618 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 20 | 20 | 619 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 21 | 21 | 620 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 22 | 22 | 621 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 23 | 23 | 622 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 24 | 24 | 623 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 25 | 25 | 624 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 26 | 26 | 625 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 27 | 27 | 626 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 28 | 28 | 627 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 29 | 29 | 628 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 30 | 30 | 629 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 31 | 31 | 630 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 32 | 32 | 631 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 33 | 33 | 632 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 34 | 34 | 633 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 35 | 35 | 634 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 36 | 36 | 635 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 37 | 37 | 636 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 38 | 38 | 637 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 39 | 39 | 638 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 40 | 40 | 639 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 41 | 41 | 640 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 42 | 42 | 641 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 43 | 43 | 642 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 44 | 44 | 643 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 45 | 45 | 644 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 46 | 46 | 645 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 47 | 47 | 646 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 48 | 48 | 647 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 49 | 49 | 648 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 50 | 50 | 649 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 51 | 51 | 650 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 52 | 52 | 651 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 53 | 53 | 652 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 54 | 54 | 653 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 55 | 55 | 654 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 56 | 56 | 655 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 57 | 57 | 656 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 58 | 58 | 657 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 59 | 59 | 658 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 60 | 60 | 659 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 61 | 61 | 660 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 62 | 62 | 661 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 63 | 63 | 662 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 64 | 64 | 663 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 65 | 65 | 664 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 66 | 66 | 665 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 67 | 67 | 666 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 68 | 68 | 667 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 69 | 69 | 668 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 70 | 70 | 669 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 71 | 71 | 670 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 72 | 72 | 671 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 73 | 73 | 672 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 74 | 74 | 673 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 75 | 75 | 674 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 76 | 76 | 675 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 77 | 77 | 676 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 78 | 78 | 677 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 79 | 79 | 678 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 80 | 80 | 679 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 81 | 81 | 680 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 82 | 82 | 681 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 83 | 83 | 682 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 84 | 84 | 683 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 85 | 85 | 684 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 86 | 86 | 685 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 87 | 87 | 686 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 88 | 88 | 687 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 89 | 89 | 688 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 90 | 90 | 689 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 91 | 91 | 690 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 92 | 92 | 691 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 93 | 93 | 692 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 94 | 94 | 693 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 95 | 95 | 694 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 96 | 96 | 695 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assignment |  | 700 | 795
| Circuit Assingment - Channel 1 | 1 | 700 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 2 | 2 | 701 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 3 | 3 | 702 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 4 | 4 | 703 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 5 | 5 | 704 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 6 | 6 | 705 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 7 | 7 | 706 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 8 | 8 | 707 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 9 | 9 | 708 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 10 | 10 | 709 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 11 | 11 | 710 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 12 | 12 | 711 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 13 | 13 | 712 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 14 | 14 | 713 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 15 | 15 | 714 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 16 | 16 | 715 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 17 | 17 | 716 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 18 | 18 | 717 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 19 | 19 | 718 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 20 | 20 | 719 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 21 | 21 | 720 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 22 | 22 | 721 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 23 | 23 | 722 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 24 | 24 | 723 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 25 | 25 | 724 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 26 | 26 | 725 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 27 | 27 | 726 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 28 | 28 | 727 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 29 | 29 | 728 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 30 | 30 | 729 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 31 | 31 | 730 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 32 | 32 | 731 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 33 | 33 | 732 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 34 | 34 | 733 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 35 | 35 | 734 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 36 | 36 | 735 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 37 | 37 | 736 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 38 | 38 | 737 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 39 | 39 | 738 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 40 | 40 | 739 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 41 | 41 | 740 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 42 | 42 | 741 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 43 | 43 | 742 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 44 | 44 | 743 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 45 | 45 | 744 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 46 | 46 | 745 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 47 | 47 | 746 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 48 | 48 | 747 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 49 | 49 | 748 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 50 | 50 | 749 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 51 | 51 | 750 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 52 | 52 | 751 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 53 | 53 | 752 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 54 | 54 | 753 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 55 | 55 | 754 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 56 | 56 | 755 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 57 | 57 | 756 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 58 | 58 | 757 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 59 | 59 | 758 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 60 | 60 | 759 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 61 | 61 | 760 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 62 | 62 | 761 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 63 | 63 | 762 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 64 | 64 | 763 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 65 | 65 | 764 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 66 | 66 | 765 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 67 | 67 | 766 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 68 | 68 | 767 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 69 | 69 | 768 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 70 | 70 | 769 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 71 | 71 | 770 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 72 | 72 | 771 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 73 | 73 | 772 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 74 | 74 | 773 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 75 | 75 | 774 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 76 | 76 | 775 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 77 | 77 | 776 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 78 | 78 | 777 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 79 | 79 | 778 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 80 | 80 | 779 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 81 | 81 | 780 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 82 | 82 | 781 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 83 | 83 | 782 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 84 | 84 | 783 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 85 | 85 | 784 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 86 | 86 | 785 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 87 | 87 | 786 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 88 | 88 | 787 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 89 | 89 | 788 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 90 | 90 | 789 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 91 | 91 | 790 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 92 | 92 | 791 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 93 | 93 | 792 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 94 | 94 | 793 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 95 | 95 | 794 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 96 | 96 | 795 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command |  | 800 | 895
| Reset/Command - Channel 1 | 1 | 800 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 2 | 2 | 801 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 3 | 3 | 802 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 4 | 4 | 803 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 5 | 5 | 804 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 6 | 6 | 805 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 7 | 7 | 806 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 8 | 8 | 807 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 9 | 9 | 808 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 10 | 10 | 809 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 11 | 11 | 810 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 12 | 12 | 811 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 13 | 13 | 812 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 14 | 14 | 813 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 15 | 15 | 814 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 16 | 16 | 815 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 17 | 17 | 816 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 18 | 18 | 817 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 19 | 19 | 818 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 20 | 20 | 819 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 21 | 21 | 820 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 22 | 22 | 821 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 23 | 23 | 822 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 24 | 24 | 823 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 25 | 25 | 824 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 26 | 26 | 825 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 27 | 27 | 826 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 28 | 28 | 827 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 29 | 29 | 828 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 30 | 30 | 829 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 31 | 31 | 830 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 32 | 32 | 831 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 33 | 33 | 832 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 34 | 34 | 833 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 35 | 35 | 834 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 36 | 36 | 835 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 37 | 37 | 836 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 38 | 38 | 837 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 39 | 39 | 838 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 40 | 40 | 839 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 41 | 41 | 840 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 42 | 42 | 841 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 43 | 43 | 842 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 44 | 44 | 843 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 45 | 45 | 844 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 46 | 46 | 845 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 47 | 47 | 846 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 48 | 48 | 847 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 49 | 49 | 848 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 50 | 50 | 849 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 51 | 51 | 850 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 52 | 52 | 851 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 53 | 53 | 852 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 54 | 54 | 853 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 55 | 55 | 854 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 56 | 56 | 855 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 57 | 57 | 856 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 58 | 58 | 857 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 59 | 59 | 858 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 60 | 60 | 859 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 61 | 61 | 860 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 62 | 62 | 861 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 63 | 63 | 862 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 64 | 64 | 863 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 65 | 65 | 864 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 66 | 66 | 865 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 67 | 67 | 866 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 68 | 68 | 867 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 69 | 69 | 868 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 70 | 70 | 869 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 71 | 71 | 870 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 72 | 72 | 871 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 73 | 73 | 872 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 74 | 74 | 873 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 75 | 75 | 874 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 76 | 76 | 875 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 77 | 77 | 876 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 78 | 78 | 877 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 79 | 79 | 878 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 80 | 80 | 879 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 81 | 81 | 880 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 82 | 82 | 881 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 83 | 83 | 882 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 84 | 84 | 883 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 85 | 85 | 884 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 86 | 86 | 885 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 87 | 87 | 886 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 88 | 88 | 887 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 89 | 89 | 888 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 90 | 90 | 889 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 91 | 91 | 890 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 92 | 92 | 891 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 93 | 93 | 892 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 94 | 94 | 893 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 95 | 95 | 894 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 96 | 96 | 895 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation |  | 900 | 995
| CT Type/Compensation - Channel 1 | 1 | 900 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 2 | 2 | 901 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 3 | 3 | 902 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 4 | 4 | 903 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 5 | 5 | 904 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 6 | 6 | 905 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 7 | 7 | 906 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 8 | 8 | 907 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 9 | 9 | 908 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 10 | 10 | 909 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 11 | 11 | 910 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 12 | 12 | 911 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 13 | 13 | 912 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 14 | 14 | 913 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 15 | 15 | 914 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 16 | 16 | 915 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 17 | 17 | 916 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 18 | 18 | 917 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 19 | 19 | 918 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 20 | 20 | 919 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 21 | 21 | 920 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 22 | 22 | 921 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 23 | 23 | 922 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 24 | 24 | 923 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 25 | 25 | 924 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 26 | 26 | 925 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 27 | 27 | 926 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 28 | 28 | 927 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 29 | 29 | 928 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 30 | 30 | 929 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 31 | 31 | 930 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 32 | 32 | 931 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 33 | 33 | 932 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 34 | 34 | 933 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 35 | 35 | 934 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 36 | 36 | 935 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 37 | 37 | 936 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 38 | 38 | 937 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 39 | 39 | 938 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 40 | 40 | 939 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 41 | 41 | 940 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 42 | 42 | 941 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 43 | 43 | 942 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 44 | 44 | 943 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 45 | 45 | 944 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 46 | 46 | 945 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 47 | 47 | 946 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 48 | 48 | 947 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 49 | 49 | 948 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 50 | 50 | 949 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 51 | 51 | 950 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 52 | 52 | 951 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 53 | 53 | 952 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 54 | 54 | 953 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 55 | 55 | 954 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 56 | 56 | 955 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 57 | 57 | 956 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 58 | 58 | 957 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 59 | 59 | 958 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 60 | 60 | 959 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 61 | 61 | 960 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 62 | 62 | 961 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 63 | 63 | 962 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 64 | 64 | 963 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 65 | 65 | 964 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 66 | 66 | 965 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 67 | 67 | 966 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 68 | 68 | 967 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 69 | 69 | 968 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 70 | 70 | 969 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 71 | 71 | 970 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 72 | 72 | 971 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 73 | 73 | 972 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 74 | 74 | 973 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 75 | 75 | 974 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 76 | 76 | 975 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 77 | 77 | 976 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 78 | 78 | 977 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 79 | 79 | 978 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 80 | 80 | 979 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 81 | 81 | 980 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 82 | 82 | 981 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 83 | 83 | 982 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 84 | 84 | 983 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 85 | 85 | 984 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 86 | 86 | 985 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 87 | 87 | 986 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 88 | 88 | 987 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 89 | 89 | 988 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 90 | 90 | 989 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 91 | 91 | 990 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 92 | 92 | 991 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 93 | 93 | 992 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 94 | 94 | 993 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 95 | 95 | 994 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 96 | 96 | 995 | [5 empty] | R/W | NV | 0 - 32000
Global
| Global CT Size |  | 996
| Global Breaker Size |  | 997
| Global Reset/Command |  | 998
| Global CT Type/Compensation |  | 999
Panel/Aux Configuration
| Configuration - Smart Port #1 |  | 1000
| Configuration - Smart Port #2 |  | 1001
| Configuration - Smart Port #3 |  | 1002
| Configuration - Smart Port #4 |  | 1003
| Location Panel #1 (64 Registers) |  | 1004 | 1067
| Location Panel #2 (64 Registers) |  | 1005 | 1068
| Location Panel #3 (64 Registers) |  | 1006 | 1069
| Location Panel #4 (64 Registers) |  | 1007 | 1070
| Aux #1 Assigned Channels |  | 1071 | 1073
| Channel 1 |  | 1071
| Channel 2 |  | 1072
| Channel 3 |  | 1073
| Aux #2 Assigned Channels |  | 1074 | 1076
| Channel 1 |  | 1074
| Channel 2 |  | 1075
| Channel 3 |  | 1076
| Aux #3 Assigned Channels |  | 1077 | 1079
| Channel 1 |  | 1077
| Channel 2 |  | 1078
| Channel 3 |  | 1079
| Aux #4 Assigned Channels |  | 1080 | 1082
| Channel 1 |  | 1080
| Channel 2 |  | 1081
| Channel 3 |  | 1082
Aux
| Aux #1 |  | 1100 | 1122 | 1200 | 1233
| Energy Scale |  | 1100
| Power Scale |  | 1101
| Current Scale |  | 1102
| kWh |  | 1103 | 1104 | 1200 | 1201
| kVARh |  | 1105 | 1106 | 1202 | 1203
| kVAh |  | 1107 | 1108 | 1204 | 1205
| kW |  | 1108 |  | 1206 | 1207
| kVAR |  | 1109 |  | 1208 | 1209
| kVA |  | 1110 |  | 1210 | 1211
| Current |  | 1111 |  | 1212 | 1213
| Power Factor |  | 1112 |  | 1214 | 1215
| Current Angle |  | 1113 |  | 1216 | 1217
| Percent THD |  | 1114 |  | 1218 | 1219
| Max Current |  | 1115 |  | 1220 | 1221
| Max kW |  | 1116 |  | 1222 | 1223
| Current Demand |  | 1117 |  | 1224 | 1225
| kW Demand |  | 1118 |  | 1226 | 1227
| Max Current Demand |  | 1119 |  | 1228 | 1229
| Max kW Demand |  | 1120 |  | 1230 | 1231
| KWH Snapshot |  | 1121 | 1122 | 1232 | 1233
| Aux #2 |  | 1300 | 1322 | 1400 | 1433
| Aux #3 |  | 1500 | 1522 | 1600 | 1633
| Aux #4 |  | 1700 | 1722 | 1800 | 1833
Dynamic Smart Port
| Smart Port #1 |  | 2000 | 2249 | [8 empty] | This section of the Pointmap is dependant on what is connected to the smart ports
| Smart Port #2 |  | 2250 | 2499
| Smart Port #3 |  | 2500 | 2749
| Smart Port #4 |  | 2750 | 2999
Alarms
Voltage Alarm Configuration |  |  | 3000 | 3004
| Overvoltage Alarm Timer |  | 3000
| Undervoltage Alarm Timer |  | 3001
| Overvoltage Alarm Threshold |  | 3002
| Undervotage Alarm Threshold |  | 3003
| Voltage Alarm Hysteresis |  | 3004
Branch Alarm Configuration |  |  | 3005 | 3019
| High-High Latching Alarm Time Delay |  | 3005
| High Latching Alarm Time Delay |  | 3006
| Low Latching Alarm Time Delay |  | 3007
| Low-Low Latching Alarm Time Delay |  | 3008
| Latching Alarm On Time |  | 3009
| Latching Alarm Off Time |  | 3010
| High-High Latching Alarm Threshold |  | 3011
| High Latching Alarm Thresold |  | 3012
| Low Latching Alarm Threshold |  | 3013
| Low-Low Latchng Alarm Threhold |  | 3014
| Non-Latching High High Threshold |  | 3015
| Non-Latching High Alarm Threshold |  | 3016
| Non-Latching Low Alarm Threshold |  | 3017
| Non-Latching Low Low Threshold |  | 3018
| Non-Latching Hysteresis |  | 3019
Global Alarm |  |  | 3020 | 3025
| Global Latching Alarm Status |  | 3020
| Global Non-Latching Alarm Status |  | 3021
| Global Most Recent Latching Alarm Channel |  | 3022
| Global Most Recent Non-Latching Alarm Channel |  | 3023
| Total Number of Latching Channels In Alarm |  | 3024
| Total Number of Non-Latching Channels In Alarm |  | 3025
Voltage Alarms
| Voltage Alarm Status |  | 3026 | 3028
| L1-L2 Alarm Status |  | 3026
| L2-L3 Alarm Status |  | 3027
| L3-L1 Alarm Status |  | 3028
Branch Alarms
| Branch Alarm Status |  | 3029 | 3124
| Branch Alarm Status - Channel 1 | 1 | 3029 | [5 empty] | R
| Branch Alarm Status - Channel 2 | 2 | 3030 | [5 empty] | R
| Branch Alarm Status - Channel 3 | 3 | 3031 | [5 empty] | R
| Branch Alarm Status - Channel 4 | 4 | 3032 | [5 empty] | R
| Branch Alarm Status - Channel 5 | 5 | 3033 | [5 empty] | R
| Branch Alarm Status - Channel 6 | 6 | 3034 | [5 empty] | R
| Branch Alarm Status - Channel 7 | 7 | 3035 | [5 empty] | R
| Branch Alarm Status - Channel 8 | 8 | 3036 | [5 empty] | R
| Branch Alarm Status - Channel 9 | 9 | 3037 | [5 empty] | R
| Branch Alarm Status - Channel 10 | 10 | 3038 | [5 empty] | R
| Branch Alarm Status - Channel 11 | 11 | 3039 | [5 empty] | R
| Branch Alarm Status - Channel 12 | 12 | 3040 | [5 empty] | R
| Branch Alarm Status - Channel 13 | 13 | 3041 | [5 empty] | R
| Branch Alarm Status - Channel 14 | 14 | 3042 | [5 empty] | R
| Branch Alarm Status - Channel 15 | 15 | 3043 | [5 empty] | R
| Branch Alarm Status - Channel 16 | 16 | 3044 | [5 empty] | R
| Branch Alarm Status - Channel 17 | 17 | 3045 | [5 empty] | R
| Branch Alarm Status - Channel 18 | 18 | 3046 | [5 empty] | R
| Branch Alarm Status - Channel 19 | 19 | 3047 | [5 empty] | R
| Branch Alarm Status - Channel 20 | 20 | 3048 | [5 empty] | R
| Branch Alarm Status - Channel 21 | 21 | 3049 | [5 empty] | R
| Branch Alarm Status - Channel 22 | 22 | 3050 | [5 empty] | R
| Branch Alarm Status - Channel 23 | 23 | 3051 | [5 empty] | R
| Branch Alarm Status - Channel 24 | 24 | 3052 | [5 empty] | R
| Branch Alarm Status - Channel 25 | 25 | 3053 | [5 empty] | R
| Branch Alarm Status - Channel 26 | 26 | 3054 | [5 empty] | R
| Branch Alarm Status - Channel 27 | 27 | 3055 | [5 empty] | R
| Branch Alarm Status - Channel 28 | 28 | 3056 | [5 empty] | R
| Branch Alarm Status - Channel 29 | 29 | 3057 | [5 empty] | R
| Branch Alarm Status - Channel 30 | 30 | 3058 | [5 empty] | R
| Branch Alarm Status - Channel 31 | 31 | 3059 | [5 empty] | R
| Branch Alarm Status - Channel 32 | 32 | 3060 | [5 empty] | R
| Branch Alarm Status - Channel 33 | 33 | 3061 | [5 empty] | R
| Branch Alarm Status - Channel 34 | 34 | 3062 | [5 empty] | R
| Branch Alarm Status - Channel 35 | 35 | 3063 | [5 empty] | R
| Branch Alarm Status - Channel 36 | 36 | 3064 | [5 empty] | R
| Branch Alarm Status - Channel 37 | 37 | 3065 | [5 empty] | R
| Branch Alarm Status - Channel 38 | 38 | 3066 | [5 empty] | R
| Branch Alarm Status - Channel 39 | 39 | 3067 | [5 empty] | R
| Branch Alarm Status - Channel 40 | 40 | 3068 | [5 empty] | R
| Branch Alarm Status - Channel 41 | 41 | 3069 | [5 empty] | R
| Branch Alarm Status - Channel 42 | 42 | 3070 | [5 empty] | R
| Branch Alarm Status - Channel 43 | 43 | 3071 | [5 empty] | R
| Branch Alarm Status - Channel 44 | 44 | 3072 | [5 empty] | R
| Branch Alarm Status - Channel 45 | 45 | 3073 | [5 empty] | R
| Branch Alarm Status - Channel 46 | 46 | 3074 | [5 empty] | R
| Branch Alarm Status - Channel 47 | 47 | 3075 | [5 empty] | R
| Branch Alarm Status - Channel 48 | 48 | 3076 | [5 empty] | R
| Branch Alarm Status - Channel 49 | 49 | 3077 | [5 empty] | R
| Branch Alarm Status - Channel 50 | 50 | 3078 | [5 empty] | R
| Branch Alarm Status - Channel 51 | 51 | 3079 | [5 empty] | R
| Branch Alarm Status - Channel 52 | 52 | 3080 | [5 empty] | R
| Branch Alarm Status - Channel 53 | 53 | 3081 | [5 empty] | R
| Branch Alarm Status - Channel 54 | 54 | 3082 | [5 empty] | R
| Branch Alarm Status - Channel 55 | 55 | 3083 | [5 empty] | R
| Branch Alarm Status - Channel 56 | 56 | 3084 | [5 empty] | R
| Branch Alarm Status - Channel 57 | 57 | 3085 | [5 empty] | R
| Branch Alarm Status - Channel 58 | 58 | 3086 | [5 empty] | R
| Branch Alarm Status - Channel 59 | 59 | 3087 | [5 empty] | R
| Branch Alarm Status - Channel 60 | 60 | 3088 | [5 empty] | R
| Branch Alarm Status - Channel 61 | 61 | 3089 | [5 empty] | R
| Branch Alarm Status - Channel 62 | 62 | 3090 | [5 empty] | R
| Branch Alarm Status - Channel 63 | 63 | 3091 | [5 empty] | R
| Branch Alarm Status - Channel 64 | 64 | 3092 | [5 empty] | R
| Branch Alarm Status - Channel 65 | 65 | 3093 | [5 empty] | R
| Branch Alarm Status - Channel 66 | 66 | 3094 | [5 empty] | R
| Branch Alarm Status - Channel 67 | 67 | 3095 | [5 empty] | R
| Branch Alarm Status - Channel 68 | 68 | 3096 | [5 empty] | R
| Branch Alarm Status - Channel 69 | 69 | 3097 | [5 empty] | R
| Branch Alarm Status - Channel 70 | 70 | 3098 | [5 empty] | R
| Branch Alarm Status - Channel 71 | 71 | 3099 | [5 empty] | R
| Branch Alarm Status - Channel 72 | 72 | 3100 | [5 empty] | R
| Branch Alarm Status - Channel 73 | 73 | 3101 | [5 empty] | R
| Branch Alarm Status - Channel 74 | 74 | 3102 | [5 empty] | R
| Branch Alarm Status - Channel 75 | 75 | 3103 | [5 empty] | R
| Branch Alarm Status - Channel 76 | 76 | 3104 | [5 empty] | R
| Branch Alarm Status - Channel 77 | 77 | 3105 | [5 empty] | R
| Branch Alarm Status - Channel 78 | 78 | 3106 | [5 empty] | R
| Branch Alarm Status - Channel 79 | 79 | 3107 | [5 empty] | R
| Branch Alarm Status - Channel 80 | 80 | 3108 | [5 empty] | R
| Branch Alarm Status - Channel 81 | 81 | 3109 | [5 empty] | R
| Branch Alarm Status - Channel 82 | 82 | 3110 | [5 empty] | R
| Branch Alarm Status - Channel 83 | 83 | 3111 | [5 empty] | R
| Branch Alarm Status - Channel 84 | 84 | 3112 | [5 empty] | R
| Branch Alarm Status - Channel 85 | 85 | 3113 | [5 empty] | R
| Branch Alarm Status - Channel 86 | 86 | 3114 | [5 empty] | R
| Branch Alarm Status - Channel 87 | 87 | 3115 | [5 empty] | R
| Branch Alarm Status - Channel 88 | 88 | 3116 | [5 empty] | R
| Branch Alarm Status - Channel 89 | 89 | 3117 | [5 empty] | R
| Branch Alarm Status - Channel 90 | 90 | 3118 | [5 empty] | R
| Branch Alarm Status - Channel 91 | 91 | 3119 | [5 empty] | R
| Branch Alarm Status - Channel 92 | 92 | 3120 | [5 empty] | R
| Branch Alarm Status - Channel 93 | 93 | 3121 | [5 empty] | R
| Branch Alarm Status - Channel 94 | 94 | 3122 | [5 empty] | R
| Branch Alarm Status - Channel 95 | 95 | 3123 | [5 empty] | R
| Branch Alarm Status - Channel 96 | 96 | 3124 | [5 empty] | R
| Voltage Presence |  | 3125 | 3220
| Branch Voltage Presence - Channel 1 | 1 | 3125 | [5 empty] | R
| Branch Voltage Presence - Channel 2 | 2 | 3126 | [5 empty] | R
| Branch Voltage Presence - Channel 3 | 3 | 3127 | [5 empty] | R
| Branch Voltage Presence - Channel 4 | 4 | 3128 | [5 empty] | R
| Branch Voltage Presence - Channel 5 | 5 | 3129 | [5 empty] | R
| Branch Voltage Presence - Channel 6 | 6 | 3130 | [5 empty] | R
| Branch Voltage Presence - Channel 7 | 7 | 3131 | [5 empty] | R
| Branch Voltage Presence - Channel 8 | 8 | 3132 | [5 empty] | R
| Branch Voltage Presence - Channel 9 | 9 | 3133 | [5 empty] | R
| Branch Voltage Presence - Channel 10 | 10 | 3134 | [5 empty] | R
| Branch Voltage Presence - Channel 11 | 11 | 3135 | [5 empty] | R
| Branch Voltage Presence - Channel 12 | 12 | 3136 | [5 empty] | R
| Branch Voltage Presence - Channel 13 | 13 | 3137 | [5 empty] | R
| Branch Voltage Presence - Channel 14 | 14 | 3138 | [5 empty] | R
| Branch Voltage Presence - Channel 15 | 15 | 3139 | [5 empty] | R
| Branch Voltage Presence - Channel 16 | 16 | 3140 | [5 empty] | R
| Branch Voltage Presence - Channel 17 | 17 | 3141 | [5 empty] | R
| Branch Voltage Presence - Channel 18 | 18 | 3142 | [5 empty] | R
| Branch Voltage Presence - Channel 19 | 19 | 3143 | [5 empty] | R
| Branch Voltage Presence - Channel 20 | 20 | 3144 | [5 empty] | R
| Branch Voltage Presence - Channel 21 | 21 | 3145 | [5 empty] | R
| Branch Voltage Presence - Channel 22 | 22 | 3146 | [5 empty] | R
| Branch Voltage Presence - Channel 23 | 23 | 3147 | [5 empty] | R
| Branch Voltage Presence - Channel 24 | 24 | 3148 | [5 empty] | R
| Branch Voltage Presence - Channel 25 | 25 | 3149 | [5 empty] | R
| Branch Voltage Presence - Channel 26 | 26 | 3150 | [5 empty] | R
| Branch Voltage Presence - Channel 27 | 27 | 3151 | [5 empty] | R
| Branch Voltage Presence - Channel 28 | 28 | 3152 | [5 empty] | R
| Branch Voltage Presence - Channel 29 | 29 | 3153 | [5 empty] | R
| Branch Voltage Presence - Channel 30 | 30 | 3154 | [5 empty] | R
| Branch Voltage Presence - Channel 31 | 31 | 3155 | [5 empty] | R
| Branch Voltage Presence - Channel 32 | 32 | 3156 | [5 empty] | R
| Branch Voltage Presence - Channel 33 | 33 | 3157 | [5 empty] | R
| Branch Voltage Presence - Channel 34 | 34 | 3158 | [5 empty] | R
| Branch Voltage Presence - Channel 35 | 35 | 3159 | [5 empty] | R
| Branch Voltage Presence - Channel 36 | 36 | 3160 | [5 empty] | R
| Branch Voltage Presence - Channel 37 | 37 | 3161 | [5 empty] | R
| Branch Voltage Presence - Channel 38 | 38 | 3162 | [5 empty] | R
| Branch Voltage Presence - Channel 39 | 39 | 3163 | [5 empty] | R
| Branch Voltage Presence - Channel 40 | 40 | 3164 | [5 empty] | R
| Branch Voltage Presence - Channel 41 | 41 | 3165 | [5 empty] | R
| Branch Voltage Presence - Channel 42 | 42 | 3166 | [5 empty] | R
| Branch Voltage Presence - Channel 43 | 43 | 3167 | [5 empty] | R
| Branch Voltage Presence - Channel 44 | 44 | 3168 | [5 empty] | R
| Branch Voltage Presence - Channel 45 | 45 | 3169 | [5 empty] | R
| Branch Voltage Presence - Channel 46 | 46 | 3170 | [5 empty] | R
| Branch Voltage Presence - Channel 47 | 47 | 3171 | [5 empty] | R
| Branch Voltage Presence - Channel 48 | 48 | 3172 | [5 empty] | R
| Branch Voltage Presence - Channel 49 | 49 | 3173 | [5 empty] | R
| Branch Voltage Presence - Channel 50 | 50 | 3174 | [5 empty] | R
| Branch Voltage Presence - Channel 51 | 51 | 3175 | [5 empty] | R
| Branch Voltage Presence - Channel 52 | 52 | 3176 | [5 empty] | R
| Branch Voltage Presence - Channel 53 | 53 | 3177 | [5 empty] | R
| Branch Voltage Presence - Channel 54 | 54 | 3178 | [5 empty] | R
| Branch Voltage Presence - Channel 55 | 55 | 3179 | [5 empty] | R
| Branch Voltage Presence - Channel 56 | 56 | 3180 | [5 empty] | R
| Branch Voltage Presence - Channel 57 | 57 | 3181 | [5 empty] | R
| Branch Voltage Presence - Channel 58 | 58 | 3182 | [5 empty] | R
| Branch Voltage Presence - Channel 59 | 59 | 3183 | [5 empty] | R
| Branch Voltage Presence - Channel 60 | 60 | 3184 | [5 empty] | R
| Branch Voltage Presence - Channel 61 | 61 | 3185 | [5 empty] | R
| Branch Voltage Presence - Channel 62 | 62 | 3186 | [5 empty] | R
| Branch Voltage Presence - Channel 63 | 63 | 3187 | [5 empty] | R
| Branch Voltage Presence - Channel 64 | 64 | 3188 | [5 empty] | R
| Branch Voltage Presence - Channel 65 | 65 | 3189 | [5 empty] | R
| Branch Voltage Presence - Channel 66 | 66 | 3190 | [5 empty] | R
| Branch Voltage Presence - Channel 67 | 67 | 3191 | [5 empty] | R
| Branch Voltage Presence - Channel 68 | 68 | 3192 | [5 empty] | R
| Branch Voltage Presence - Channel 69 | 69 | 3193 | [5 empty] | R
| Branch Voltage Presence - Channel 70 | 70 | 3194 | [5 empty] | R
| Branch Voltage Presence - Channel 71 | 71 | 3195 | [5 empty] | R
| Branch Voltage Presence - Channel 72 | 72 | 3196 | [5 empty] | R
| Branch Voltage Presence - Channel 73 | 73 | 3197 | [5 empty] | R
| Branch Voltage Presence - Channel 74 | 74 | 3198 | [5 empty] | R
| Branch Voltage Presence - Channel 75 | 75 | 3199 | [5 empty] | R
| Branch Voltage Presence - Channel 76 | 76 | 3200 | [5 empty] | R
| Branch Voltage Presence - Channel 77 | 77 | 3201 | [5 empty] | R
| Branch Voltage Presence - Channel 78 | 78 | 3202 | [5 empty] | R
| Branch Voltage Presence - Channel 79 | 79 | 3203 | [5 empty] | R
| Branch Voltage Presence - Channel 80 | 80 | 3204 | [5 empty] | R
| Branch Voltage Presence - Channel 81 | 81 | 3205 | [5 empty] | R
| Branch Voltage Presence - Channel 82 | 82 | 3206 | [5 empty] | R
| Branch Voltage Presence - Channel 83 | 83 | 3207 | [5 empty] | R
| Branch Voltage Presence - Channel 84 | 84 | 3208 | [5 empty] | R
| Branch Voltage Presence - Channel 85 | 85 | 3209 | [5 empty] | R
| Branch Voltage Presence - Channel 86 | 86 | 3210 | [5 empty] | R
| Branch Voltage Presence - Channel 87 | 87 | 3211 | [5 empty] | R
| Branch Voltage Presence - Channel 88 | 88 | 3212 | [5 empty] | R
| Branch Voltage Presence - Channel 89 | 89 | 3213 | [5 empty] | R
| Branch Voltage Presence - Channel 90 | 90 | 3214 | [5 empty] | R
| Branch Voltage Presence - Channel 91 | 91 | 3215 | [5 empty] | R
| Branch Voltage Presence - Channel 92 | 92 | 3216 | [5 empty] | R
| Branch Voltage Presence - Channel 93 | 93 | 3217 | [5 empty] | R
| Branch Voltage Presence - Channel 94 | 94 | 3218 | [5 empty] | R
| Branch Voltage Presence - Channel 95 | 95 | 3219 | [5 empty] | R
| Branch Voltage Presence - Channel 96 | 96 | 3220 | [5 empty] | R
| Predictive Health |  | 3221 | 3316
| Predictive Health - Channel 1 | 1 | 3221 | [5 empty] | R
| Predictive Health - Channel 2 | 2 | 3222 | [5 empty] | R
| Predictive Health - Channel 3 | 3 | 3223 | [5 empty] | R
| Predictive Health - Channel 4 | 4 | 3224 | [5 empty] | R
| Predictive Health - Channel 5 | 5 | 3225 | [5 empty] | R
| Predictive Health - Channel 6 | 6 | 3226 | [5 empty] | R
| Predictive Health - Channel 7 | 7 | 3227 | [5 empty] | R
| Predictive Health - Channel 8 | 8 | 3228 | [5 empty] | R
| Predictive Health - Channel 9 | 9 | 3229 | [5 empty] | R
| Predictive Health - Channel 10 | 10 | 3230 | [5 empty] | R
| Predictive Health - Channel 11 | 11 | 3231 | [5 empty] | R
| Predictive Health - Channel 12 | 12 | 3232 | [5 empty] | R
| Predictive Health - Channel 13 | 13 | 3233 | [5 empty] | R
| Predictive Health - Channel 14 | 14 | 3234 | [5 empty] | R
| Predictive Health - Channel 15 | 15 | 3235 | [5 empty] | R
| Predictive Health - Channel 16 | 16 | 3236 | [5 empty] | R
| Predictive Health - Channel 17 | 17 | 3237 | [5 empty] | R
| Predictive Health - Channel 18 | 18 | 3238 | [5 empty] | R
| Predictive Health - Channel 19 | 19 | 3239 | [5 empty] | R
| Predictive Health - Channel 20 | 20 | 3240 | [5 empty] | R
| Predictive Health - Channel 21 | 21 | 3241 | [5 empty] | R
| Predictive Health - Channel 22 | 22 | 3242 | [5 empty] | R
| Predictive Health - Channel 23 | 23 | 3243 | [5 empty] | R
| Predictive Health - Channel 24 | 24 | 3244 | [5 empty] | R
| Predictive Health - Channel 25 | 25 | 3245 | [5 empty] | R
| Predictive Health - Channel 26 | 26 | 3246 | [5 empty] | R
| Predictive Health - Channel 27 | 27 | 3247 | [5 empty] | R
| Predictive Health - Channel 28 | 28 | 3248 | [5 empty] | R
| Predictive Health - Channel 29 | 29 | 3249 | [5 empty] | R
| Predictive Health - Channel 30 | 30 | 3250 | [5 empty] | R
| Predictive Health - Channel 31 | 31 | 3251 | [5 empty] | R
| Predictive Health - Channel 32 | 32 | 3252 | [5 empty] | R
| Predictive Health - Channel 33 | 33 | 3253 | [5 empty] | R
| Predictive Health - Channel 34 | 34 | 3254 | [5 empty] | R
| Predictive Health - Channel 35 | 35 | 3255 | [5 empty] | R
| Predictive Health - Channel 36 | 36 | 3256 | [5 empty] | R
| Predictive Health - Channel 37 | 37 | 3257 | [5 empty] | R
| Predictive Health - Channel 38 | 38 | 3258 | [5 empty] | R
| Predictive Health - Channel 39 | 39 | 3259 | [5 empty] | R
| Predictive Health - Channel 40 | 40 | 3260 | [5 empty] | R
| Predictive Health - Channel 41 | 41 | 3261 | [5 empty] | R
| Predictive Health - Channel 42 | 42 | 3262 | [5 empty] | R
| Predictive Health - Channel 43 | 43 | 3263 | [5 empty] | R
| Predictive Health - Channel 44 | 44 | 3264 | [5 empty] | R
| Predictive Health - Channel 45 | 45 | 3265 | [5 empty] | R
| Predictive Health - Channel 46 | 46 | 3266 | [5 empty] | R
| Predictive Health - Channel 47 | 47 | 3267 | [5 empty] | R
| Predictive Health - Channel 48 | 48 | 3268 | [5 empty] | R
| Predictive Health - Channel 49 | 49 | 3269 | [5 empty] | R
| Predictive Health - Channel 50 | 50 | 3270 | [5 empty] | R
| Predictive Health - Channel 51 | 51 | 3271 | [5 empty] | R
| Predictive Health - Channel 52 | 52 | 3272 | [5 empty] | R
| Predictive Health - Channel 53 | 53 | 3273 | [5 empty] | R
| Predictive Health - Channel 54 | 54 | 3274 | [5 empty] | R
| Predictive Health - Channel 55 | 55 | 3275 | [5 empty] | R
| Predictive Health - Channel 56 | 56 | 3276 | [5 empty] | R
| Predictive Health - Channel 57 | 57 | 3277 | [5 empty] | R
| Predictive Health - Channel 58 | 58 | 3278 | [5 empty] | R
| Predictive Health - Channel 59 | 59 | 3279 | [5 empty] | R
| Predictive Health - Channel 60 | 60 | 3280 | [5 empty] | R
| Predictive Health - Channel 61 | 61 | 3281 | [5 empty] | R
| Predictive Health - Channel 62 | 62 | 3282 | [5 empty] | R
| Predictive Health - Channel 63 | 63 | 3283 | [5 empty] | R
| Predictive Health - Channel 64 | 64 | 3284 | [5 empty] | R
| Predictive Health - Channel 65 | 65 | 3285 | [5 empty] | R
| Predictive Health - Channel 66 | 66 | 3286 | [5 empty] | R
| Predictive Health - Channel 67 | 67 | 3287 | [5 empty] | R
| Predictive Health - Channel 68 | 68 | 3288 | [5 empty] | R
| Predictive Health - Channel 69 | 69 | 3289 | [5 empty] | R
| Predictive Health - Channel 70 | 70 | 3290 | [5 empty] | R
| Predictive Health - Channel 71 | 71 | 3291 | [5 empty] | R
| Predictive Health - Channel 72 | 72 | 3292 | [5 empty] | R
| Predictive Health - Channel 73 | 73 | 3293 | [5 empty] | R
| Predictive Health - Channel 74 | 74 | 3294 | [5 empty] | R
| Predictive Health - Channel 75 | 75 | 3295 | [5 empty] | R
| Predictive Health - Channel 76 | 76 | 3296 | [5 empty] | R
| Predictive Health - Channel 77 | 77 | 3297 | [5 empty] | R
| Predictive Health - Channel 78 | 78 | 3298 | [5 empty] | R
| Predictive Health - Channel 79 | 79 | 3299 | [5 empty] | R
| Predictive Health - Channel 80 | 80 | 3300 | [5 empty] | R
| Predictive Health - Channel 81 | 81 | 3301 | [5 empty] | R
| Predictive Health - Channel 82 | 82 | 3302 | [5 empty] | R
| Predictive Health - Channel 83 | 83 | 3303 | [5 empty] | R
| Predictive Health - Channel 84 | 84 | 3304 | [5 empty] | R
| Predictive Health - Channel 85 | 85 | 3305 | [5 empty] | R
| Predictive Health - Channel 86 | 86 | 3306 | [5 empty] | R
| Predictive Health - Channel 87 | 87 | 3307 | [5 empty] | R
| Predictive Health - Channel 88 | 88 | 3308 | [5 empty] | R
| Predictive Health - Channel 89 | 89 | 3309 | [5 empty] | R
| Predictive Health - Channel 90 | 90 | 3310 | [5 empty] | R
| Predictive Health - Channel 91 | 91 | 3311 | [5 empty] | R
| Predictive Health - Channel 92 | 92 | 3312 | [5 empty] | R
| Predictive Health - Channel 93 | 93 | 3313 | [5 empty] | R
| Predictive Health - Channel 94 | 94 | 3314 | [5 empty] | R
| Predictive Health - Channel 95 | 95 | 3315 | [5 empty] | R
| Predictive Health - Channel 96 | 96 | 3316 | [5 empty] | R
| Zero Current State |  | 3317 | 3412
| Branch Zero Current State - Channel 1 | 1 | 3317 | [5 empty] | R
| Branch Zero Current State - Channel 2 | 2 | 3318 | [5 empty] | R
| Branch Zero Current State - Channel 3 | 3 | 3319 | [5 empty] | R
| Branch Zero Current State - Channel 4 | 4 | 3320 | [5 empty] | R
| Branch Zero Current State - Channel 5 | 5 | 3321 | [5 empty] | R
| Branch Zero Current State - Channel 6 | 6 | 3322 | [5 empty] | R
| Branch Zero Current State - Channel 7 | 7 | 3323 | [5 empty] | R
| Branch Zero Current State - Channel 8 | 8 | 3324 | [5 empty] | R
| Branch Zero Current State - Channel 9 | 9 | 3325 | [5 empty] | R
| Branch Zero Current State - Channel 10 | 10 | 3326 | [5 empty] | R
| Branch Zero Current State - Channel 11 | 11 | 3327 | [5 empty] | R
| Branch Zero Current State - Channel 12 | 12 | 3328 | [5 empty] | R
| Branch Zero Current State - Channel 13 | 13 | 3329 | [5 empty] | R
| Branch Zero Current State - Channel 14 | 14 | 3330 | [5 empty] | R
| Branch Zero Current State - Channel 15 | 15 | 3331 | [5 empty] | R
| Branch Zero Current State - Channel 16 | 16 | 3332 | [5 empty] | R
| Branch Zero Current State - Channel 17 | 17 | 3333 | [5 empty] | R
| Branch Zero Current State - Channel 18 | 18 | 3334 | [5 empty] | R
| Branch Zero Current State - Channel 19 | 19 | 3335 | [5 empty] | R
| Branch Zero Current State - Channel 20 | 20 | 3336 | [5 empty] | R
| Branch Zero Current State - Channel 21 | 21 | 3337 | [5 empty] | R
| Branch Zero Current State - Channel 22 | 22 | 3338 | [5 empty] | R
| Branch Zero Current State - Channel 23 | 23 | 3339 | [5 empty] | R
| Branch Zero Current State - Channel 24 | 24 | 3340 | [5 empty] | R
| Branch Zero Current State - Channel 25 | 25 | 3341 | [5 empty] | R
| Branch Zero Current State - Channel 26 | 26 | 3342 | [5 empty] | R
| Branch Zero Current State - Channel 27 | 27 | 3343 | [5 empty] | R
| Branch Zero Current State - Channel 28 | 28 | 3344 | [5 empty] | R
| Branch Zero Current State - Channel 29 | 29 | 3345 | [5 empty] | R
| Branch Zero Current State - Channel 30 | 30 | 3346 | [5 empty] | R
| Branch Zero Current State - Channel 31 | 31 | 3347 | [5 empty] | R
| Branch Zero Current State - Channel 32 | 32 | 3348 | [5 empty] | R
| Branch Zero Current State - Channel 33 | 33 | 3349 | [5 empty] | R
| Branch Zero Current State - Channel 34 | 34 | 3350 | [5 empty] | R
| Branch Zero Current State - Channel 35 | 35 | 3351 | [5 empty] | R
| Branch Zero Current State - Channel 36 | 36 | 3352 | [5 empty] | R
| Branch Zero Current State - Channel 37 | 37 | 3353 | [5 empty] | R
| Branch Zero Current State - Channel 38 | 38 | 3354 | [5 empty] | R
| Branch Zero Current State - Channel 39 | 39 | 3355 | [5 empty] | R
| Branch Zero Current State - Channel 40 | 40 | 3356 | [5 empty] | R
| Branch Zero Current State - Channel 41 | 41 | 3357 | [5 empty] | R
| Branch Zero Current State - Channel 42 | 42 | 3358 | [5 empty] | R
| Branch Zero Current State - Channel 43 | 43 | 3359 | [5 empty] | R
| Branch Zero Current State - Channel 44 | 44 | 3360 | [5 empty] | R
| Branch Zero Current State - Channel 45 | 45 | 3361 | [5 empty] | R
| Branch Zero Current State - Channel 46 | 46 | 3362 | [5 empty] | R
| Branch Zero Current State - Channel 47 | 47 | 3363 | [5 empty] | R
| Branch Zero Current State - Channel 48 | 48 | 3364 | [5 empty] | R
| Branch Zero Current State - Channel 49 | 49 | 3365 | [5 empty] | R
| Branch Zero Current State - Channel 50 | 50 | 3366 | [5 empty] | R
| Branch Zero Current State - Channel 51 | 51 | 3367 | [5 empty] | R
| Branch Zero Current State - Channel 52 | 52 | 3368 | [5 empty] | R
| Branch Zero Current State - Channel 53 | 53 | 3369 | [5 empty] | R
| Branch Zero Current State - Channel 54 | 54 | 3370 | [5 empty] | R
| Branch Zero Current State - Channel 55 | 55 | 3371 | [5 empty] | R
| Branch Zero Current State - Channel 56 | 56 | 3372 | [5 empty] | R
| Branch Zero Current State - Channel 57 | 57 | 3373 | [5 empty] | R
| Branch Zero Current State - Channel 58 | 58 | 3374 | [5 empty] | R
| Branch Zero Current State - Channel 59 | 59 | 3375 | [5 empty] | R
| Branch Zero Current State - Channel 60 | 60 | 3376 | [5 empty] | R
| Branch Zero Current State - Channel 61 | 61 | 3377 | [5 empty] | R
| Branch Zero Current State - Channel 62 | 62 | 3378 | [5 empty] | R
| Branch Zero Current State - Channel 63 | 63 | 3379 | [5 empty] | R
| Branch Zero Current State - Channel 64 | 64 | 3380 | [5 empty] | R
| Branch Zero Current State - Channel 65 | 65 | 3381 | [5 empty] | R
| Branch Zero Current State - Channel 66 | 66 | 3382 | [5 empty] | R
| Branch Zero Current State - Channel 67 | 67 | 3383 | [5 empty] | R
| Branch Zero Current State - Channel 68 | 68 | 3384 | [5 empty] | R
| Branch Zero Current State - Channel 69 | 69 | 3385 | [5 empty] | R
| Branch Zero Current State - Channel 70 | 70 | 3386 | [5 empty] | R
| Branch Zero Current State - Channel 71 | 71 | 3387 | [5 empty] | R
| Branch Zero Current State - Channel 72 | 72 | 3388 | [5 empty] | R
| Branch Zero Current State - Channel 73 | 73 | 3389 | [5 empty] | R
| Branch Zero Current State - Channel 74 | 74 | 3390 | [5 empty] | R
| Branch Zero Current State - Channel 75 | 75 | 3391 | [5 empty] | R
| Branch Zero Current State - Channel 76 | 76 | 3392 | [5 empty] | R
| Branch Zero Current State - Channel 77 | 77 | 3393 | [5 empty] | R
| Branch Zero Current State - Channel 78 | 78 | 3394 | [5 empty] | R
| Branch Zero Current State - Channel 79 | 79 | 3395 | [5 empty] | R
| Branch Zero Current State - Channel 80 | 80 | 3396 | [5 empty] | R
| Branch Zero Current State - Channel 81 | 81 | 3397 | [5 empty] | R
| Branch Zero Current State - Channel 82 | 82 | 3398 | [5 empty] | R
| Branch Zero Current State - Channel 83 | 83 | 3399 | [5 empty] | R
| Branch Zero Current State - Channel 84 | 84 | 3400 | [5 empty] | R
| Branch Zero Current State - Channel 85 | 85 | 3401 | [5 empty] | R
| Branch Zero Current State - Channel 86 | 86 | 3402 | [5 empty] | R
| Branch Zero Current State - Channel 87 | 87 | 3403 | [5 empty] | R
| Branch Zero Current State - Channel 88 | 88 | 3404 | [5 empty] | R
| Branch Zero Current State - Channel 89 | 89 | 3405 | [5 empty] | R
| Branch Zero Current State - Channel 90 | 90 | 3406 | [5 empty] | R
| Branch Zero Current State - Channel 91 | 91 | 3407 | [5 empty] | R
| Branch Zero Current State - Channel 92 | 92 | 3408 | [5 empty] | R
| Branch Zero Current State - Channel 93 | 93 | 3409 | [5 empty] | R
| Branch Zero Current State - Channel 94 | 94 | 3410 | [5 empty] | R
| Branch Zero Current State - Channel 95 | 95 | 3411 | [5 empty] | R
| Branch Zero Current State - Channel 96 | 96 | 3412 | [5 empty] | R
Voltage Readings
| Voltage Scale |  | 4800
| Frequency |  | 4801 |  | 4900 | 4901
| Voltage LN Average |  | 4802 |  | 4902 | 4903
| Voltage LL Average |  | 4803 |  | 4904 | 4905
| Voltage LN |  | 4804 | 4806 | 4906 | 4909
| Voltage L1 |  | 4804 |  | 4906 | 4907
| Voltage L2 |  | 4805 |  | 4907 | 4908
| Voltage L3 |  | 4806 |  | 4908 | 4909
| Voltage LL |  | 4807 | 4809 | 4910 | 4913
| Voltage L1 - L2 |  | 4807 |  | 4910 | 4911
| Voltage L2 - L3 |  | 4808 |  | 4911 | 4912
| Voltage L3 - L1 |  | 4809 |  | 4912 | 4913
| Voltage Angle |  | 4810 | 4812 | 4914 | 4917
| Voltage Angle L1 |  | 4810 |  | 4914 | 4915 | [6 empty] | Always Read 0
| Voltage Angle L2 |  | 4811 |  | 4915 | 4916
| Voltage Angle L3 |  | 4812 |  | 4916 | 4917
| Percent THD |  | 4813 | 4815 | 4918 | 4921
| Percent THD - L1 |  | 4813 |  | 4918 | 4919 | [6 empty] | Always Reads 0
| Percent THD - L2 |  | 4814 |  | 4919 | 4920
| Percent THD - L3 |  | 4815 |  | 4920 | 4921
| Voltage Angle |  | 4816 | 4818 | 4922 | 4925
| L1 Angle |  | 4816 |  | 4922 | 4923 | [6 empty] | Always Reads 0
| L2 Angle |  | 4817 |  | 4923 | 4924
| L3 Angle |  | 4818 |  | 4924 | 4925
Single Phase Reading by Type
| Energy Scale |  | 5000 | 5095 |  |  |  |  | R
| Energy Scale - Channel 1 | 1 | 5000 | [5 empty] | R
| Energy Scale - Channel 2 | 2 | 5001 | [5 empty] | R
| Energy Scale - Channel 3 | 3 | 5002 | [5 empty] | R
| Energy Scale - Channel 4 | 4 | 5003 | [5 empty] | R
| Energy Scale - Channel 5 | 5 | 5004 | [5 empty] | R
| Energy Scale - Channel 6 | 6 | 5005 | [5 empty] | R
| Energy Scale - Channel 7 | 7 | 5006 | [5 empty] | R
| Energy Scale - Channel 8 | 8 | 5007 | [5 empty] | R
| Energy Scale - Channel 9 | 9 | 5008 | [5 empty] | R
| Energy Scale - Channel 10 | 10 | 5009 | [5 empty] | R
| Energy Scale - Channel 11 | 11 | 5010 | [5 empty] | R
| Energy Scale - Channel 12 | 12 | 5011 | [5 empty] | R
| Energy Scale - Channel 13 | 13 | 5012 | [5 empty] | R
| Energy Scale - Channel 14 | 14 | 5013 | [5 empty] | R
| Energy Scale - Channel 15 | 15 | 5014 | [5 empty] | R
| Energy Scale - Channel 16 | 16 | 5015 | [5 empty] | R
| Energy Scale - Channel 17 | 17 | 5016 | [5 empty] | R
| Energy Scale - Channel 18 | 18 | 5017 | [5 empty] | R
| Energy Scale - Channel 19 | 19 | 5018 | [5 empty] | R
| Energy Scale - Channel 20 | 20 | 5019 | [5 empty] | R
| Energy Scale - Channel 21 | 21 | 5020 | [5 empty] | R
| Energy Scale - Channel 22 | 22 | 5021 | [5 empty] | R
| Energy Scale - Channel 23 | 23 | 5022 | [5 empty] | R
| Energy Scale - Channel 24 | 24 | 5023 | [5 empty] | R
| Energy Scale - Channel 25 | 25 | 5024 | [5 empty] | R
| Energy Scale - Channel 26 | 26 | 5025 | [5 empty] | R
| Energy Scale - Channel 27 | 27 | 5026 | [5 empty] | R
| Energy Scale - Channel 28 | 28 | 5027 | [5 empty] | R
| Energy Scale - Channel 29 | 29 | 5028 | [5 empty] | R
| Energy Scale - Channel 30 | 30 | 5029 | [5 empty] | R
| Energy Scale - Channel 31 | 31 | 5030 | [5 empty] | R
| Energy Scale - Channel 32 | 32 | 5031 | [5 empty] | R
| Energy Scale - Channel 33 | 33 | 5032 | [5 empty] | R
| Energy Scale - Channel 34 | 34 | 5033 | [5 empty] | R
| Energy Scale - Channel 35 | 35 | 5034 | [5 empty] | R
| Energy Scale - Channel 36 | 36 | 5035 | [5 empty] | R
| Energy Scale - Channel 37 | 37 | 5036 | [5 empty] | R
| Energy Scale - Channel 38 | 38 | 5037 | [5 empty] | R
| Energy Scale - Channel 39 | 39 | 5038 | [5 empty] | R
| Energy Scale - Channel 40 | 40 | 5039 | [5 empty] | R
| Energy Scale - Channel 41 | 41 | 5040 | [5 empty] | R
| Energy Scale - Channel 42 | 42 | 5041 | [5 empty] | R
| Energy Scale - Channel 43 | 43 | 5042 | [5 empty] | R
| Energy Scale - Channel 44 | 44 | 5043 | [5 empty] | R
| Energy Scale - Channel 45 | 45 | 5044 | [5 empty] | R
| Energy Scale - Channel 46 | 46 | 5045 | [5 empty] | R
| Energy Scale - Channel 47 | 47 | 5046 | [5 empty] | R
| Energy Scale - Channel 48 | 48 | 5047 | [5 empty] | R
| Energy Scale - Channel 49 | 49 | 5048 | [5 empty] | R
| Energy Scale - Channel 50 | 50 | 5049 | [5 empty] | R
| Energy Scale - Channel 51 | 51 | 5050 | [5 empty] | R
| Energy Scale - Channel 52 | 52 | 5051 | [5 empty] | R
| Energy Scale - Channel 53 | 53 | 5052 | [5 empty] | R
| Energy Scale - Channel 54 | 54 | 5053 | [5 empty] | R
| Energy Scale - Channel 55 | 55 | 5054 | [5 empty] | R
| Energy Scale - Channel 56 | 56 | 5055 | [5 empty] | R
| Energy Scale - Channel 57 | 57 | 5056 | [5 empty] | R
| Energy Scale - Channel 58 | 58 | 5057 | [5 empty] | R
| Energy Scale - Channel 59 | 59 | 5058 | [5 empty] | R
| Energy Scale - Channel 60 | 60 | 5059 | [5 empty] | R
| Energy Scale - Channel 61 | 61 | 5060 | [5 empty] | R
| Energy Scale - Channel 62 | 62 | 5061 | [5 empty] | R
| Energy Scale - Channel 63 | 63 | 5062 | [5 empty] | R
| Energy Scale - Channel 64 | 64 | 5063 | [5 empty] | R
| Energy Scale - Channel 65 | 65 | 5064 | [5 empty] | R
| Energy Scale - Channel 66 | 66 | 5065 | [5 empty] | R
| Energy Scale - Channel 67 | 67 | 5066 | [5 empty] | R
| Energy Scale - Channel 68 | 68 | 5067 | [5 empty] | R
| Energy Scale - Channel 69 | 69 | 5068 | [5 empty] | R
| Energy Scale - Channel 70 | 70 | 5069 | [5 empty] | R
| Energy Scale - Channel 71 | 71 | 5070 | [5 empty] | R
| Energy Scale - Channel 72 | 72 | 5071 | [5 empty] | R
| Energy Scale - Channel 73 | 73 | 5072 | [5 empty] | R
| Energy Scale - Channel 74 | 74 | 5073 | [5 empty] | R
| Energy Scale - Channel 75 | 75 | 5074 | [5 empty] | R
| Energy Scale - Channel 76 | 76 | 5075 | [5 empty] | R
| Energy Scale - Channel 77 | 77 | 5076 | [5 empty] | R
| Energy Scale - Channel 78 | 78 | 5077 | [5 empty] | R
| Energy Scale - Channel 79 | 79 | 5078 | [5 empty] | R
| Energy Scale - Channel 80 | 80 | 5079 | [5 empty] | R
| Energy Scale - Channel 81 | 81 | 5080 | [5 empty] | R
| Energy Scale - Channel 82 | 82 | 5081 | [5 empty] | R
| Energy Scale - Channel 83 | 83 | 5082 | [5 empty] | R
| Energy Scale - Channel 84 | 84 | 5083 | [5 empty] | R
| Energy Scale - Channel 85 | 85 | 5084 | [5 empty] | R
| Energy Scale - Channel 86 | 86 | 5085 | [5 empty] | R
| Energy Scale - Channel 87 | 87 | 5086 | [5 empty] | R
| Energy Scale - Channel 88 | 88 | 5087 | [5 empty] | R
| Energy Scale - Channel 89 | 89 | 5088 | [5 empty] | R
| Energy Scale - Channel 90 | 90 | 5089 | [5 empty] | R
| Energy Scale - Channel 91 | 91 | 5090 | [5 empty] | R
| Energy Scale - Channel 92 | 92 | 5091 | [5 empty] | R
| Energy Scale - Channel 93 | 93 | 5092 | [5 empty] | R
| Energy Scale - Channel 94 | 94 | 5093 | [5 empty] | R
| Energy Scale - Channel 95 | 95 | 5094 | [5 empty] | R
| Energy Scale - Channel 96 | 96 | 5095 | [5 empty] | R
| Power Scale |  | 5096 | 5191 |  |  |  |  | R
| Power Scale - Channel 1 | 1 | 5096 | [5 empty] | R
| Power Scale - Channel 2 | 2 | 5097 | [5 empty] | R
| Power Scale - Channel 3 | 3 | 5098 | [5 empty] | R
| Power Scale - Channel 4 | 4 | 5099 | [5 empty] | R
| Power Scale - Channel 5 | 5 | 5100 | [5 empty] | R
| Power Scale - Channel 6 | 6 | 5101 | [5 empty] | R
| Power Scale - Channel 7 | 7 | 5102 | [5 empty] | R
| Power Scale - Channel 8 | 8 | 5103 | [5 empty] | R
| Power Scale - Channel 9 | 9 | 5104 | [5 empty] | R
| Power Scale - Channel 10 | 10 | 5105 | [5 empty] | R
| Power Scale - Channel 11 | 11 | 5106 | [5 empty] | R
| Power Scale - Channel 12 | 12 | 5107 | [5 empty] | R
| Power Scale - Channel 13 | 13 | 5108 | [5 empty] | R
| Power Scale - Channel 14 | 14 | 5109 | [5 empty] | R
| Power Scale - Channel 15 | 15 | 5110 | [5 empty] | R
| Power Scale - Channel 16 | 16 | 5111 | [5 empty] | R
| Power Scale - Channel 17 | 17 | 5112 | [5 empty] | R
| Power Scale - Channel 18 | 18 | 5113 | [5 empty] | R
| Power Scale - Channel 19 | 19 | 5114 | [5 empty] | R
| Power Scale - Channel 20 | 20 | 5115 | [5 empty] | R
| Power Scale - Channel 21 | 21 | 5116 | [5 empty] | R
| Power Scale - Channel 22 | 22 | 5117 | [5 empty] | R
| Power Scale - Channel 23 | 23 | 5118 | [5 empty] | R
| Power Scale - Channel 24 | 24 | 5119 | [5 empty] | R
| Power Scale - Channel 25 | 25 | 5120 | [5 empty] | R
| Power Scale - Channel 26 | 26 | 5121 | [5 empty] | R
| Power Scale - Channel 27 | 27 | 5122 | [5 empty] | R
| Power Scale - Channel 28 | 28 | 5123 | [5 empty] | R
| Power Scale - Channel 29 | 29 | 5124 | [5 empty] | R
| Power Scale - Channel 30 | 30 | 5125 | [5 empty] | R
| Power Scale - Channel 31 | 31 | 5126 | [5 empty] | R
| Power Scale - Channel 32 | 32 | 5127 | [5 empty] | R
| Power Scale - Channel 33 | 33 | 5128 | [5 empty] | R
| Power Scale - Channel 34 | 34 | 5129 | [5 empty] | R
| Power Scale - Channel 35 | 35 | 5130 | [5 empty] | R
| Power Scale - Channel 36 | 36 | 5131 | [5 empty] | R
| Power Scale - Channel 37 | 37 | 5132 | [5 empty] | R
| Power Scale - Channel 38 | 38 | 5133 | [5 empty] | R
| Power Scale - Channel 39 | 39 | 5134 | [5 empty] | R
| Power Scale - Channel 40 | 40 | 5135 | [5 empty] | R
| Power Scale - Channel 41 | 41 | 5136 | [5 empty] | R
| Power Scale - Channel 42 | 42 | 5137 | [5 empty] | R
| Power Scale - Channel 43 | 43 | 5138 | [5 empty] | R
| Power Scale - Channel 44 | 44 | 5139 | [5 empty] | R
| Power Scale - Channel 45 | 45 | 5140 | [5 empty] | R
| Power Scale - Channel 46 | 46 | 5141 | [5 empty] | R
| Power Scale - Channel 47 | 47 | 5142 | [5 empty] | R
| Power Scale - Channel 48 | 48 | 5143 | [5 empty] | R
| Power Scale - Channel 49 | 49 | 5144 | [5 empty] | R
| Power Scale - Channel 50 | 50 | 5145 | [5 empty] | R
| Power Scale - Channel 51 | 51 | 5146 | [5 empty] | R
| Power Scale - Channel 52 | 52 | 5147 | [5 empty] | R
| Power Scale - Channel 53 | 53 | 5148 | [5 empty] | R
| Power Scale - Channel 54 | 54 | 5149 | [5 empty] | R
| Power Scale - Channel 55 | 55 | 5150 | [5 empty] | R
| Power Scale - Channel 56 | 56 | 5151 | [5 empty] | R
| Power Scale - Channel 57 | 57 | 5152 | [5 empty] | R
| Power Scale - Channel 58 | 58 | 5153 | [5 empty] | R
| Power Scale - Channel 59 | 59 | 5154 | [5 empty] | R
| Power Scale - Channel 60 | 60 | 5155 | [5 empty] | R
| Power Scale - Channel 61 | 61 | 5156 | [5 empty] | R
| Power Scale - Channel 62 | 62 | 5157 | [5 empty] | R
| Power Scale - Channel 63 | 63 | 5158 | [5 empty] | R
| Power Scale - Channel 64 | 64 | 5159 | [5 empty] | R
| Power Scale - Channel 65 | 65 | 5160 | [5 empty] | R
| Power Scale - Channel 66 | 66 | 5161 | [5 empty] | R
| Power Scale - Channel 67 | 67 | 5162 | [5 empty] | R
| Power Scale - Channel 68 | 68 | 5163 | [5 empty] | R
| Power Scale - Channel 69 | 69 | 5164 | [5 empty] | R
| Power Scale - Channel 70 | 70 | 5165 | [5 empty] | R
| Power Scale - Channel 71 | 71 | 5166 | [5 empty] | R
| Power Scale - Channel 72 | 72 | 5167 | [5 empty] | R
| Power Scale - Channel 73 | 73 | 5168 | [5 empty] | R
| Power Scale - Channel 74 | 74 | 5169 | [5 empty] | R
| Power Scale - Channel 75 | 75 | 5170 | [5 empty] | R
| Power Scale - Channel 76 | 76 | 5171 | [5 empty] | R
| Power Scale - Channel 77 | 77 | 5172 | [5 empty] | R
| Power Scale - Channel 78 | 78 | 5173 | [5 empty] | R
| Power Scale - Channel 79 | 79 | 5174 | [5 empty] | R
| Power Scale - Channel 80 | 80 | 5175 | [5 empty] | R
| Power Scale - Channel 81 | 81 | 5176 | [5 empty] | R
| Power Scale - Channel 82 | 82 | 5177 | [5 empty] | R
| Power Scale - Channel 83 | 83 | 5178 | [5 empty] | R
| Power Scale - Channel 84 | 84 | 5179 | [5 empty] | R
| Power Scale - Channel 85 | 85 | 5180 | [5 empty] | R
| Power Scale - Channel 86 | 86 | 5181 | [5 empty] | R
| Power Scale - Channel 87 | 87 | 5182 | [5 empty] | R
| Power Scale - Channel 88 | 88 | 5183 | [5 empty] | R
| Power Scale - Channel 89 | 89 | 5184 | [5 empty] | R
| Power Scale - Channel 90 | 90 | 5185 | [5 empty] | R
| Power Scale - Channel 91 | 91 | 5186 | [5 empty] | R
| Power Scale - Channel 92 | 92 | 5187 | [5 empty] | R
| Power Scale - Channel 93 | 93 | 5188 | [5 empty] | R
| Power Scale - Channel 94 | 94 | 5189 | [5 empty] | R
| Power Scale - Channel 95 | 95 | 5190 | [5 empty] | R
| Power Scale - Channel 96 | 96 | 5191 | [5 empty] | R
| Current Scale |  | 5192 | 5287 |  |  |  |  | R
| Current Scale - Channel 1 | 1 | 5192 | [5 empty] | R
| Current Scale - Channel 2 | 2 | 5193 | [5 empty] | R
| Current Scale - Channel 3 | 3 | 5194 | [5 empty] | R
| Current Scale - Channel 4 | 4 | 5195 | [5 empty] | R
| Current Scale - Channel 5 | 5 | 5196 | [5 empty] | R
| Current Scale - Channel 6 | 6 | 5197 | [5 empty] | R
| Current Scale - Channel 7 | 7 | 5198 | [5 empty] | R
| Current Scale - Channel 8 | 8 | 5199 | [5 empty] | R
| Current Scale - Channel 9 | 9 | 5200 | [5 empty] | R
| Current Scale - Channel 10 | 10 | 5201 | [5 empty] | R
| Current Scale - Channel 11 | 11 | 5202 | [5 empty] | R
| Current Scale - Channel 12 | 12 | 5203 | [5 empty] | R
| Current Scale - Channel 13 | 13 | 5204 | [5 empty] | R
| Current Scale - Channel 14 | 14 | 5205 | [5 empty] | R
| Current Scale - Channel 15 | 15 | 5206 | [5 empty] | R
| Current Scale - Channel 16 | 16 | 5207 | [5 empty] | R
| Current Scale - Channel 17 | 17 | 5208 | [5 empty] | R
| Current Scale - Channel 18 | 18 | 5209 | [5 empty] | R
| Current Scale - Channel 19 | 19 | 5210 | [5 empty] | R
| Current Scale - Channel 20 | 20 | 5211 | [5 empty] | R
| Current Scale - Channel 21 | 21 | 5212 | [5 empty] | R
| Current Scale - Channel 22 | 22 | 5213 | [5 empty] | R
| Current Scale - Channel 23 | 23 | 5214 | [5 empty] | R
| Current Scale - Channel 24 | 24 | 5215 | [5 empty] | R
| Current Scale - Channel 25 | 25 | 5216 | [5 empty] | R
| Current Scale - Channel 26 | 26 | 5217 | [5 empty] | R
| Current Scale - Channel 27 | 27 | 5218 | [5 empty] | R
| Current Scale - Channel 28 | 28 | 5219 | [5 empty] | R
| Current Scale - Channel 29 | 29 | 5220 | [5 empty] | R
| Current Scale - Channel 30 | 30 | 5221 | [5 empty] | R
| Current Scale - Channel 31 | 31 | 5222 | [5 empty] | R
| Current Scale - Channel 32 | 32 | 5223 | [5 empty] | R
| Current Scale - Channel 33 | 33 | 5224 | [5 empty] | R
| Current Scale - Channel 34 | 34 | 5225 | [5 empty] | R
| Current Scale - Channel 35 | 35 | 5226 | [5 empty] | R
| Current Scale - Channel 36 | 36 | 5227 | [5 empty] | R
| Current Scale - Channel 37 | 37 | 5228 | [5 empty] | R
| Current Scale - Channel 38 | 38 | 5229 | [5 empty] | R
| Current Scale - Channel 39 | 39 | 5230 | [5 empty] | R
| Current Scale - Channel 40 | 40 | 5231 | [5 empty] | R
| Current Scale - Channel 41 | 41 | 5232 | [5 empty] | R
| Current Scale - Channel 42 | 42 | 5233 | [5 empty] | R
| Current Scale - Channel 43 | 43 | 5234 | [5 empty] | R
| Current Scale - Channel 44 | 44 | 5235 | [5 empty] | R
| Current Scale - Channel 45 | 45 | 5236 | [5 empty] | R
| Current Scale - Channel 46 | 46 | 5237 | [5 empty] | R
| Current Scale - Channel 47 | 47 | 5238 | [5 empty] | R
| Current Scale - Channel 48 | 48 | 5239 | [5 empty] | R
| Current Scale - Channel 49 | 49 | 5240 | [5 empty] | R
| Current Scale - Channel 50 | 50 | 5241 | [5 empty] | R
| Current Scale - Channel 51 | 51 | 5242 | [5 empty] | R
| Current Scale - Channel 52 | 52 | 5243 | [5 empty] | R
| Current Scale - Channel 53 | 53 | 5244 | [5 empty] | R
| Current Scale - Channel 54 | 54 | 5245 | [5 empty] | R
| Current Scale - Channel 55 | 55 | 5246 | [5 empty] | R
| Current Scale - Channel 56 | 56 | 5247 | [5 empty] | R
| Current Scale - Channel 57 | 57 | 5248 | [5 empty] | R
| Current Scale - Channel 58 | 58 | 5249 | [5 empty] | R
| Current Scale - Channel 59 | 59 | 5250 | [5 empty] | R
| Current Scale - Channel 60 | 60 | 5251 | [5 empty] | R
| Current Scale - Channel 61 | 61 | 5252 | [5 empty] | R
| Current Scale - Channel 62 | 62 | 5253 | [5 empty] | R
| Current Scale - Channel 63 | 63 | 5254 | [5 empty] | R
| Current Scale - Channel 64 | 64 | 5255 | [5 empty] | R
| Current Scale - Channel 65 | 65 | 5256 | [5 empty] | R
| Current Scale - Channel 66 | 66 | 5257 | [5 empty] | R
| Current Scale - Channel 67 | 67 | 5258 | [5 empty] | R
| Current Scale - Channel 68 | 68 | 5259 | [5 empty] | R
| Current Scale - Channel 69 | 69 | 5260 | [5 empty] | R
| Current Scale - Channel 70 | 70 | 5261 | [5 empty] | R
| Current Scale - Channel 71 | 71 | 5262 | [5 empty] | R
| Current Scale - Channel 72 | 72 | 5263 | [5 empty] | R
| Current Scale - Channel 73 | 73 | 5264 | [5 empty] | R
| Current Scale - Channel 74 | 74 | 5265 | [5 empty] | R
| Current Scale - Channel 75 | 75 | 5266 | [5 empty] | R
| Current Scale - Channel 76 | 76 | 5267 | [5 empty] | R
| Current Scale - Channel 77 | 77 | 5268 | [5 empty] | R
| Current Scale - Channel 78 | 78 | 5269 | [5 empty] | R
| Current Scale - Channel 79 | 79 | 5270 | [5 empty] | R
| Current Scale - Channel 80 | 80 | 5271 | [5 empty] | R
| Current Scale - Channel 81 | 81 | 5272 | [5 empty] | R
| Current Scale - Channel 82 | 82 | 5273 | [5 empty] | R
| Current Scale - Channel 83 | 83 | 5274 | [5 empty] | R
| Current Scale - Channel 84 | 84 | 5275 | [5 empty] | R
| Current Scale - Channel 85 | 85 | 5276 | [5 empty] | R
| Current Scale - Channel 86 | 86 | 5277 | [5 empty] | R
| Current Scale - Channel 87 | 87 | 5278 | [5 empty] | R
| Current Scale - Channel 88 | 88 | 5279 | [5 empty] | R
| Current Scale - Channel 89 | 89 | 5280 | [5 empty] | R
| Current Scale - Channel 90 | 90 | 5281 | [5 empty] | R
| Current Scale - Channel 91 | 91 | 5282 | [5 empty] | R
| Current Scale - Channel 92 | 92 | 5283 | [5 empty] | R
| Current Scale - Channel 93 | 93 | 5284 | [5 empty] | R
| Current Scale - Channel 94 | 94 | 5285 | [5 empty] | R
| Current Scale - Channel 95 | 95 | 5286 | [5 empty] | R
| Current Scale - Channel 96 | 96 | 5287 | [5 empty] | R
| kWh |  | 5288 | 5479 | 10000 | 10191 |  |  | R | NV |  |  | 32 bit unsigned integer
| kWh - Channel 1 | 1 | 5288 | 5289 | 10000 | 10001 |  |  | R | NV
| kWh - Channel 2 | 2 | 5290 | 5291 | 10002 | 10003 |  |  | R | NV
| kWh - Channel 3 | 3 | 5292 | 5293 | 10004 | 10005 |  |  | R | NV
| kWh - Channel 4 | 4 | 5294 | 5295 | 10006 | 10007 |  |  | R | NV
| kWh - Channel 5 | 5 | 5296 | 5297 | 10008 | 10009 |  |  | R | NV
| kWh - Channel 6 | 6 | 5298 | 5299 | 10010 | 10011 |  |  | R | NV
| kWh - Channel 7 | 7 | 5300 | 5301 | 10012 | 10013 |  |  | R | NV
| kWh - Channel 8 | 8 | 5302 | 5303 | 10014 | 10015 |  |  | R | NV
| kWh - Channel 9 | 9 | 5304 | 5305 | 10016 | 10017 |  |  | R | NV
| kWh - Channel 10 | 10 | 5306 | 5307 | 10018 | 10019 |  |  | R | NV
| kWh - Channel 11 | 11 | 5308 | 5309 | 10020 | 10021 |  |  | R | NV
| kWh - Channel 12 | 12 | 5310 | 5311 | 10022 | 10023 |  |  | R | NV
| kWh - Channel 13 | 13 | 5312 | 5313 | 10024 | 10025 |  |  | R | NV
| kWh - Channel 14 | 14 | 5314 | 5315 | 10026 | 10027 |  |  | R | NV
| kWh - Channel 15 | 15 | 5316 | 5317 | 10028 | 10029 |  |  | R | NV
| kWh - Channel 16 | 16 | 5318 | 5319 | 10030 | 10031 |  |  | R | NV
| kWh - Channel 17 | 17 | 5320 | 5321 | 10032 | 10033 |  |  | R | NV
| kWh - Channel 18 | 18 | 5322 | 5323 | 10034 | 10035 |  |  | R | NV
| kWh - Channel 19 | 19 | 5324 | 5325 | 10036 | 10037 |  |  | R | NV
| kWh - Channel 20 | 20 | 5326 | 5327 | 10038 | 10039 |  |  | R | NV
| kWh - Channel 21 | 21 | 5328 | 5329 | 10040 | 10041 |  |  | R | NV
| kWh - Channel 22 | 22 | 5330 | 5331 | 10042 | 10043 |  |  | R | NV
| kWh - Channel 23 | 23 | 5332 | 5333 | 10044 | 10045 |  |  | R | NV
| kWh - Channel 24 | 24 | 5334 | 5335 | 10046 | 10047 |  |  | R | NV
| kWh - Channel 25 | 25 | 5336 | 5337 | 10048 | 10049 |  |  | R | NV
| kWh - Channel 26 | 26 | 5338 | 5339 | 10050 | 10051 |  |  | R | NV
| kWh - Channel 27 | 27 | 5340 | 5341 | 10052 | 10053 |  |  | R | NV
| kWh - Channel 28 | 28 | 5342 | 5343 | 10054 | 10055 |  |  | R | NV
| kWh - Channel 29 | 29 | 5344 | 5345 | 10056 | 10057 |  |  | R | NV
| kWh - Channel 30 | 30 | 5346 | 5347 | 10058 | 10059 |  |  | R | NV
| kWh - Channel 31 | 31 | 5348 | 5349 | 10060 | 10061 |  |  | R | NV
| kWh - Channel 32 | 32 | 5350 | 5351 | 10062 | 10063 |  |  | R | NV
| kWh - Channel 33 | 33 | 5352 | 5353 | 10064 | 10065 |  |  | R | NV
| kWh - Channel 34 | 34 | 5354 | 5355 | 10066 | 10067 |  |  | R | NV
| kWh - Channel 35 | 35 | 5356 | 5357 | 10068 | 10069 |  |  | R | NV
| kWh - Channel 36 | 36 | 5358 | 5359 | 10070 | 10071 |  |  | R | NV
| kWh - Channel 37 | 37 | 5360 | 5361 | 10072 | 10073 |  |  | R | NV
| kWh - Channel 38 | 38 | 5362 | 5363 | 10074 | 10075 |  |  | R | NV
| kWh - Channel 39 | 39 | 5364 | 5365 | 10076 | 10077 |  |  | R | NV
| kWh - Channel 40 | 40 | 5366 | 5367 | 10078 | 10079 |  |  | R | NV
| kWh - Channel 41 | 41 | 5368 | 5369 | 10080 | 10081 |  |  | R | NV
| kWh - Channel 42 | 42 | 5370 | 5371 | 10082 | 10083 |  |  | R | NV
| kWh - Channel 43 | 43 | 5372 | 5373 | 10084 | 10085 |  |  | R | NV
| kWh - Channel 44 | 44 | 5374 | 5375 | 10086 | 10087 |  |  | R | NV
| kWh - Channel 45 | 45 | 5376 | 5377 | 10088 | 10089 |  |  | R | NV
| kWh - Channel 46 | 46 | 5378 | 5379 | 10090 | 10091 |  |  | R | NV
| kWh - Channel 47 | 47 | 5380 | 5381 | 10092 | 10093 |  |  | R | NV
| kWh - Channel 48 | 48 | 5382 | 5383 | 10094 | 10095 |  |  | R | NV
| kWh - Channel 49 | 49 | 5384 | 5385 | 10096 | 10097 |  |  | R | NV
| kWh - Channel 50 | 50 | 5386 | 5387 | 10098 | 10099 |  |  | R | NV
| kWh - Channel 51 | 51 | 5388 | 5389 | 10100 | 10101 |  |  | R | NV
| kWh - Channel 52 | 52 | 5390 | 5391 | 10102 | 10103 |  |  | R | NV
| kWh - Channel 53 | 53 | 5392 | 5393 | 10104 | 10105 |  |  | R | NV
| kWh - Channel 54 | 54 | 5394 | 5395 | 10106 | 10107 |  |  | R | NV
| kWh - Channel 55 | 55 | 5396 | 5397 | 10108 | 10109 |  |  | R | NV
| kWh - Channel 56 | 56 | 5398 | 5399 | 10110 | 10111 |  |  | R | NV
| kWh - Channel 57 | 57 | 5400 | 5401 | 10112 | 10113 |  |  | R | NV
| kWh - Channel 58 | 58 | 5402 | 5403 | 10114 | 10115 |  |  | R | NV
| kWh - Channel 59 | 59 | 5404 | 5405 | 10116 | 10117 |  |  | R | NV
| kWh - Channel 60 | 60 | 5406 | 5407 | 10118 | 10119 |  |  | R | NV
| kWh - Channel 61 | 61 | 5408 | 5409 | 10120 | 10121 |  |  | R | NV
| kWh - Channel 62 | 62 | 5410 | 5411 | 10122 | 10123 |  |  | R | NV
| kWh - Channel 63 | 63 | 5412 | 5413 | 10124 | 10125 |  |  | R | NV
| kWh - Channel 64 | 64 | 5414 | 5415 | 10126 | 10127 |  |  | R | NV
| kWh - Channel 65 | 65 | 5416 | 5417 | 10128 | 10129 |  |  | R | NV
| kWh - Channel 66 | 66 | 5418 | 5419 | 10130 | 10131 |  |  | R | NV
| kWh - Channel 67 | 67 | 5420 | 5421 | 10132 | 10133 |  |  | R | NV
| kWh - Channel 68 | 68 | 5422 | 5423 | 10134 | 10135 |  |  | R | NV
| kWh - Channel 69 | 69 | 5424 | 5425 | 10136 | 10137 |  |  | R | NV
| kWh - Channel 70 | 70 | 5426 | 5427 | 10138 | 10139 |  |  | R | NV
| kWh - Channel 71 | 71 | 5428 | 5429 | 10140 | 10141 |  |  | R | NV
| kWh - Channel 72 | 72 | 5430 | 5431 | 10142 | 10143 |  |  | R | NV
| kWh - Channel 73 | 73 | 5432 | 5433 | 10144 | 10145 |  |  | R | NV
| kWh - Channel 74 | 74 | 5434 | 5435 | 10146 | 10147 |  |  | R | NV
| kWh - Channel 75 | 75 | 5436 | 5437 | 10148 | 10149 |  |  | R | NV
| kWh - Channel 76 | 76 | 5438 | 5439 | 10150 | 10151 |  |  | R | NV
| kWh - Channel 77 | 77 | 5440 | 5441 | 10152 | 10153 |  |  | R | NV
| kWh - Channel 78 | 78 | 5442 | 5443 | 10154 | 10155 |  |  | R | NV
| kWh - Channel 79 | 79 | 5444 | 5445 | 10156 | 10157 |  |  | R | NV
| kWh - Channel 80 | 80 | 5446 | 5447 | 10158 | 10159 |  |  | R | NV
| kWh - Channel 81 | 81 | 5448 | 5449 | 10160 | 10161 |  |  | R | NV
| kWh - Channel 82 | 82 | 5450 | 5451 | 10162 | 10163 |  |  | R | NV
| kWh - Channel 83 | 83 | 5452 | 5453 | 10164 | 10165 |  |  | R | NV
| kWh - Channel 84 | 84 | 5454 | 5455 | 10166 | 10167 |  |  | R | NV
| kWh - Channel 85 | 85 | 5456 | 5457 | 10168 | 10169 |  |  | R | NV
| kWh - Channel 86 | 86 | 5458 | 5459 | 10170 | 10171 |  |  | R | NV
| kWh - Channel 87 | 87 | 5460 | 5461 | 10172 | 10173 |  |  | R | NV
| kWh - Channel 88 | 88 | 5462 | 5463 | 10174 | 10175 |  |  | R | NV
| kWh - Channel 89 | 89 | 5464 | 5465 | 10176 | 10177 |  |  | R | NV
| kWh - Channel 90 | 90 | 5466 | 5467 | 10178 | 10179 |  |  | R | NV
| kWh - Channel 91 | 91 | 5468 | 5469 | 10180 | 10181 |  |  | R | NV
| kWh - Channel 92 | 92 | 5470 | 5471 | 10182 | 10183 |  |  | R | NV
| kWh - Channel 93 | 93 | 5472 | 5473 | 10184 | 10185 |  |  | R | NV
| kWh - Channel 94 | 94 | 5474 | 5475 | 10186 | 10187 |  |  | R | NV
| kWh - Channel 95 | 95 | 5476 | 5477 | 10188 | 10189 |  |  | R | NV
| kWh - Channel 96 | 96 | 5478 | 5479 | 10190 | 10191 |  |  | R | NV
| kVARh |  | 5480 | 5671 | 10192 | 10383 |  |  | R | NV |  |  | 32 bit unsigned integer
| kVARh - Channel 1 | 1 | 5480 | 5481 | 10192 | 10193 |  |  | R | NV
| kVARh - Channel 2 | 2 | 5482 | 5483 | 10194 | 10195 |  |  | R | NV
| kVARh - Channel 3 | 3 | 5484 | 5485 | 10196 | 10197 |  |  | R | NV
| kVARh - Channel 4 | 4 | 5486 | 5487 | 10198 | 10199 |  |  | R | NV
| kVARh - Channel 5 | 5 | 5488 | 5489 | 10200 | 10201 |  |  | R | NV
| kVARh - Channel 6 | 6 | 5490 | 5491 | 10202 | 10203 |  |  | R | NV
| kVARh - Channel 7 | 7 | 5492 | 5493 | 10204 | 10205 |  |  | R | NV
| kVARh - Channel 8 | 8 | 5494 | 5495 | 10206 | 10207 |  |  | R | NV
| kVARh - Channel 9 | 9 | 5496 | 5497 | 10208 | 10209 |  |  | R | NV
| kVARh - Channel 10 | 10 | 5498 | 5499 | 10210 | 10211 |  |  | R | NV
| kVARh - Channel 11 | 11 | 5500 | 5501 | 10212 | 10213 |  |  | R | NV
| kVARh - Channel 12 | 12 | 5502 | 5503 | 10214 | 10215 |  |  | R | NV
| kVARh - Channel 13 | 13 | 5504 | 5505 | 10216 | 10217 |  |  | R | NV
| kVARh - Channel 14 | 14 | 5506 | 5507 | 10218 | 10219 |  |  | R | NV
| kVARh - Channel 15 | 15 | 5508 | 5509 | 10220 | 10221 |  |  | R | NV
| kVARh - Channel 16 | 16 | 5510 | 5511 | 10222 | 10223 |  |  | R | NV
| kVARh - Channel 17 | 17 | 5512 | 5513 | 10224 | 10225 |  |  | R | NV
| kVARh - Channel 18 | 18 | 5514 | 5515 | 10226 | 10227 |  |  | R | NV
| kVARh - Channel 19 | 19 | 5516 | 5517 | 10228 | 10229 |  |  | R | NV
| kVARh - Channel 20 | 20 | 5518 | 5519 | 10230 | 10231 |  |  | R | NV
| kVARh - Channel 21 | 21 | 5520 | 5521 | 10232 | 10233 |  |  | R | NV
| kVARh - Channel 22 | 22 | 5522 | 5523 | 10234 | 10235 |  |  | R | NV
| kVARh - Channel 23 | 23 | 5524 | 5525 | 10236 | 10237 |  |  | R | NV
| kVARh - Channel 24 | 24 | 5526 | 5527 | 10238 | 10239 |  |  | R | NV
| kVARh - Channel 25 | 25 | 5528 | 5529 | 10240 | 10241 |  |  | R | NV
| kVARh - Channel 26 | 26 | 5530 | 5531 | 10242 | 10243 |  |  | R | NV
| kVARh - Channel 27 | 27 | 5532 | 5533 | 10244 | 10245 |  |  | R | NV
| kVARh - Channel 28 | 28 | 5534 | 5535 | 10246 | 10247 |  |  | R | NV
| kVARh - Channel 29 | 29 | 5536 | 5537 | 10248 | 10249 |  |  | R | NV
| kVARh - Channel 30 | 30 | 5538 | 5539 | 10250 | 10251 |  |  | R | NV
| kVARh - Channel 31 | 31 | 5540 | 5541 | 10252 | 10253 |  |  | R | NV
| kVARh - Channel 32 | 32 | 5542 | 5543 | 10254 | 10255 |  |  | R | NV
| kVARh - Channel 33 | 33 | 5544 | 5545 | 10256 | 10257 |  |  | R | NV
| kVARh - Channel 34 | 34 | 5546 | 5547 | 10258 | 10259 |  |  | R | NV
| kVARh - Channel 35 | 35 | 5548 | 5549 | 10260 | 10261 |  |  | R | NV
| kVARh - Channel 36 | 36 | 5550 | 5551 | 10262 | 10263 |  |  | R | NV
| kVARh - Channel 37 | 37 | 5552 | 5553 | 10264 | 10265 |  |  | R | NV
| kVARh - Channel 38 | 38 | 5554 | 5555 | 10266 | 10267 |  |  | R | NV
| kVARh - Channel 39 | 39 | 5556 | 5557 | 10268 | 10269 |  |  | R | NV
| kVARh - Channel 40 | 40 | 5558 | 5559 | 10270 | 10271 |  |  | R | NV
| kVARh - Channel 41 | 41 | 5560 | 5561 | 10272 | 10273 |  |  | R | NV
| kVARh - Channel 42 | 42 | 5562 | 5563 | 10274 | 10275 |  |  | R | NV
| kVARh - Channel 43 | 43 | 5564 | 5565 | 10276 | 10277 |  |  | R | NV
| kVARh - Channel 44 | 44 | 5566 | 5567 | 10278 | 10279 |  |  | R | NV
| kVARh - Channel 45 | 45 | 5568 | 5569 | 10280 | 10281 |  |  | R | NV
| kVARh - Channel 46 | 46 | 5570 | 5571 | 10282 | 10283 |  |  | R | NV
| kVARh - Channel 47 | 47 | 5572 | 5573 | 10284 | 10285 |  |  | R | NV
| kVARh - Channel 48 | 48 | 5574 | 5575 | 10286 | 10287 |  |  | R | NV
| kVARh - Channel 49 | 49 | 5576 | 5577 | 10288 | 10289 |  |  | R | NV
| kVARh - Channel 50 | 50 | 5578 | 5579 | 10290 | 10291 |  |  | R | NV
| kVARh - Channel 51 | 51 | 5580 | 5581 | 10292 | 10293 |  |  | R | NV
| kVARh - Channel 52 | 52 | 5582 | 5583 | 10294 | 10295 |  |  | R | NV
| kVARh - Channel 53 | 53 | 5584 | 5585 | 10296 | 10297 |  |  | R | NV
| kVARh - Channel 54 | 54 | 5586 | 5587 | 10298 | 10299 |  |  | R | NV
| kVARh - Channel 55 | 55 | 5588 | 5589 | 10300 | 10301 |  |  | R | NV
| kVARh - Channel 56 | 56 | 5590 | 5591 | 10302 | 10303 |  |  | R | NV
| kVARh - Channel 57 | 57 | 5592 | 5593 | 10304 | 10305 |  |  | R | NV
| kVARh - Channel 58 | 58 | 5594 | 5595 | 10306 | 10307 |  |  | R | NV
| kVARh - Channel 59 | 59 | 5596 | 5597 | 10308 | 10309 |  |  | R | NV
| kVARh - Channel 60 | 60 | 5598 | 5599 | 10310 | 10311 |  |  | R | NV
| kVARh - Channel 61 | 61 | 5600 | 5601 | 10312 | 10313 |  |  | R | NV
| kVARh - Channel 62 | 62 | 5602 | 5603 | 10314 | 10315 |  |  | R | NV
| kVARh - Channel 63 | 63 | 5604 | 5605 | 10316 | 10317 |  |  | R | NV
| kVARh - Channel 64 | 64 | 5606 | 5607 | 10318 | 10319 |  |  | R | NV
| kVARh - Channel 65 | 65 | 5608 | 5609 | 10320 | 10321 |  |  | R | NV
| kVARh - Channel 66 | 66 | 5610 | 5611 | 10322 | 10323 |  |  | R | NV
| kVARh - Channel 67 | 67 | 5612 | 5613 | 10324 | 10325 |  |  | R | NV
| kVARh - Channel 68 | 68 | 5614 | 5615 | 10326 | 10327 |  |  | R | NV
| kVARh - Channel 69 | 69 | 5616 | 5617 | 10328 | 10329 |  |  | R | NV
| kVARh - Channel 70 | 70 | 5618 | 5619 | 10330 | 10331 |  |  | R | NV
| kVARh - Channel 71 | 71 | 5620 | 5621 | 10332 | 10333 |  |  | R | NV
| kVARh - Channel 72 | 72 | 5622 | 5623 | 10334 | 10335 |  |  | R | NV
| kVARh - Channel 73 | 73 | 5624 | 5625 | 10336 | 10337 |  |  | R | NV
| kVARh - Channel 74 | 74 | 5626 | 5627 | 10338 | 10339 |  |  | R | NV
| kVARh - Channel 75 | 75 | 5628 | 5629 | 10340 | 10341 |  |  | R | NV
| kVARh - Channel 76 | 76 | 5630 | 5631 | 10342 | 10343 |  |  | R | NV
| kVARh - Channel 77 | 77 | 5632 | 5633 | 10344 | 10345 |  |  | R | NV
| kVARh - Channel 78 | 78 | 5634 | 5635 | 10346 | 10347 |  |  | R | NV
| kVARh - Channel 79 | 79 | 5636 | 5637 | 10348 | 10349 |  |  | R | NV
| kVARh - Channel 80 | 80 | 5638 | 5639 | 10350 | 10351 |  |  | R | NV
| kVARh - Channel 81 | 81 | 5640 | 5641 | 10352 | 10353 |  |  | R | NV
| kVARh - Channel 82 | 82 | 5642 | 5643 | 10354 | 10355 |  |  | R | NV
| kVARh - Channel 83 | 83 | 5644 | 5645 | 10356 | 10357 |  |  | R | NV
| kVARh - Channel 84 | 84 | 5646 | 5647 | 10358 | 10359 |  |  | R | NV
| kVARh - Channel 85 | 85 | 5648 | 5649 | 10360 | 10361 |  |  | R | NV
| kVARh - Channel 86 | 86 | 5650 | 5651 | 10362 | 10363 |  |  | R | NV
| kVARh - Channel 87 | 87 | 5652 | 5653 | 10364 | 10365 |  |  | R | NV
| kVARh - Channel 88 | 88 | 5654 | 5655 | 10366 | 10367 |  |  | R | NV
| kVARh - Channel 89 | 89 | 5656 | 5657 | 10368 | 10369 |  |  | R | NV
| kVARh - Channel 90 | 90 | 5658 | 5659 | 10370 | 10371 |  |  | R | NV
| kVARh - Channel 91 | 91 | 5660 | 5661 | 10372 | 10373 |  |  | R | NV
| kVARh - Channel 92 | 92 | 5662 | 5663 | 10374 | 10375 |  |  | R | NV
| kVARh - Channel 93 | 93 | 5664 | 5665 | 10376 | 10377 |  |  | R | NV
| kVARh - Channel 94 | 94 | 5666 | 5667 | 10378 | 10379 |  |  | R | NV
| kVARh - Channel 95 | 95 | 5668 | 5669 | 10380 | 10381 |  |  | R | NV
| kVARh - Channel 96 | 96 | 5670 | 5671 | 10382 | 10383 |  |  | R | NV
| kVAh |  | 5672 | 5863 | 10384 | 10575 |  |  | R | NV |  |  | 32 bit unsigned integer
| kVAh - Channel 1 | 1 | 5672 | 5673 | 10384 | 10385 |  |  | R | NV
| kVAh - Channel 2 | 2 | 5674 | 5675 | 10386 | 10387 |  |  | R | NV
| kVAh - Channel 3 | 3 | 5676 | 5677 | 10388 | 10389 |  |  | R | NV
| kVAh - Channel 4 | 4 | 5678 | 5679 | 10390 | 10391 |  |  | R | NV
| kVAh - Channel 5 | 5 | 5680 | 5681 | 10392 | 10393 |  |  | R | NV
| kVAh - Channel 6 | 6 | 5682 | 5683 | 10394 | 10395 |  |  | R | NV
| kVAh - Channel 7 | 7 | 5684 | 5685 | 10396 | 10397 |  |  | R | NV
| kVAh - Channel 8 | 8 | 5686 | 5687 | 10398 | 10399 |  |  | R | NV
| kVAh - Channel 9 | 9 | 5688 | 5689 | 10400 | 10401 |  |  | R | NV
| kVAh - Channel 10 | 10 | 5690 | 5691 | 10402 | 10403 |  |  | R | NV
| kVAh - Channel 11 | 11 | 5692 | 5693 | 10404 | 10405 |  |  | R | NV
| kVAh - Channel 12 | 12 | 5694 | 5695 | 10406 | 10407 |  |  | R | NV
| kVAh - Channel 13 | 13 | 5696 | 5697 | 10408 | 10409 |  |  | R | NV
| kVAh - Channel 14 | 14 | 5698 | 5699 | 10410 | 10411 |  |  | R | NV
| kVAh - Channel 15 | 15 | 5700 | 5701 | 10412 | 10413 |  |  | R | NV
| kVAh - Channel 16 | 16 | 5702 | 5703 | 10414 | 10415 |  |  | R | NV
| kVAh - Channel 17 | 17 | 5704 | 5705 | 10416 | 10417 |  |  | R | NV
| kVAh - Channel 18 | 18 | 5706 | 5707 | 10418 | 10419 |  |  | R | NV
| kVAh - Channel 19 | 19 | 5708 | 5709 | 10420 | 10421 |  |  | R | NV
| kVAh - Channel 20 | 20 | 5710 | 5711 | 10422 | 10423 |  |  | R | NV
| kVAh - Channel 21 | 21 | 5712 | 5713 | 10424 | 10425 |  |  | R | NV
| kVAh - Channel 22 | 22 | 5714 | 5715 | 10426 | 10427 |  |  | R | NV
| kVAh - Channel 23 | 23 | 5716 | 5717 | 10428 | 10429 |  |  | R | NV
| kVAh - Channel 24 | 24 | 5718 | 5719 | 10430 | 10431 |  |  | R | NV
| kVAh - Channel 25 | 25 | 5720 | 5721 | 10432 | 10433 |  |  | R | NV
| kVAh - Channel 26 | 26 | 5722 | 5723 | 10434 | 10435 |  |  | R | NV
| kVAh - Channel 27 | 27 | 5724 | 5725 | 10436 | 10437 |  |  | R | NV
| kVAh - Channel 28 | 28 | 5726 | 5727 | 10438 | 10439 |  |  | R | NV
| kVAh - Channel 29 | 29 | 5728 | 5729 | 10440 | 10441 |  |  | R | NV
| kVAh - Channel 30 | 30 | 5730 | 5731 | 10442 | 10443 |  |  | R | NV
| kVAh - Channel 31 | 31 | 5732 | 5733 | 10444 | 10445 |  |  | R | NV
| kVAh - Channel 32 | 32 | 5734 | 5735 | 10446 | 10447 |  |  | R | NV
| kVAh - Channel 33 | 33 | 5736 | 5737 | 10448 | 10449 |  |  | R | NV
| kVAh - Channel 34 | 34 | 5738 | 5739 | 10450 | 10451 |  |  | R | NV
| kVAh - Channel 35 | 35 | 5740 | 5741 | 10452 | 10453 |  |  | R | NV
| kVAh - Channel 36 | 36 | 5742 | 5743 | 10454 | 10455 |  |  | R | NV
| kVAh - Channel 37 | 37 | 5744 | 5745 | 10456 | 10457 |  |  | R | NV
| kVAh - Channel 38 | 38 | 5746 | 5747 | 10458 | 10459 |  |  | R | NV
| kVAh - Channel 39 | 39 | 5748 | 5749 | 10460 | 10461 |  |  | R | NV
| kVAh - Channel 40 | 40 | 5750 | 5751 | 10462 | 10463 |  |  | R | NV
| kVAh - Channel 41 | 41 | 5752 | 5753 | 10464 | 10465 |  |  | R | NV
| kVAh - Channel 42 | 42 | 5754 | 5755 | 10466 | 10467 |  |  | R | NV
| kVAh - Channel 43 | 43 | 5756 | 5757 | 10468 | 10469 |  |  | R | NV
| kVAh - Channel 44 | 44 | 5758 | 5759 | 10470 | 10471 |  |  | R | NV
| kVAh - Channel 45 | 45 | 5760 | 5761 | 10472 | 10473 |  |  | R | NV
| kVAh - Channel 46 | 46 | 5762 | 5763 | 10474 | 10475 |  |  | R | NV
| kVAh - Channel 47 | 47 | 5764 | 5765 | 10476 | 10477 |  |  | R | NV
| kVAh - Channel 48 | 48 | 5766 | 5767 | 10478 | 10479 |  |  | R | NV
| kVAh - Channel 49 | 49 | 5768 | 5769 | 10480 | 10481 |  |  | R | NV
| kVAh - Channel 50 | 50 | 5770 | 5771 | 10482 | 10483 |  |  | R | NV
| kVAh - Channel 51 | 51 | 5772 | 5773 | 10484 | 10485 |  |  | R | NV
| kVAh - Channel 52 | 52 | 5774 | 5775 | 10486 | 10487 |  |  | R | NV
| kVAh - Channel 53 | 53 | 5776 | 5777 | 10488 | 10489 |  |  | R | NV
| kVAh - Channel 54 | 54 | 5778 | 5779 | 10490 | 10491 |  |  | R | NV
| kVAh - Channel 55 | 55 | 5780 | 5781 | 10492 | 10493 |  |  | R | NV
| kVAh - Channel 56 | 56 | 5782 | 5783 | 10494 | 10495 |  |  | R | NV
| kVAh - Channel 57 | 57 | 5784 | 5785 | 10496 | 10497 |  |  | R | NV
| kVAh - Channel 58 | 58 | 5786 | 5787 | 10498 | 10499 |  |  | R | NV
| kVAh - Channel 59 | 59 | 5788 | 5789 | 10500 | 10501 |  |  | R | NV
| kVAh - Channel 60 | 60 | 5790 | 5791 | 10502 | 10503 |  |  | R | NV
| kVAh - Channel 61 | 61 | 5792 | 5793 | 10504 | 10505 |  |  | R | NV
| kVAh - Channel 62 | 62 | 5794 | 5795 | 10506 | 10507 |  |  | R | NV
| kVAh - Channel 63 | 63 | 5796 | 5797 | 10508 | 10509 |  |  | R | NV
| kVAh - Channel 64 | 64 | 5798 | 5799 | 10510 | 10511 |  |  | R | NV
| kVAh - Channel 65 | 65 | 5800 | 5801 | 10512 | 10513 |  |  | R | NV
| kVAh - Channel 66 | 66 | 5802 | 5803 | 10514 | 10515 |  |  | R | NV
| kVAh - Channel 67 | 67 | 5804 | 5805 | 10516 | 10517 |  |  | R | NV
| kVAh - Channel 68 | 68 | 5806 | 5807 | 10518 | 10519 |  |  | R | NV
| kVAh - Channel 69 | 69 | 5808 | 5809 | 10520 | 10521 |  |  | R | NV
| kVAh - Channel 70 | 70 | 5810 | 5811 | 10522 | 10523 |  |  | R | NV
| kVAh - Channel 71 | 71 | 5812 | 5813 | 10524 | 10525 |  |  | R | NV
| kVAh - Channel 72 | 72 | 5814 | 5815 | 10526 | 10527 |  |  | R | NV
| kVAh - Channel 73 | 73 | 5816 | 5817 | 10528 | 10529 |  |  | R | NV
| kVAh - Channel 74 | 74 | 5818 | 5819 | 10530 | 10531 |  |  | R | NV
| kVAh - Channel 75 | 75 | 5820 | 5821 | 10532 | 10533 |  |  | R | NV
| kVAh - Channel 76 | 76 | 5822 | 5823 | 10534 | 10535 |  |  | R | NV
| kVAh - Channel 77 | 77 | 5824 | 5825 | 10536 | 10537 |  |  | R | NV
| kVAh - Channel 78 | 78 | 5826 | 5827 | 10538 | 10539 |  |  | R | NV
| kVAh - Channel 79 | 79 | 5828 | 5829 | 10540 | 10541 |  |  | R | NV
| kVAh - Channel 80 | 80 | 5830 | 5831 | 10542 | 10543 |  |  | R | NV
| kVAh - Channel 81 | 81 | 5832 | 5833 | 10544 | 10545 |  |  | R | NV
| kVAh - Channel 82 | 82 | 5834 | 5835 | 10546 | 10547 |  |  | R | NV
| kVAh - Channel 83 | 83 | 5836 | 5837 | 10548 | 10549 |  |  | R | NV
| kVAh - Channel 84 | 84 | 5838 | 5839 | 10550 | 10551 |  |  | R | NV
| kVAh - Channel 85 | 85 | 5840 | 5841 | 10552 | 10553 |  |  | R | NV
| kVAh - Channel 86 | 86 | 5842 | 5843 | 10554 | 10555 |  |  | R | NV
| kVAh - Channel 87 | 87 | 5844 | 5845 | 10556 | 10557 |  |  | R | NV
| kVAh - Channel 88 | 88 | 5846 | 5847 | 10558 | 10559 |  |  | R | NV
| kVAh - Channel 89 | 89 | 5848 | 5849 | 10560 | 10561 |  |  | R | NV
| kVAh - Channel 90 | 90 | 5850 | 5851 | 10562 | 10563 |  |  | R | NV
| kVAh - Channel 91 | 91 | 5852 | 5853 | 10564 | 10565 |  |  | R | NV
| kVAh - Channel 92 | 92 | 5854 | 5855 | 10566 | 10567 |  |  | R | NV
| kVAh - Channel 93 | 93 | 5856 | 5857 | 10568 | 10569 |  |  | R | NV
| kVAh - Channel 94 | 94 | 5858 | 5859 | 10570 | 10571 |  |  | R | NV
| kVAh - Channel 95 | 95 | 5860 | 5861 | 10572 | 10573 |  |  | R | NV
| kVAh - Channel 96 | 96 | 5862 | 5863 | 10574 | 10575 |  |  | R | NV
| kW |  | 5864 | 5959 | 10576 | 10767 |  |  | R
| kW - Channel 1 | 1 | 5864 |  | 10576 | 10577 |  |  | R
| kW - Channel 2 | 2 | 5865 |  | 10578 | 10579 |  |  | R
| kW - Channel 3 | 3 | 5866 |  | 10580 | 10581 |  |  | R
| kW - Channel 4 | 4 | 5867 |  | 10582 | 10583 |  |  | R
| kW - Channel 5 | 5 | 5868 |  | 10584 | 10585 |  |  | R
| kW - Channel 6 | 6 | 5869 |  | 10586 | 10587 |  |  | R
| kW - Channel 7 | 7 | 5870 |  | 10588 | 10589 |  |  | R
| kW - Channel 8 | 8 | 5871 |  | 10590 | 10591 |  |  | R
| kW - Channel 9 | 9 | 5872 |  | 10592 | 10593 |  |  | R
| kW - Channel 10 | 10 | 5873 |  | 10594 | 10595 |  |  | R
| kW - Channel 11 | 11 | 5874 |  | 10596 | 10597 |  |  | R
| kW - Channel 12 | 12 | 5875 |  | 10598 | 10599 |  |  | R
| kW - Channel 13 | 13 | 5876 |  | 10600 | 10601 |  |  | R
| kW - Channel 14 | 14 | 5877 |  | 10602 | 10603 |  |  | R
| kW - Channel 15 | 15 | 5878 |  | 10604 | 10605 |  |  | R
| kW - Channel 16 | 16 | 5879 |  | 10606 | 10607 |  |  | R
| kW - Channel 17 | 17 | 5880 |  | 10608 | 10609 |  |  | R
| kW - Channel 18 | 18 | 5881 |  | 10610 | 10611 |  |  | R
| kW - Channel 19 | 19 | 5882 |  | 10612 | 10613 |  |  | R
| kW - Channel 20 | 20 | 5883 |  | 10614 | 10615 |  |  | R
| kW - Channel 21 | 21 | 5884 |  | 10616 | 10617 |  |  | R
| kW - Channel 22 | 22 | 5885 |  | 10618 | 10619 |  |  | R
| kW - Channel 23 | 23 | 5886 |  | 10620 | 10621 |  |  | R
| kW - Channel 24 | 24 | 5887 |  | 10622 | 10623 |  |  | R
| kW - Channel 25 | 25 | 5888 |  | 10624 | 10625 |  |  | R
| kW - Channel 26 | 26 | 5889 |  | 10626 | 10627 |  |  | R
| kW - Channel 27 | 27 | 5890 |  | 10628 | 10629 |  |  | R
| kW - Channel 28 | 28 | 5891 |  | 10630 | 10631 |  |  | R
| kW - Channel 29 | 29 | 5892 |  | 10632 | 10633 |  |  | R
| kW - Channel 30 | 30 | 5893 |  | 10634 | 10635 |  |  | R
| kW - Channel 31 | 31 | 5894 |  | 10636 | 10637 |  |  | R
| kW - Channel 32 | 32 | 5895 |  | 10638 | 10639 |  |  | R
| kW - Channel 33 | 33 | 5896 |  | 10640 | 10641 |  |  | R
| kW - Channel 34 | 34 | 5897 |  | 10642 | 10643 |  |  | R
| kW - Channel 35 | 35 | 5898 |  | 10644 | 10645 |  |  | R
| kW - Channel 36 | 36 | 5899 |  | 10646 | 10647 |  |  | R
| kW - Channel 37 | 37 | 5900 |  | 10648 | 10649 |  |  | R
| kW - Channel 38 | 38 | 5901 |  | 10650 | 10651 |  |  | R
| kW - Channel 39 | 39 | 5902 |  | 10652 | 10653 |  |  | R
| kW - Channel 40 | 40 | 5903 |  | 10654 | 10655 |  |  | R
| kW - Channel 41 | 41 | 5904 |  | 10656 | 10657 |  |  | R
| kW - Channel 42 | 42 | 5905 |  | 10658 | 10659 |  |  | R
| kW - Channel 43 | 43 | 5906 |  | 10660 | 10661 |  |  | R
| kW - Channel 44 | 44 | 5907 |  | 10662 | 10663 |  |  | R
| kW - Channel 45 | 45 | 5908 |  | 10664 | 10665 |  |  | R
| kW - Channel 46 | 46 | 5909 |  | 10666 | 10667 |  |  | R
| kW - Channel 47 | 47 | 5910 |  | 10668 | 10669 |  |  | R
| kW - Channel 48 | 48 | 5911 |  | 10670 | 10671 |  |  | R
| kW - Channel 49 | 49 | 5912 |  | 10672 | 10673 |  |  | R
| kW - Channel 50 | 50 | 5913 |  | 10674 | 10675 |  |  | R
| kW - Channel 51 | 51 | 5914 |  | 10676 | 10677 |  |  | R
| kW - Channel 52 | 52 | 5915 |  | 10678 | 10679 |  |  | R
| kW - Channel 53 | 53 | 5916 |  | 10680 | 10681 |  |  | R
| kW - Channel 54 | 54 | 5917 |  | 10682 | 10683 |  |  | R
| kW - Channel 55 | 55 | 5918 |  | 10684 | 10685 |  |  | R
| kW - Channel 56 | 56 | 5919 |  | 10686 | 10687 |  |  | R
| kW - Channel 57 | 57 | 5920 |  | 10688 | 10689 |  |  | R
| kW - Channel 58 | 58 | 5921 |  | 10690 | 10691 |  |  | R
| kW - Channel 59 | 59 | 5922 |  | 10692 | 10693 |  |  | R
| kW - Channel 60 | 60 | 5923 |  | 10694 | 10695 |  |  | R
| kW - Channel 61 | 61 | 5924 |  | 10696 | 10697 |  |  | R
| kW - Channel 62 | 62 | 5925 |  | 10698 | 10699 |  |  | R
| kW - Channel 63 | 63 | 5926 |  | 10700 | 10701 |  |  | R
| kW - Channel 64 | 64 | 5927 |  | 10702 | 10703 |  |  | R
| kW - Channel 65 | 65 | 5928 |  | 10704 | 10705 |  |  | R
| kW - Channel 66 | 66 | 5929 |  | 10706 | 10707 |  |  | R
| kW - Channel 67 | 67 | 5930 |  | 10708 | 10709 |  |  | R
| kW - Channel 68 | 68 | 5931 |  | 10710 | 10711 |  |  | R
| kW - Channel 69 | 69 | 5932 |  | 10712 | 10713 |  |  | R
| kW - Channel 70 | 70 | 5933 |  | 10714 | 10715 |  |  | R
| kW - Channel 71 | 71 | 5934 |  | 10716 | 10717 |  |  | R
| kW - Channel 72 | 72 | 5935 |  | 10718 | 10719 |  |  | R
| kW - Channel 73 | 73 | 5936 |  | 10720 | 10721 |  |  | R
| kW - Channel 74 | 74 | 5937 |  | 10722 | 10723 |  |  | R
| kW - Channel 75 | 75 | 5938 |  | 10724 | 10725 |  |  | R
| kW - Channel 76 | 76 | 5939 |  | 10726 | 10727 |  |  | R
| kW - Channel 77 | 77 | 5940 |  | 10728 | 10729 |  |  | R
| kW - Channel 78 | 78 | 5941 |  | 10730 | 10731 |  |  | R
| kW - Channel 79 | 79 | 5942 |  | 10732 | 10733 |  |  | R
| kW - Channel 80 | 80 | 5943 |  | 10734 | 10735 |  |  | R
| kW - Channel 81 | 81 | 5944 |  | 10736 | 10737 |  |  | R
| kW - Channel 82 | 82 | 5945 |  | 10738 | 10739 |  |  | R
| kW - Channel 83 | 83 | 5946 |  | 10740 | 10741 |  |  | R
| kW - Channel 84 | 84 | 5947 |  | 10742 | 10743 |  |  | R
| kW - Channel 85 | 85 | 5948 |  | 10744 | 10745 |  |  | R
| kW - Channel 86 | 86 | 5949 |  | 10746 | 10747 |  |  | R
| kW - Channel 87 | 87 | 5950 |  | 10748 | 10749 |  |  | R
| kW - Channel 88 | 88 | 5951 |  | 10750 | 10751 |  |  | R
| kW - Channel 89 | 89 | 5952 |  | 10752 | 10753 |  |  | R
| kW - Channel 90 | 90 | 5953 |  | 10754 | 10755 |  |  | R
| kW - Channel 91 | 91 | 5954 |  | 10756 | 10757 |  |  | R
| kW - Channel 92 | 92 | 5955 |  | 10758 | 10759 |  |  | R
| kW - Channel 93 | 93 | 5956 |  | 10760 | 10761 |  |  | R
| kW - Channel 94 | 94 | 5957 |  | 10762 | 10763 |  |  | R
| kW - Channel 95 | 95 | 5958 |  | 10764 | 10765 |  |  | R
| kW - Channel 96 | 96 | 5959 |  | 10766 | 10767 |  |  | R
| kVAR |  | 5960 | 6055 | 10768 | 10959 |  |  | R
| kVAR - Channel 1 | 1 | 5960 |  | 10768 | 10769 |  |  | R
| kVAR - Channel 2 | 2 | 5961 |  | 10770 | 10771 |  |  | R
| kVAR - Channel 3 | 3 | 5962 |  | 10772 | 10773 |  |  | R
| kVAR - Channel 4 | 4 | 5963 |  | 10774 | 10775 |  |  | R
| kVAR - Channel 5 | 5 | 5964 |  | 10776 | 10777 |  |  | R
| kVAR - Channel 6 | 6 | 5965 |  | 10778 | 10779 |  |  | R
| kVAR - Channel 7 | 7 | 5966 |  | 10780 | 10781 |  |  | R
| kVAR - Channel 8 | 8 | 5967 |  | 10782 | 10783 |  |  | R
| kVAR - Channel 9 | 9 | 5968 |  | 10784 | 10785 |  |  | R
| kVAR - Channel 10 | 10 | 5969 |  | 10786 | 10787 |  |  | R
| kVAR - Channel 11 | 11 | 5970 |  | 10788 | 10789 |  |  | R
| kVAR - Channel 12 | 12 | 5971 |  | 10790 | 10791 |  |  | R
| kVAR - Channel 13 | 13 | 5972 |  | 10792 | 10793 |  |  | R
| kVAR - Channel 14 | 14 | 5973 |  | 10794 | 10795 |  |  | R
| kVAR - Channel 15 | 15 | 5974 |  | 10796 | 10797 |  |  | R
| kVAR - Channel 16 | 16 | 5975 |  | 10798 | 10799 |  |  | R
| kVAR - Channel 17 | 17 | 5976 |  | 10800 | 10801 |  |  | R
| kVAR - Channel 18 | 18 | 5977 |  | 10802 | 10803 |  |  | R
| kVAR - Channel 19 | 19 | 5978 |  | 10804 | 10805 |  |  | R
| kVAR - Channel 20 | 20 | 5979 |  | 10806 | 10807 |  |  | R
| kVAR - Channel 21 | 21 | 5980 |  | 10808 | 10809 |  |  | R
| kVAR - Channel 22 | 22 | 5981 |  | 10810 | 10811 |  |  | R
| kVAR - Channel 23 | 23 | 5982 |  | 10812 | 10813 |  |  | R
| kVAR - Channel 24 | 24 | 5983 |  | 10814 | 10815 |  |  | R
| kVAR - Channel 25 | 25 | 5984 |  | 10816 | 10817 |  |  | R
| kVAR - Channel 26 | 26 | 5985 |  | 10818 | 10819 |  |  | R
| kVAR - Channel 27 | 27 | 5986 |  | 10820 | 10821 |  |  | R
| kVAR - Channel 28 | 28 | 5987 |  | 10822 | 10823 |  |  | R
| kVAR - Channel 29 | 29 | 5988 |  | 10824 | 10825 |  |  | R
| kVAR - Channel 30 | 30 | 5989 |  | 10826 | 10827 |  |  | R
| kVAR - Channel 31 | 31 | 5990 |  | 10828 | 10829 |  |  | R
| kVAR - Channel 32 | 32 | 5991 |  | 10830 | 10831 |  |  | R
| kVAR - Channel 33 | 33 | 5992 |  | 10832 | 10833 |  |  | R
| kVAR - Channel 34 | 34 | 5993 |  | 10834 | 10835 |  |  | R
| kVAR - Channel 35 | 35 | 5994 |  | 10836 | 10837 |  |  | R
| kVAR - Channel 36 | 36 | 5995 |  | 10838 | 10839 |  |  | R
| kVAR - Channel 37 | 37 | 5996 |  | 10840 | 10841 |  |  | R
| kVAR - Channel 38 | 38 | 5997 |  | 10842 | 10843 |  |  | R
| kVAR - Channel 39 | 39 | 5998 |  | 10844 | 10845 |  |  | R
| kVAR - Channel 40 | 40 | 5999 |  | 10846 | 10847 |  |  | R
| kVAR - Channel 41 | 41 | 6000 |  | 10848 | 10849 |  |  | R
| kVAR - Channel 42 | 42 | 6001 |  | 10850 | 10851 |  |  | R
| kVAR - Channel 43 | 43 | 6002 |  | 10852 | 10853 |  |  | R
| kVAR - Channel 44 | 44 | 6003 |  | 10854 | 10855 |  |  | R
| kVAR - Channel 45 | 45 | 6004 |  | 10856 | 10857 |  |  | R
| kVAR - Channel 46 | 46 | 6005 |  | 10858 | 10859 |  |  | R
| kVAR - Channel 47 | 47 | 6006 |  | 10860 | 10861 |  |  | R
| kVAR - Channel 48 | 48 | 6007 |  | 10862 | 10863 |  |  | R
| kVAR - Channel 49 | 49 | 6008 |  | 10864 | 10865 |  |  | R
| kVAR - Channel 50 | 50 | 6009 |  | 10866 | 10867 |  |  | R
| kVAR - Channel 51 | 51 | 6010 |  | 10868 | 10869 |  |  | R
| kVAR - Channel 52 | 52 | 6011 |  | 10870 | 10871 |  |  | R
| kVAR - Channel 53 | 53 | 6012 |  | 10872 | 10873 |  |  | R
| kVAR - Channel 54 | 54 | 6013 |  | 10874 | 10875 |  |  | R
| kVAR - Channel 55 | 55 | 6014 |  | 10876 | 10877 |  |  | R
| kVAR - Channel 56 | 56 | 6015 |  | 10878 | 10879 |  |  | R
| kVAR - Channel 57 | 57 | 6016 |  | 10880 | 10881 |  |  | R
| kVAR - Channel 58 | 58 | 6017 |  | 10882 | 10883 |  |  | R
| kVAR - Channel 59 | 59 | 6018 |  | 10884 | 10885 |  |  | R
| kVAR - Channel 60 | 60 | 6019 |  | 10886 | 10887 |  |  | R
| kVAR - Channel 61 | 61 | 6020 |  | 10888 | 10889 |  |  | R
| kVAR - Channel 62 | 62 | 6021 |  | 10890 | 10891 |  |  | R
| kVAR - Channel 63 | 63 | 6022 |  | 10892 | 10893 |  |  | R
| kVAR - Channel 64 | 64 | 6023 |  | 10894 | 10895 |  |  | R
| kVAR - Channel 65 | 65 | 6024 |  | 10896 | 10897 |  |  | R
| kVAR - Channel 66 | 66 | 6025 |  | 10898 | 10899 |  |  | R
| kVAR - Channel 67 | 67 | 6026 |  | 10900 | 10901 |  |  | R
| kVAR - Channel 68 | 68 | 6027 |  | 10902 | 10903 |  |  | R
| kVAR - Channel 69 | 69 | 6028 |  | 10904 | 10905 |  |  | R
| kVAR - Channel 70 | 70 | 6029 |  | 10906 | 10907 |  |  | R
| kVAR - Channel 71 | 71 | 6030 |  | 10908 | 10909 |  |  | R
| kVAR - Channel 72 | 72 | 6031 |  | 10910 | 10911 |  |  | R
| kVAR - Channel 73 | 73 | 6032 |  | 10912 | 10913 |  |  | R
| kVAR - Channel 74 | 74 | 6033 |  | 10914 | 10915 |  |  | R
| kVAR - Channel 75 | 75 | 6034 |  | 10916 | 10917 |  |  | R
| kVAR - Channel 76 | 76 | 6035 |  | 10918 | 10919 |  |  | R
| kVAR - Channel 77 | 77 | 6036 |  | 10920 | 10921 |  |  | R
| kVAR - Channel 78 | 78 | 6037 |  | 10922 | 10923 |  |  | R
| kVAR - Channel 79 | 79 | 6038 |  | 10924 | 10925 |  |  | R
| kVAR - Channel 80 | 80 | 6039 |  | 10926 | 10927 |  |  | R
| kVAR - Channel 81 | 81 | 6040 |  | 10928 | 10929 |  |  | R
| kVAR - Channel 82 | 82 | 6041 |  | 10930 | 10931 |  |  | R
| kVAR - Channel 83 | 83 | 6042 |  | 10932 | 10933 |  |  | R
| kVAR - Channel 84 | 84 | 6043 |  | 10934 | 10935 |  |  | R
| kVAR - Channel 85 | 85 | 6044 |  | 10936 | 10937 |  |  | R
| kVAR - Channel 86 | 86 | 6045 |  | 10938 | 10939 |  |  | R
| kVAR - Channel 87 | 87 | 6046 |  | 10940 | 10941 |  |  | R
| kVAR - Channel 88 | 88 | 6047 |  | 10942 | 10943 |  |  | R
| kVAR - Channel 89 | 89 | 6048 |  | 10944 | 10945 |  |  | R
| kVAR - Channel 90 | 90 | 6049 |  | 10946 | 10947 |  |  | R
| kVAR - Channel 91 | 91 | 6050 |  | 10948 | 10949 |  |  | R
| kVAR - Channel 92 | 92 | 6051 |  | 10950 | 10951 |  |  | R
| kVAR - Channel 93 | 93 | 6052 |  | 10952 | 10953 |  |  | R
| kVAR - Channel 94 | 94 | 6053 |  | 10954 | 10955 |  |  | R
| kVAR - Channel 95 | 95 | 6054 |  | 10956 | 10957 |  |  | R
| kVAR - Channel 96 | 96 | 6055 |  | 10958 | 10959 |  |  | R
| kVA |  | 6056 | 6151 | 10960 | 11151 |  |  | R
| kVA - Channel 1 | 1 | 6056 |  | 10960 | 10961 |  |  | R
| kVA - Channel 2 | 2 | 6057 |  | 10962 | 10963 |  |  | R
| kVA - Channel 3 | 3 | 6058 |  | 10964 | 10965 |  |  | R
| kVA - Channel 4 | 4 | 6059 |  | 10966 | 10967 |  |  | R
| kVA - Channel 5 | 5 | 6060 |  | 10968 | 10969 |  |  | R
| kVA - Channel 6 | 6 | 6061 |  | 10970 | 10971 |  |  | R
| kVA - Channel 7 | 7 | 6062 |  | 10972 | 10973 |  |  | R
| kVA - Channel 8 | 8 | 6063 |  | 10974 | 10975 |  |  | R
| kVA - Channel 9 | 9 | 6064 |  | 10976 | 10977 |  |  | R
| kVA - Channel 10 | 10 | 6065 |  | 10978 | 10979 |  |  | R
| kVA - Channel 11 | 11 | 6066 |  | 10980 | 10981 |  |  | R
| kVA - Channel 12 | 12 | 6067 |  | 10982 | 10983 |  |  | R
| kVA - Channel 13 | 13 | 6068 |  | 10984 | 10985 |  |  | R
| kVA - Channel 14 | 14 | 6069 |  | 10986 | 10987 |  |  | R
| kVA - Channel 15 | 15 | 6070 |  | 10988 | 10989 |  |  | R
| kVA - Channel 16 | 16 | 6071 |  | 10990 | 10991 |  |  | R
| kVA - Channel 17 | 17 | 6072 |  | 10992 | 10993 |  |  | R
| kVA - Channel 18 | 18 | 6073 |  | 10994 | 10995 |  |  | R
| kVA - Channel 19 | 19 | 6074 |  | 10996 | 10997 |  |  | R
| kVA - Channel 20 | 20 | 6075 |  | 10998 | 10999 |  |  | R
| kVA - Channel 21 | 21 | 6076 |  | 11000 | 11001 |  |  | R
| kVA - Channel 22 | 22 | 6077 |  | 11002 | 11003 |  |  | R
| kVA - Channel 23 | 23 | 6078 |  | 11004 | 11005 |  |  | R
| kVA - Channel 24 | 24 | 6079 |  | 11006 | 11007 |  |  | R
| kVA - Channel 25 | 25 | 6080 |  | 11008 | 11009 |  |  | R
| kVA - Channel 26 | 26 | 6081 |  | 11010 | 11011 |  |  | R
| kVA - Channel 27 | 27 | 6082 |  | 11012 | 11013 |  |  | R
| kVA - Channel 28 | 28 | 6083 |  | 11014 | 11015 |  |  | R
| kVA - Channel 29 | 29 | 6084 |  | 11016 | 11017 |  |  | R
| kVA - Channel 30 | 30 | 6085 |  | 11018 | 11019 |  |  | R
| kVA - Channel 31 | 31 | 6086 |  | 11020 | 11021 |  |  | R
| kVA - Channel 32 | 32 | 6087 |  | 11022 | 11023 |  |  | R
| kVA - Channel 33 | 33 | 6088 |  | 11024 | 11025 |  |  | R
| kVA - Channel 34 | 34 | 6089 |  | 11026 | 11027 |  |  | R
| kVA - Channel 35 | 35 | 6090 |  | 11028 | 11029 |  |  | R
| kVA - Channel 36 | 36 | 6091 |  | 11030 | 11031 |  |  | R
| kVA - Channel 37 | 37 | 6092 |  | 11032 | 11033 |  |  | R
| kVA - Channel 38 | 38 | 6093 |  | 11034 | 11035 |  |  | R
| kVA - Channel 39 | 39 | 6094 |  | 11036 | 11037 |  |  | R
| kVA - Channel 40 | 40 | 6095 |  | 11038 | 11039 |  |  | R
| kVA - Channel 41 | 41 | 6096 |  | 11040 | 11041 |  |  | R
| kVA - Channel 42 | 42 | 6097 |  | 11042 | 11043 |  |  | R
| kVA - Channel 43 | 43 | 6098 |  | 11044 | 11045 |  |  | R
| kVA - Channel 44 | 44 | 6099 |  | 11046 | 11047 |  |  | R
| kVA - Channel 45 | 45 | 6100 |  | 11048 | 11049 |  |  | R
| kVA - Channel 46 | 46 | 6101 |  | 11050 | 11051 |  |  | R
| kVA - Channel 47 | 47 | 6102 |  | 11052 | 11053 |  |  | R
| kVA - Channel 48 | 48 | 6103 |  | 11054 | 11055 |  |  | R
| kVA - Channel 49 | 49 | 6104 |  | 11056 | 11057 |  |  | R
| kVA - Channel 50 | 50 | 6105 |  | 11058 | 11059 |  |  | R
| kVA - Channel 51 | 51 | 6106 |  | 11060 | 11061 |  |  | R
| kVA - Channel 52 | 52 | 6107 |  | 11062 | 11063 |  |  | R
| kVA - Channel 53 | 53 | 6108 |  | 11064 | 11065 |  |  | R
| kVA - Channel 54 | 54 | 6109 |  | 11066 | 11067 |  |  | R
| kVA - Channel 55 | 55 | 6110 |  | 11068 | 11069 |  |  | R
| kVA - Channel 56 | 56 | 6111 |  | 11070 | 11071 |  |  | R
| kVA - Channel 57 | 57 | 6112 |  | 11072 | 11073 |  |  | R
| kVA - Channel 58 | 58 | 6113 |  | 11074 | 11075 |  |  | R
| kVA - Channel 59 | 59 | 6114 |  | 11076 | 11077 |  |  | R
| kVA - Channel 60 | 60 | 6115 |  | 11078 | 11079 |  |  | R
| kVA - Channel 61 | 61 | 6116 |  | 11080 | 11081 |  |  | R
| kVA - Channel 62 | 62 | 6117 |  | 11082 | 11083 |  |  | R
| kVA - Channel 63 | 63 | 6118 |  | 11084 | 11085 |  |  | R
| kVA - Channel 64 | 64 | 6119 |  | 11086 | 11087 |  |  | R
| kVA - Channel 65 | 65 | 6120 |  | 11088 | 11089 |  |  | R
| kVA - Channel 66 | 66 | 6121 |  | 11090 | 11091 |  |  | R
| kVA - Channel 67 | 67 | 6122 |  | 11092 | 11093 |  |  | R
| kVA - Channel 68 | 68 | 6123 |  | 11094 | 11095 |  |  | R
| kVA - Channel 69 | 69 | 6124 |  | 11096 | 11097 |  |  | R
| kVA - Channel 70 | 70 | 6125 |  | 11098 | 11099 |  |  | R
| kVA - Channel 71 | 71 | 6126 |  | 11100 | 11101 |  |  | R
| kVA - Channel 72 | 72 | 6127 |  | 11102 | 11103 |  |  | R
| kVA - Channel 73 | 73 | 6128 |  | 11104 | 11105 |  |  | R
| kVA - Channel 74 | 74 | 6129 |  | 11106 | 11107 |  |  | R
| kVA - Channel 75 | 75 | 6130 |  | 11108 | 11109 |  |  | R
| kVA - Channel 76 | 76 | 6131 |  | 11110 | 11111 |  |  | R
| kVA - Channel 77 | 77 | 6132 |  | 11112 | 11113 |  |  | R
| kVA - Channel 78 | 78 | 6133 |  | 11114 | 11115 |  |  | R
| kVA - Channel 79 | 79 | 6134 |  | 11116 | 11117 |  |  | R
| kVA - Channel 80 | 80 | 6135 |  | 11118 | 11119 |  |  | R
| kVA - Channel 81 | 81 | 6136 |  | 11120 | 11121 |  |  | R
| kVA - Channel 82 | 82 | 6137 |  | 11122 | 11123 |  |  | R
| kVA - Channel 83 | 83 | 6138 |  | 11124 | 11125 |  |  | R
| kVA - Channel 84 | 84 | 6139 |  | 11126 | 11127 |  |  | R
| kVA - Channel 85 | 85 | 6140 |  | 11128 | 11129 |  |  | R
| kVA - Channel 86 | 86 | 6141 |  | 11130 | 11131 |  |  | R
| kVA - Channel 87 | 87 | 6142 |  | 11132 | 11133 |  |  | R
| kVA - Channel 88 | 88 | 6143 |  | 11134 | 11135 |  |  | R
| kVA - Channel 89 | 89 | 6144 |  | 11136 | 11137 |  |  | R
| kVA - Channel 90 | 90 | 6145 |  | 11138 | 11139 |  |  | R
| kVA - Channel 91 | 91 | 6146 |  | 11140 | 11141 |  |  | R
| kVA - Channel 92 | 92 | 6147 |  | 11142 | 11143 |  |  | R
| kVA - Channel 93 | 93 | 6148 |  | 11144 | 11145 |  |  | R
| kVA - Channel 94 | 94 | 6149 |  | 11146 | 11147 |  |  | R
| kVA - Channel 95 | 95 | 6150 |  | 11148 | 11149 |  |  | R
| kVA - Channel 96 | 96 | 6151 |  | 11150 | 11151 |  |  | R
| Current |  | 6152 | 6247 | 11152 | 11343 |  |  | R
| Current - Channel 1 | 1 | 6152 |  | 11152 | 11153 |  |  | R
| Current - Channel 2 | 2 | 6153 |  | 11154 | 11155 |  |  | R
| Current - Channel 3 | 3 | 6154 |  | 11156 | 11157 |  |  | R
| Current - Channel 4 | 4 | 6155 |  | 11158 | 11159 |  |  | R
| Current - Channel 5 | 5 | 6156 |  | 11160 | 11161 |  |  | R
| Current - Channel 6 | 6 | 6157 |  | 11162 | 11163 |  |  | R
| Current - Channel 7 | 7 | 6158 |  | 11164 | 11165 |  |  | R
| Current - Channel 8 | 8 | 6159 |  | 11166 | 11167 |  |  | R
| Current - Channel 9 | 9 | 6160 |  | 11168 | 11169 |  |  | R
| Current - Channel 10 | 10 | 6161 |  | 11170 | 11171 |  |  | R
| Current - Channel 11 | 11 | 6162 |  | 11172 | 11173 |  |  | R
| Current - Channel 12 | 12 | 6163 |  | 11174 | 11175 |  |  | R
| Current - Channel 13 | 13 | 6164 |  | 11176 | 11177 |  |  | R
| Current - Channel 14 | 14 | 6165 |  | 11178 | 11179 |  |  | R
| Current - Channel 15 | 15 | 6166 |  | 11180 | 11181 |  |  | R
| Current - Channel 16 | 16 | 6167 |  | 11182 | 11183 |  |  | R
| Current - Channel 17 | 17 | 6168 |  | 11184 | 11185 |  |  | R
| Current - Channel 18 | 18 | 6169 |  | 11186 | 11187 |  |  | R
| Current - Channel 19 | 19 | 6170 |  | 11188 | 11189 |  |  | R
| Current - Channel 20 | 20 | 6171 |  | 11190 | 11191 |  |  | R
| Current - Channel 21 | 21 | 6172 |  | 11192 | 11193 |  |  | R
| Current - Channel 22 | 22 | 6173 |  | 11194 | 11195 |  |  | R
| Current - Channel 23 | 23 | 6174 |  | 11196 | 11197 |  |  | R
| Current - Channel 24 | 24 | 6175 |  | 11198 | 11199 |  |  | R
| Current - Channel 25 | 25 | 6176 |  | 11200 | 11201 |  |  | R
| Current - Channel 26 | 26 | 6177 |  | 11202 | 11203 |  |  | R
| Current - Channel 27 | 27 | 6178 |  | 11204 | 11205 |  |  | R
| Current - Channel 28 | 28 | 6179 |  | 11206 | 11207 |  |  | R
| Current - Channel 29 | 29 | 6180 |  | 11208 | 11209 |  |  | R
| Current - Channel 30 | 30 | 6181 |  | 11210 | 11211 |  |  | R
| Current - Channel 31 | 31 | 6182 |  | 11212 | 11213 |  |  | R
| Current - Channel 32 | 32 | 6183 |  | 11214 | 11215 |  |  | R
| Current - Channel 33 | 33 | 6184 |  | 11216 | 11217 |  |  | R
| Current - Channel 34 | 34 | 6185 |  | 11218 | 11219 |  |  | R
| Current - Channel 35 | 35 | 6186 |  | 11220 | 11221 |  |  | R
| Current - Channel 36 | 36 | 6187 |  | 11222 | 11223 |  |  | R
| Current - Channel 37 | 37 | 6188 |  | 11224 | 11225 |  |  | R
| Current - Channel 38 | 38 | 6189 |  | 11226 | 11227 |  |  | R
| Current - Channel 39 | 39 | 6190 |  | 11228 | 11229 |  |  | R
| Current - Channel 40 | 40 | 6191 |  | 11230 | 11231 |  |  | R
| Current - Channel 41 | 41 | 6192 |  | 11232 | 11233 |  |  | R
| Current - Channel 42 | 42 | 6193 |  | 11234 | 11235 |  |  | R
| Current - Channel 43 | 43 | 6194 |  | 11236 | 11237 |  |  | R
| Current - Channel 44 | 44 | 6195 |  | 11238 | 11239 |  |  | R
| Current - Channel 45 | 45 | 6196 |  | 11240 | 11241 |  |  | R
| Current - Channel 46 | 46 | 6197 |  | 11242 | 11243 |  |  | R
| Current - Channel 47 | 47 | 6198 |  | 11244 | 11245 |  |  | R
| Current - Channel 48 | 48 | 6199 |  | 11246 | 11247 |  |  | R
| Current - Channel 49 | 49 | 6200 |  | 11248 | 11249 |  |  | R
| Current - Channel 50 | 50 | 6201 |  | 11250 | 11251 |  |  | R
| Current - Channel 51 | 51 | 6202 |  | 11252 | 11253 |  |  | R
| Current - Channel 52 | 52 | 6203 |  | 11254 | 11255 |  |  | R
| Current - Channel 53 | 53 | 6204 |  | 11256 | 11257 |  |  | R
| Current - Channel 54 | 54 | 6205 |  | 11258 | 11259 |  |  | R
| Current - Channel 55 | 55 | 6206 |  | 11260 | 11261 |  |  | R
| Current - Channel 56 | 56 | 6207 |  | 11262 | 11263 |  |  | R
| Current - Channel 57 | 57 | 6208 |  | 11264 | 11265 |  |  | R
| Current - Channel 58 | 58 | 6209 |  | 11266 | 11267 |  |  | R
| Current - Channel 59 | 59 | 6210 |  | 11268 | 11269 |  |  | R
| Current - Channel 60 | 60 | 6211 |  | 11270 | 11271 |  |  | R
| Current - Channel 61 | 61 | 6212 |  | 11272 | 11273 |  |  | R
| Current - Channel 62 | 62 | 6213 |  | 11274 | 11275 |  |  | R
| Current - Channel 63 | 63 | 6214 |  | 11276 | 11277 |  |  | R
| Current - Channel 64 | 64 | 6215 |  | 11278 | 11279 |  |  | R
| Current - Channel 65 | 65 | 6216 |  | 11280 | 11281 |  |  | R
| Current - Channel 66 | 66 | 6217 |  | 11282 | 11283 |  |  | R
| Current - Channel 67 | 67 | 6218 |  | 11284 | 11285 |  |  | R
| Current - Channel 68 | 68 | 6219 |  | 11286 | 11287 |  |  | R
| Current - Channel 69 | 69 | 6220 |  | 11288 | 11289 |  |  | R
| Current - Channel 70 | 70 | 6221 |  | 11290 | 11291 |  |  | R
| Current - Channel 71 | 71 | 6222 |  | 11292 | 11293 |  |  | R
| Current - Channel 72 | 72 | 6223 |  | 11294 | 11295 |  |  | R
| Current - Channel 73 | 73 | 6224 |  | 11296 | 11297 |  |  | R
| Current - Channel 74 | 74 | 6225 |  | 11298 | 11299 |  |  | R
| Current - Channel 75 | 75 | 6226 |  | 11300 | 11301 |  |  | R
| Current - Channel 76 | 76 | 6227 |  | 11302 | 11303 |  |  | R
| Current - Channel 77 | 77 | 6228 |  | 11304 | 11305 |  |  | R
| Current - Channel 78 | 78 | 6229 |  | 11306 | 11307 |  |  | R
| Current - Channel 79 | 79 | 6230 |  | 11308 | 11309 |  |  | R
| Current - Channel 80 | 80 | 6231 |  | 11310 | 11311 |  |  | R
| Current - Channel 81 | 81 | 6232 |  | 11312 | 11313 |  |  | R
| Current - Channel 82 | 82 | 6233 |  | 11314 | 11315 |  |  | R
| Current - Channel 83 | 83 | 6234 |  | 11316 | 11317 |  |  | R
| Current - Channel 84 | 84 | 6235 |  | 11318 | 11319 |  |  | R
| Current - Channel 85 | 85 | 6236 |  | 11320 | 11321 |  |  | R
| Current - Channel 86 | 86 | 6237 |  | 11322 | 11323 |  |  | R
| Current - Channel 87 | 87 | 6238 |  | 11324 | 11325 |  |  | R
| Current - Channel 88 | 88 | 6239 |  | 11326 | 11327 |  |  | R
| Current - Channel 89 | 89 | 6240 |  | 11328 | 11329 |  |  | R
| Current - Channel 90 | 90 | 6241 |  | 11330 | 11331 |  |  | R
| Current - Channel 91 | 91 | 6242 |  | 11332 | 11333 |  |  | R
| Current - Channel 92 | 92 | 6243 |  | 11334 | 11335 |  |  | R
| Current - Channel 93 | 93 | 6244 |  | 11336 | 11337 |  |  | R
| Current - Channel 94 | 94 | 6245 |  | 11338 | 11339 |  |  | R
| Current - Channel 95 | 95 | 6246 |  | 11340 | 11341 |  |  | R
| Current - Channel 96 | 96 | 6247 |  | 11342 | 11343 |  |  | R
| Power Factor |  | 6248 | 6343 | 11344 | 11535 |  |  | R
| Power Factor - Channel 1 | 1 | 6248 |  | 11344 | 11345 |  |  | R
| Power Factor - Channel 2 | 2 | 6249 |  | 11346 | 11347 |  |  | R
| Power Factor - Channel 3 | 3 | 6250 |  | 11348 | 11349 |  |  | R
| Power Factor - Channel 4 | 4 | 6251 |  | 11350 | 11351 |  |  | R
| Power Factor - Channel 5 | 5 | 6252 |  | 11352 | 11353 |  |  | R
| Power Factor - Channel 6 | 6 | 6253 |  | 11354 | 11355 |  |  | R
| Power Factor - Channel 7 | 7 | 6254 |  | 11356 | 11357 |  |  | R
| Power Factor - Channel 8 | 8 | 6255 |  | 11358 | 11359 |  |  | R
| Power Factor - Channel 9 | 9 | 6256 |  | 11360 | 11361 |  |  | R
| Power Factor - Channel 10 | 10 | 6257 |  | 11362 | 11363 |  |  | R
| Power Factor - Channel 11 | 11 | 6258 |  | 11364 | 11365 |  |  | R
| Power Factor - Channel 12 | 12 | 6259 |  | 11366 | 11367 |  |  | R
| Power Factor - Channel 13 | 13 | 6260 |  | 11368 | 11369 |  |  | R
| Power Factor - Channel 14 | 14 | 6261 |  | 11370 | 11371 |  |  | R
| Power Factor - Channel 15 | 15 | 6262 |  | 11372 | 11373 |  |  | R
| Power Factor - Channel 16 | 16 | 6263 |  | 11374 | 11375 |  |  | R
| Power Factor - Channel 17 | 17 | 6264 |  | 11376 | 11377 |  |  | R
| Power Factor - Channel 18 | 18 | 6265 |  | 11378 | 11379 |  |  | R
| Power Factor - Channel 19 | 19 | 6266 |  | 11380 | 11381 |  |  | R
| Power Factor - Channel 20 | 20 | 6267 |  | 11382 | 11383 |  |  | R
| Power Factor - Channel 21 | 21 | 6268 |  | 11384 | 11385 |  |  | R
| Power Factor - Channel 22 | 22 | 6269 |  | 11386 | 11387 |  |  | R
| Power Factor - Channel 23 | 23 | 6270 |  | 11388 | 11389 |  |  | R
| Power Factor - Channel 24 | 24 | 6271 |  | 11390 | 11391 |  |  | R
| Power Factor - Channel 25 | 25 | 6272 |  | 11392 | 11393 |  |  | R
| Power Factor - Channel 26 | 26 | 6273 |  | 11394 | 11395 |  |  | R
| Power Factor - Channel 27 | 27 | 6274 |  | 11396 | 11397 |  |  | R
| Power Factor - Channel 28 | 28 | 6275 |  | 11398 | 11399 |  |  | R
| Power Factor - Channel 29 | 29 | 6276 |  | 11400 | 11401 |  |  | R
| Power Factor - Channel 30 | 30 | 6277 |  | 11402 | 11403 |  |  | R
| Power Factor - Channel 31 | 31 | 6278 |  | 11404 | 11405 |  |  | R
| Power Factor - Channel 32 | 32 | 6279 |  | 11406 | 11407 |  |  | R
| Power Factor - Channel 33 | 33 | 6280 |  | 11408 | 11409 |  |  | R
| Power Factor - Channel 34 | 34 | 6281 |  | 11410 | 11411 |  |  | R
| Power Factor - Channel 35 | 35 | 6282 |  | 11412 | 11413 |  |  | R
| Power Factor - Channel 36 | 36 | 6283 |  | 11414 | 11415 |  |  | R
| Power Factor - Channel 37 | 37 | 6284 |  | 11416 | 11417 |  |  | R
| Power Factor - Channel 38 | 38 | 6285 |  | 11418 | 11419 |  |  | R
| Power Factor - Channel 39 | 39 | 6286 |  | 11420 | 11421 |  |  | R
| Power Factor - Channel 40 | 40 | 6287 |  | 11422 | 11423 |  |  | R
| Power Factor - Channel 41 | 41 | 6288 |  | 11424 | 11425 |  |  | R
| Power Factor - Channel 42 | 42 | 6289 |  | 11426 | 11427 |  |  | R
| Power Factor - Channel 43 | 43 | 6290 |  | 11428 | 11429 |  |  | R
| Power Factor - Channel 44 | 44 | 6291 |  | 11430 | 11431 |  |  | R
| Power Factor - Channel 45 | 45 | 6292 |  | 11432 | 11433 |  |  | R
| Power Factor - Channel 46 | 46 | 6293 |  | 11434 | 11435 |  |  | R
| Power Factor - Channel 47 | 47 | 6294 |  | 11436 | 11437 |  |  | R
| Power Factor - Channel 48 | 48 | 6295 |  | 11438 | 11439 |  |  | R
| Power Factor - Channel 49 | 49 | 6296 |  | 11440 | 11441 |  |  | R
| Power Factor - Channel 50 | 50 | 6297 |  | 11442 | 11443 |  |  | R
| Power Factor - Channel 51 | 51 | 6298 |  | 11444 | 11445 |  |  | R
| Power Factor - Channel 52 | 52 | 6299 |  | 11446 | 11447 |  |  | R
| Power Factor - Channel 53 | 53 | 6300 |  | 11448 | 11449 |  |  | R
| Power Factor - Channel 54 | 54 | 6301 |  | 11450 | 11451 |  |  | R
| Power Factor - Channel 55 | 55 | 6302 |  | 11452 | 11453 |  |  | R
| Power Factor - Channel 56 | 56 | 6303 |  | 11454 | 11455 |  |  | R
| Power Factor - Channel 57 | 57 | 6304 |  | 11456 | 11457 |  |  | R
| Power Factor - Channel 58 | 58 | 6305 |  | 11458 | 11459 |  |  | R
| Power Factor - Channel 59 | 59 | 6306 |  | 11460 | 11461 |  |  | R
| Power Factor - Channel 60 | 60 | 6307 |  | 11462 | 11463 |  |  | R
| Power Factor - Channel 61 | 61 | 6308 |  | 11464 | 11465 |  |  | R
| Power Factor - Channel 62 | 62 | 6309 |  | 11466 | 11467 |  |  | R
| Power Factor - Channel 63 | 63 | 6310 |  | 11468 | 11469 |  |  | R
| Power Factor - Channel 64 | 64 | 6311 |  | 11470 | 11471 |  |  | R
| Power Factor - Channel 65 | 65 | 6312 |  | 11472 | 11473 |  |  | R
| Power Factor - Channel 66 | 66 | 6313 |  | 11474 | 11475 |  |  | R
| Power Factor - Channel 67 | 67 | 6314 |  | 11476 | 11477 |  |  | R
| Power Factor - Channel 68 | 68 | 6315 |  | 11478 | 11479 |  |  | R
| Power Factor - Channel 69 | 69 | 6316 |  | 11480 | 11481 |  |  | R
| Power Factor - Channel 70 | 70 | 6317 |  | 11482 | 11483 |  |  | R
| Power Factor - Channel 71 | 71 | 6318 |  | 11484 | 11485 |  |  | R
| Power Factor - Channel 72 | 72 | 6319 |  | 11486 | 11487 |  |  | R
| Power Factor - Channel 73 | 73 | 6320 |  | 11488 | 11489 |  |  | R
| Power Factor - Channel 74 | 74 | 6321 |  | 11490 | 11491 |  |  | R
| Power Factor - Channel 75 | 75 | 6322 |  | 11492 | 11493 |  |  | R
| Power Factor - Channel 76 | 76 | 6323 |  | 11494 | 11495 |  |  | R
| Power Factor - Channel 77 | 77 | 6324 |  | 11496 | 11497 |  |  | R
| Power Factor - Channel 78 | 78 | 6325 |  | 11498 | 11499 |  |  | R
| Power Factor - Channel 79 | 79 | 6326 |  | 11500 | 11501 |  |  | R
| Power Factor - Channel 80 | 80 | 6327 |  | 11502 | 11503 |  |  | R
| Power Factor - Channel 81 | 81 | 6328 |  | 11504 | 11505 |  |  | R
| Power Factor - Channel 82 | 82 | 6329 |  | 11506 | 11507 |  |  | R
| Power Factor - Channel 83 | 83 | 6330 |  | 11508 | 11509 |  |  | R
| Power Factor - Channel 84 | 84 | 6331 |  | 11510 | 11511 |  |  | R
| Power Factor - Channel 85 | 85 | 6332 |  | 11512 | 11513 |  |  | R
| Power Factor - Channel 86 | 86 | 6333 |  | 11514 | 11515 |  |  | R
| Power Factor - Channel 87 | 87 | 6334 |  | 11516 | 11517 |  |  | R
| Power Factor - Channel 88 | 88 | 6335 |  | 11518 | 11519 |  |  | R
| Power Factor - Channel 89 | 89 | 6336 |  | 11520 | 11521 |  |  | R
| Power Factor - Channel 90 | 90 | 6337 |  | 11522 | 11523 |  |  | R
| Power Factor - Channel 91 | 91 | 6338 |  | 11524 | 11525 |  |  | R
| Power Factor - Channel 92 | 92 | 6339 |  | 11526 | 11527 |  |  | R
| Power Factor - Channel 93 | 93 | 6340 |  | 11528 | 11529 |  |  | R
| Power Factor - Channel 94 | 94 | 6341 |  | 11530 | 11531 |  |  | R
| Power Factor - Channel 95 | 95 | 6342 |  | 11532 | 11533 |  |  | R
| Power Factor - Channel 96 | 96 | 6343 |  | 11534 | 11535 |  |  | R
| Current Angle |  | 6344 | 6439 | 11536 | 11727 |  |  | R
| Current Angle- Channel 1 | 1 | 6344 |  | 11536 | 11537 |  |  | R
| Current Angle- Channel 2 | 2 | 6345 |  | 11538 | 11539 |  |  | R
| Current Angle- Channel 3 | 3 | 6346 |  | 11540 | 11541 |  |  | R
| Current Angle- Channel 4 | 4 | 6347 |  | 11542 | 11543 |  |  | R
| Current Angle- Channel 5 | 5 | 6348 |  | 11544 | 11545 |  |  | R
| Current Angle- Channel 6 | 6 | 6349 |  | 11546 | 11547 |  |  | R
| Current Angle- Channel 7 | 7 | 6350 |  | 11548 | 11549 |  |  | R
| Current Angle- Channel 8 | 8 | 6351 |  | 11550 | 11551 |  |  | R
| Current Angle- Channel 9 | 9 | 6352 |  | 11552 | 11553 |  |  | R
| Current Angle- Channel 10 | 10 | 6353 |  | 11554 | 11555 |  |  | R
| Current Angle- Channel 11 | 11 | 6354 |  | 11556 | 11557 |  |  | R
| Current Angle- Channel 12 | 12 | 6355 |  | 11558 | 11559 |  |  | R
| Current Angle- Channel 13 | 13 | 6356 |  | 11560 | 11561 |  |  | R
| Current Angle- Channel 14 | 14 | 6357 |  | 11562 | 11563 |  |  | R
| Current Angle- Channel 15 | 15 | 6358 |  | 11564 | 11565 |  |  | R
| Current Angle- Channel 16 | 16 | 6359 |  | 11566 | 11567 |  |  | R
| Current Angle- Channel 17 | 17 | 6360 |  | 11568 | 11569 |  |  | R
| Current Angle- Channel 18 | 18 | 6361 |  | 11570 | 11571 |  |  | R
| Current Angle- Channel 19 | 19 | 6362 |  | 11572 | 11573 |  |  | R
| Current Angle- Channel 20 | 20 | 6363 |  | 11574 | 11575 |  |  | R
| Current Angle- Channel 21 | 21 | 6364 |  | 11576 | 11577 |  |  | R
| Current Angle- Channel 22 | 22 | 6365 |  | 11578 | 11579 |  |  | R
| Current Angle- Channel 23 | 23 | 6366 |  | 11580 | 11581 |  |  | R
| Current Angle- Channel 24 | 24 | 6367 |  | 11582 | 11583 |  |  | R
| Current Angle- Channel 25 | 25 | 6368 |  | 11584 | 11585 |  |  | R
| Current Angle- Channel 26 | 26 | 6369 |  | 11586 | 11587 |  |  | R
| Current Angle- Channel 27 | 27 | 6370 |  | 11588 | 11589 |  |  | R
| Current Angle- Channel 28 | 28 | 6371 |  | 11590 | 11591 |  |  | R
| Current Angle- Channel 29 | 29 | 6372 |  | 11592 | 11593 |  |  | R
| Current Angle- Channel 30 | 30 | 6373 |  | 11594 | 11595 |  |  | R
| Current Angle- Channel 31 | 31 | 6374 |  | 11596 | 11597 |  |  | R
| Current Angle- Channel 32 | 32 | 6375 |  | 11598 | 11599 |  |  | R
| Current Angle- Channel 33 | 33 | 6376 |  | 11600 | 11601 |  |  | R
| Current Angle- Channel 34 | 34 | 6377 |  | 11602 | 11603 |  |  | R
| Current Angle- Channel 35 | 35 | 6378 |  | 11604 | 11605 |  |  | R
| Current Angle- Channel 36 | 36 | 6379 |  | 11606 | 11607 |  |  | R
| Current Angle- Channel 37 | 37 | 6380 |  | 11608 | 11609 |  |  | R
| Current Angle- Channel 38 | 38 | 6381 |  | 11610 | 11611 |  |  | R
| Current Angle- Channel 39 | 39 | 6382 |  | 11612 | 11613 |  |  | R
| Current Angle- Channel 40 | 40 | 6383 |  | 11614 | 11615 |  |  | R
| Current Angle- Channel 41 | 41 | 6384 |  | 11616 | 11617 |  |  | R
| Current Angle- Channel 42 | 42 | 6385 |  | 11618 | 11619 |  |  | R
| Current Angle- Channel 43 | 43 | 6386 |  | 11620 | 11621 |  |  | R
| Current Angle- Channel 44 | 44 | 6387 |  | 11622 | 11623 |  |  | R
| Current Angle- Channel 45 | 45 | 6388 |  | 11624 | 11625 |  |  | R
| Current Angle- Channel 46 | 46 | 6389 |  | 11626 | 11627 |  |  | R
| Current Angle- Channel 47 | 47 | 6390 |  | 11628 | 11629 |  |  | R
| Current Angle- Channel 48 | 48 | 6391 |  | 11630 | 11631 |  |  | R
| Current Angle- Channel 49 | 49 | 6392 |  | 11632 | 11633 |  |  | R
| Current Angle- Channel 50 | 50 | 6393 |  | 11634 | 11635 |  |  | R
| Current Angle- Channel 51 | 51 | 6394 |  | 11636 | 11637 |  |  | R
| Current Angle- Channel 52 | 52 | 6395 |  | 11638 | 11639 |  |  | R
| Current Angle- Channel 53 | 53 | 6396 |  | 11640 | 11641 |  |  | R
| Current Angle- Channel 54 | 54 | 6397 |  | 11642 | 11643 |  |  | R
| Current Angle- Channel 55 | 55 | 6398 |  | 11644 | 11645 |  |  | R
| Current Angle- Channel 56 | 56 | 6399 |  | 11646 | 11647 |  |  | R
| Current Angle- Channel 57 | 57 | 6400 |  | 11648 | 11649 |  |  | R
| Current Angle- Channel 58 | 58 | 6401 |  | 11650 | 11651 |  |  | R
| Current Angle- Channel 59 | 59 | 6402 |  | 11652 | 11653 |  |  | R
| Current Angle- Channel 60 | 60 | 6403 |  | 11654 | 11655 |  |  | R
| Current Angle- Channel 61 | 61 | 6404 |  | 11656 | 11657 |  |  | R
| Current Angle- Channel 62 | 62 | 6405 |  | 11658 | 11659 |  |  | R
| Current Angle- Channel 63 | 63 | 6406 |  | 11660 | 11661 |  |  | R
| Current Angle- Channel 64 | 64 | 6407 |  | 11662 | 11663 |  |  | R
| Current Angle- Channel 65 | 65 | 6408 |  | 11664 | 11665 |  |  | R
| Current Angle- Channel 66 | 66 | 6409 |  | 11666 | 11667 |  |  | R
| Current Angle- Channel 67 | 67 | 6410 |  | 11668 | 11669 |  |  | R
| Current Angle- Channel 68 | 68 | 6411 |  | 11670 | 11671 |  |  | R
| Current Angle- Channel 69 | 69 | 6412 |  | 11672 | 11673 |  |  | R
| Current Angle- Channel 70 | 70 | 6413 |  | 11674 | 11675 |  |  | R
| Current Angle- Channel 71 | 71 | 6414 |  | 11676 | 11677 |  |  | R
| Current Angle- Channel 72 | 72 | 6415 |  | 11678 | 11679 |  |  | R
| Current Angle- Channel 73 | 73 | 6416 |  | 11680 | 11681 |  |  | R
| Current Angle- Channel 74 | 74 | 6417 |  | 11682 | 11683 |  |  | R
| Current Angle- Channel 75 | 75 | 6418 |  | 11684 | 11685 |  |  | R
| Current Angle- Channel 76 | 76 | 6419 |  | 11686 | 11687 |  |  | R
| Current Angle- Channel 77 | 77 | 6420 |  | 11688 | 11689 |  |  | R
| Current Angle- Channel 78 | 78 | 6421 |  | 11690 | 11691 |  |  | R
| Current Angle- Channel 79 | 79 | 6422 |  | 11692 | 11693 |  |  | R
| Current Angle- Channel 80 | 80 | 6423 |  | 11694 | 11695 |  |  | R
| Current Angle- Channel 81 | 81 | 6424 |  | 11696 | 11697 |  |  | R
| Current Angle- Channel 82 | 82 | 6425 |  | 11698 | 11699 |  |  | R
| Current Angle- Channel 83 | 83 | 6426 |  | 11700 | 11701 |  |  | R
| Current Angle- Channel 84 | 84 | 6427 |  | 11702 | 11703 |  |  | R
| Current Angle- Channel 85 | 85 | 6428 |  | 11704 | 11705 |  |  | R
| Current Angle- Channel 86 | 86 | 6429 |  | 11706 | 11707 |  |  | R
| Current Angle- Channel 87 | 87 | 6430 |  | 11708 | 11709 |  |  | R
| Current Angle- Channel 88 | 88 | 6431 |  | 11710 | 11711 |  |  | R
| Current Angle- Channel 89 | 89 | 6432 |  | 11712 | 11713 |  |  | R
| Current Angle- Channel 90 | 90 | 6433 |  | 11714 | 11715 |  |  | R
| Current Angle- Channel 91 | 91 | 6434 |  | 11716 | 11717 |  |  | R
| Current Angle- Channel 92 | 92 | 6435 |  | 11718 | 11719 |  |  | R
| Current Angle- Channel 93 | 93 | 6436 |  | 11720 | 11721 |  |  | R
| Current Angle- Channel 94 | 94 | 6437 |  | 11722 | 11723 |  |  | R
| Current Angle- Channel 95 | 95 | 6438 |  | 11724 | 11725 |  |  | R
| Current Angle- Channel 96 | 96 | 6439 |  | 11726 | 11727 |  |  | R
| Percent THD |  | 6440 | 6535 | 11728 | 11919 |  |  | R
| Percent THD - Channel 1 | 1 | 6440 |  | 11728 | 11729 |  |  | R
| Percent THD - Channel 2 | 2 | 6441 |  | 11730 | 11731 |  |  | R
| Percent THD - Channel 3 | 3 | 6442 |  | 11732 | 11733 |  |  | R
| Percent THD - Channel 4 | 4 | 6443 |  | 11734 | 11735 |  |  | R
| Percent THD - Channel 5 | 5 | 6444 |  | 11736 | 11737 |  |  | R
| Percent THD - Channel 6 | 6 | 6445 |  | 11738 | 11739 |  |  | R
| Percent THD - Channel 7 | 7 | 6446 |  | 11740 | 11741 |  |  | R
| Percent THD - Channel 8 | 8 | 6447 |  | 11742 | 11743 |  |  | R
| Percent THD - Channel 9 | 9 | 6448 |  | 11744 | 11745 |  |  | R
| Percent THD - Channel 10 | 10 | 6449 |  | 11746 | 11747 |  |  | R
| Percent THD - Channel 11 | 11 | 6450 |  | 11748 | 11749 |  |  | R
| Percent THD - Channel 12 | 12 | 6451 |  | 11750 | 11751 |  |  | R
| Percent THD - Channel 13 | 13 | 6452 |  | 11752 | 11753 |  |  | R
| Percent THD - Channel 14 | 14 | 6453 |  | 11754 | 11755 |  |  | R
| Percent THD - Channel 15 | 15 | 6454 |  | 11756 | 11757 |  |  | R
| Percent THD - Channel 16 | 16 | 6455 |  | 11758 | 11759 |  |  | R
| Percent THD - Channel 17 | 17 | 6456 |  | 11760 | 11761 |  |  | R
| Percent THD - Channel 18 | 18 | 6457 |  | 11762 | 11763 |  |  | R
| Percent THD - Channel 19 | 19 | 6458 |  | 11764 | 11765 |  |  | R
| Percent THD - Channel 20 | 20 | 6459 |  | 11766 | 11767 |  |  | R
| Percent THD - Channel 21 | 21 | 6460 |  | 11768 | 11769 |  |  | R
| Percent THD - Channel 22 | 22 | 6461 |  | 11770 | 11771 |  |  | R
| Percent THD - Channel 23 | 23 | 6462 |  | 11772 | 11773 |  |  | R
| Percent THD - Channel 24 | 24 | 6463 |  | 11774 | 11775 |  |  | R
| Percent THD - Channel 25 | 25 | 6464 |  | 11776 | 11777 |  |  | R
| Percent THD - Channel 26 | 26 | 6465 |  | 11778 | 11779 |  |  | R
| Percent THD - Channel 27 | 27 | 6466 |  | 11780 | 11781 |  |  | R
| Percent THD - Channel 28 | 28 | 6467 |  | 11782 | 11783 |  |  | R
| Percent THD - Channel 29 | 29 | 6468 |  | 11784 | 11785 |  |  | R
| Percent THD - Channel 30 | 30 | 6469 |  | 11786 | 11787 |  |  | R
| Percent THD - Channel 31 | 31 | 6470 |  | 11788 | 11789 |  |  | R
| Percent THD - Channel 32 | 32 | 6471 |  | 11790 | 11791 |  |  | R
| Percent THD - Channel 33 | 33 | 6472 |  | 11792 | 11793 |  |  | R
| Percent THD - Channel 34 | 34 | 6473 |  | 11794 | 11795 |  |  | R
| Percent THD - Channel 35 | 35 | 6474 |  | 11796 | 11797 |  |  | R
| Percent THD - Channel 36 | 36 | 6475 |  | 11798 | 11799 |  |  | R
| Percent THD - Channel 37 | 37 | 6476 |  | 11800 | 11801 |  |  | R
| Percent THD - Channel 38 | 38 | 6477 |  | 11802 | 11803 |  |  | R
| Percent THD - Channel 39 | 39 | 6478 |  | 11804 | 11805 |  |  | R
| Percent THD - Channel 40 | 40 | 6479 |  | 11806 | 11807 |  |  | R
| Percent THD - Channel 41 | 41 | 6480 |  | 11808 | 11809 |  |  | R
| Percent THD - Channel 42 | 42 | 6481 |  | 11810 | 11811 |  |  | R
| Percent THD - Channel 43 | 43 | 6482 |  | 11812 | 11813 |  |  | R
| Percent THD - Channel 44 | 44 | 6483 |  | 11814 | 11815 |  |  | R
| Percent THD - Channel 45 | 45 | 6484 |  | 11816 | 11817 |  |  | R
| Percent THD - Channel 46 | 46 | 6485 |  | 11818 | 11819 |  |  | R
| Percent THD - Channel 47 | 47 | 6486 |  | 11820 | 11821 |  |  | R
| Percent THD - Channel 48 | 48 | 6487 |  | 11822 | 11823 |  |  | R
| Percent THD - Channel 49 | 49 | 6488 |  | 11824 | 11825 |  |  | R
| Percent THD - Channel 50 | 50 | 6489 |  | 11826 | 11827 |  |  | R
| Percent THD - Channel 51 | 51 | 6490 |  | 11828 | 11829 |  |  | R
| Percent THD - Channel 52 | 52 | 6491 |  | 11830 | 11831 |  |  | R
| Percent THD - Channel 53 | 53 | 6492 |  | 11832 | 11833 |  |  | R
| Percent THD - Channel 54 | 54 | 6493 |  | 11834 | 11835 |  |  | R
| Percent THD - Channel 55 | 55 | 6494 |  | 11836 | 11837 |  |  | R
| Percent THD - Channel 56 | 56 | 6495 |  | 11838 | 11839 |  |  | R
| Percent THD - Channel 57 | 57 | 6496 |  | 11840 | 11841 |  |  | R
| Percent THD - Channel 58 | 58 | 6497 |  | 11842 | 11843 |  |  | R
| Percent THD - Channel 59 | 59 | 6498 |  | 11844 | 11845 |  |  | R
| Percent THD - Channel 60 | 60 | 6499 |  | 11846 | 11847 |  |  | R
| Percent THD - Channel 61 | 61 | 6500 |  | 11848 | 11849 |  |  | R
| Percent THD - Channel 62 | 62 | 6501 |  | 11850 | 11851 |  |  | R
| Percent THD - Channel 63 | 63 | 6502 |  | 11852 | 11853 |  |  | R
| Percent THD - Channel 64 | 64 | 6503 |  | 11854 | 11855 |  |  | R
| Percent THD - Channel 65 | 65 | 6504 |  | 11856 | 11857 |  |  | R
| Percent THD - Channel 66 | 66 | 6505 |  | 11858 | 11859 |  |  | R
| Percent THD - Channel 67 | 67 | 6506 |  | 11860 | 11861 |  |  | R
| Percent THD - Channel 68 | 68 | 6507 |  | 11862 | 11863 |  |  | R
| Percent THD - Channel 69 | 69 | 6508 |  | 11864 | 11865 |  |  | R
| Percent THD - Channel 70 | 70 | 6509 |  | 11866 | 11867 |  |  | R
| Percent THD - Channel 71 | 71 | 6510 |  | 11868 | 11869 |  |  | R
| Percent THD - Channel 72 | 72 | 6511 |  | 11870 | 11871 |  |  | R
| Percent THD - Channel 73 | 73 | 6512 |  | 11872 | 11873 |  |  | R
| Percent THD - Channel 74 | 74 | 6513 |  | 11874 | 11875 |  |  | R
| Percent THD - Channel 75 | 75 | 6514 |  | 11876 | 11877 |  |  | R
| Percent THD - Channel 76 | 76 | 6515 |  | 11878 | 11879 |  |  | R
| Percent THD - Channel 77 | 77 | 6516 |  | 11880 | 11881 |  |  | R
| Percent THD - Channel 78 | 78 | 6517 |  | 11882 | 11883 |  |  | R
| Percent THD - Channel 79 | 79 | 6518 |  | 11884 | 11885 |  |  | R
| Percent THD - Channel 80 | 80 | 6519 |  | 11886 | 11887 |  |  | R
| Percent THD - Channel 81 | 81 | 6520 |  | 11888 | 11889 |  |  | R
| Percent THD - Channel 82 | 82 | 6521 |  | 11890 | 11891 |  |  | R
| Percent THD - Channel 83 | 83 | 6522 |  | 11892 | 11893 |  |  | R
| Percent THD - Channel 84 | 84 | 6523 |  | 11894 | 11895 |  |  | R
| Percent THD - Channel 85 | 85 | 6524 |  | 11896 | 11897 |  |  | R
| Percent THD - Channel 86 | 86 | 6525 |  | 11898 | 11899 |  |  | R
| Percent THD - Channel 87 | 87 | 6526 |  | 11900 | 11901 |  |  | R
| Percent THD - Channel 88 | 88 | 6527 |  | 11902 | 11903 |  |  | R
| Percent THD - Channel 89 | 89 | 6528 |  | 11904 | 11905 |  |  | R
| Percent THD - Channel 90 | 90 | 6529 |  | 11906 | 11907 |  |  | R
| Percent THD - Channel 91 | 91 | 6530 |  | 11908 | 11909 |  |  | R
| Percent THD - Channel 92 | 92 | 6531 |  | 11910 | 11911 |  |  | R
| Percent THD - Channel 93 | 93 | 6532 |  | 11912 | 11913 |  |  | R
| Percent THD - Channel 94 | 94 | 6533 |  | 11914 | 11915 |  |  | R
| Percent THD - Channel 95 | 95 | 6534 |  | 11916 | 11917 |  |  | R
| Percent THD - Channel 96 | 96 | 6535 |  | 11918 | 11919 |  |  | R
| Max Current |  | 6536 | 6631 | 11920 | 12111 |  |  | R | NV
| Max Current- Channel 1 | 1 | 6536 |  | 11920 | 11921 |  |  | R | NV
| Max Current- Channel 2 | 2 | 6537 |  | 11922 | 11923 |  |  | R | NV
| Max Current- Channel 3 | 3 | 6538 |  | 11924 | 11925 |  |  | R | NV
| Max Current- Channel 4 | 4 | 6539 |  | 11926 | 11927 |  |  | R | NV
| Max Current- Channel 5 | 5 | 6540 |  | 11928 | 11929 |  |  | R | NV
| Max Current- Channel 6 | 6 | 6541 |  | 11930 | 11931 |  |  | R | NV
| Max Current- Channel 7 | 7 | 6542 |  | 11932 | 11933 |  |  | R | NV
| Max Current- Channel 8 | 8 | 6543 |  | 11934 | 11935 |  |  | R | NV
| Max Current- Channel 9 | 9 | 6544 |  | 11936 | 11937 |  |  | R | NV
| Max Current- Channel 10 | 10 | 6545 |  | 11938 | 11939 |  |  | R | NV
| Max Current- Channel 11 | 11 | 6546 |  | 11940 | 11941 |  |  | R | NV
| Max Current- Channel 12 | 12 | 6547 |  | 11942 | 11943 |  |  | R | NV
| Max Current- Channel 13 | 13 | 6548 |  | 11944 | 11945 |  |  | R | NV
| Max Current- Channel 14 | 14 | 6549 |  | 11946 | 11947 |  |  | R | NV
| Max Current- Channel 15 | 15 | 6550 |  | 11948 | 11949 |  |  | R | NV
| Max Current- Channel 16 | 16 | 6551 |  | 11950 | 11951 |  |  | R | NV
| Max Current- Channel 17 | 17 | 6552 |  | 11952 | 11953 |  |  | R | NV
| Max Current- Channel 18 | 18 | 6553 |  | 11954 | 11955 |  |  | R | NV
| Max Current- Channel 19 | 19 | 6554 |  | 11956 | 11957 |  |  | R | NV
| Max Current- Channel 20 | 20 | 6555 |  | 11958 | 11959 |  |  | R | NV
| Max Current- Channel 21 | 21 | 6556 |  | 11960 | 11961 |  |  | R | NV
| Max Current- Channel 22 | 22 | 6557 |  | 11962 | 11963 |  |  | R | NV
| Max Current- Channel 23 | 23 | 6558 |  | 11964 | 11965 |  |  | R | NV
| Max Current- Channel 24 | 24 | 6559 |  | 11966 | 11967 |  |  | R | NV
| Max Current- Channel 25 | 25 | 6560 |  | 11968 | 11969 |  |  | R | NV
| Max Current- Channel 26 | 26 | 6561 |  | 11970 | 11971 |  |  | R | NV
| Max Current- Channel 27 | 27 | 6562 |  | 11972 | 11973 |  |  | R | NV
| Max Current- Channel 28 | 28 | 6563 |  | 11974 | 11975 |  |  | R | NV
| Max Current- Channel 29 | 29 | 6564 |  | 11976 | 11977 |  |  | R | NV
| Max Current- Channel 30 | 30 | 6565 |  | 11978 | 11979 |  |  | R | NV
| Max Current- Channel 31 | 31 | 6566 |  | 11980 | 11981 |  |  | R | NV
| Max Current- Channel 32 | 32 | 6567 |  | 11982 | 11983 |  |  | R | NV
| Max Current- Channel 33 | 33 | 6568 |  | 11984 | 11985 |  |  | R | NV
| Max Current- Channel 34 | 34 | 6569 |  | 11986 | 11987 |  |  | R | NV
| Max Current- Channel 35 | 35 | 6570 |  | 11988 | 11989 |  |  | R | NV
| Max Current- Channel 36 | 36 | 6571 |  | 11990 | 11991 |  |  | R | NV
| Max Current- Channel 37 | 37 | 6572 |  | 11992 | 11993 |  |  | R | NV
| Max Current- Channel 38 | 38 | 6573 |  | 11994 | 11995 |  |  | R | NV
| Max Current- Channel 39 | 39 | 6574 |  | 11996 | 11997 |  |  | R | NV
| Max Current- Channel 40 | 40 | 6575 |  | 11998 | 11999 |  |  | R | NV
| Max Current- Channel 41 | 41 | 6576 |  | 12000 | 12001 |  |  | R | NV
| Max Current- Channel 42 | 42 | 6577 |  | 12002 | 12003 |  |  | R | NV
| Max Current- Channel 43 | 43 | 6578 |  | 12004 | 12005 |  |  | R | NV
| Max Current- Channel 44 | 44 | 6579 |  | 12006 | 12007 |  |  | R | NV
| Max Current- Channel 45 | 45 | 6580 |  | 12008 | 12009 |  |  | R | NV
| Max Current- Channel 46 | 46 | 6581 |  | 12010 | 12011 |  |  | R | NV
| Max Current- Channel 47 | 47 | 6582 |  | 12012 | 12013 |  |  | R | NV
| Max Current- Channel 48 | 48 | 6583 |  | 12014 | 12015 |  |  | R | NV
| Max Current- Channel 49 | 49 | 6584 |  | 12016 | 12017 |  |  | R | NV
| Max Current- Channel 50 | 50 | 6585 |  | 12018 | 12019 |  |  | R | NV
| Max Current- Channel 51 | 51 | 6586 |  | 12020 | 12021 |  |  | R | NV
| Max Current- Channel 52 | 52 | 6587 |  | 12022 | 12023 |  |  | R | NV
| Max Current- Channel 53 | 53 | 6588 |  | 12024 | 12025 |  |  | R | NV
| Max Current- Channel 54 | 54 | 6589 |  | 12026 | 12027 |  |  | R | NV
| Max Current- Channel 55 | 55 | 6590 |  | 12028 | 12029 |  |  | R | NV
| Max Current- Channel 56 | 56 | 6591 |  | 12030 | 12031 |  |  | R | NV
| Max Current- Channel 57 | 57 | 6592 |  | 12032 | 12033 |  |  | R | NV
| Max Current- Channel 58 | 58 | 6593 |  | 12034 | 12035 |  |  | R | NV
| Max Current- Channel 59 | 59 | 6594 |  | 12036 | 12037 |  |  | R | NV
| Max Current- Channel 60 | 60 | 6595 |  | 12038 | 12039 |  |  | R | NV
| Max Current- Channel 61 | 61 | 6596 |  | 12040 | 12041 |  |  | R | NV
| Max Current- Channel 62 | 62 | 6597 |  | 12042 | 12043 |  |  | R | NV
| Max Current- Channel 63 | 63 | 6598 |  | 12044 | 12045 |  |  | R | NV
| Max Current- Channel 64 | 64 | 6599 |  | 12046 | 12047 |  |  | R | NV
| Max Current- Channel 65 | 65 | 6600 |  | 12048 | 12049 |  |  | R | NV
| Max Current- Channel 66 | 66 | 6601 |  | 12050 | 12051 |  |  | R | NV
| Max Current- Channel 67 | 67 | 6602 |  | 12052 | 12053 |  |  | R | NV
| Max Current- Channel 68 | 68 | 6603 |  | 12054 | 12055 |  |  | R | NV
| Max Current- Channel 69 | 69 | 6604 |  | 12056 | 12057 |  |  | R | NV
| Max Current- Channel 70 | 70 | 6605 |  | 12058 | 12059 |  |  | R | NV
| Max Current- Channel 71 | 71 | 6606 |  | 12060 | 12061 |  |  | R | NV
| Max Current- Channel 72 | 72 | 6607 |  | 12062 | 12063 |  |  | R | NV
| Max Current- Channel 73 | 73 | 6608 |  | 12064 | 12065 |  |  | R | NV
| Max Current- Channel 74 | 74 | 6609 |  | 12066 | 12067 |  |  | R | NV
| Max Current- Channel 75 | 75 | 6610 |  | 12068 | 12069 |  |  | R | NV
| Max Current- Channel 76 | 76 | 6611 |  | 12070 | 12071 |  |  | R | NV
| Max Current- Channel 77 | 77 | 6612 |  | 12072 | 12073 |  |  | R | NV
| Max Current- Channel 78 | 78 | 6613 |  | 12074 | 12075 |  |  | R | NV
| Max Current- Channel 79 | 79 | 6614 |  | 12076 | 12077 |  |  | R | NV
| Max Current- Channel 80 | 80 | 6615 |  | 12078 | 12079 |  |  | R | NV
| Max Current- Channel 81 | 81 | 6616 |  | 12080 | 12081 |  |  | R | NV
| Max Current- Channel 82 | 82 | 6617 |  | 12082 | 12083 |  |  | R | NV
| Max Current- Channel 83 | 83 | 6618 |  | 12084 | 12085 |  |  | R | NV
| Max Current- Channel 84 | 84 | 6619 |  | 12086 | 12087 |  |  | R | NV
| Max Current- Channel 85 | 85 | 6620 |  | 12088 | 12089 |  |  | R | NV
| Max Current- Channel 86 | 86 | 6621 |  | 12090 | 12091 |  |  | R | NV
| Max Current- Channel 87 | 87 | 6622 |  | 12092 | 12093 |  |  | R | NV
| Max Current- Channel 88 | 88 | 6623 |  | 12094 | 12095 |  |  | R | NV
| Max Current- Channel 89 | 89 | 6624 |  | 12096 | 12097 |  |  | R | NV
| Max Current- Channel 90 | 90 | 6625 |  | 12098 | 12099 |  |  | R | NV
| Max Current- Channel 91 | 91 | 6626 |  | 12100 | 12101 |  |  | R | NV
| Max Current- Channel 92 | 92 | 6627 |  | 12102 | 12103 |  |  | R | NV
| Max Current- Channel 93 | 93 | 6628 |  | 12104 | 12105 |  |  | R | NV
| Max Current- Channel 94 | 94 | 6629 |  | 12106 | 12107 |  |  | R | NV
| Max Current- Channel 95 | 95 | 6630 |  | 12108 | 12109 |  |  | R | NV
| Max Current- Channel 96 | 96 | 6631 |  | 12110 | 12111 |  |  | R | NV
| Max kW |  | 6632 | 6727 | 12112 | 12303 |  |  | R | NV
| Max kW- Channel 1 | 1 | 6632 |  | 12112 | 12113 |  |  | R | NV
| Max kW- Channel 2 | 2 | 6633 |  | 12114 | 12115 |  |  | R | NV
| Max kW- Channel 3 | 3 | 6634 |  | 12116 | 12117 |  |  | R | NV
| Max kW- Channel 4 | 4 | 6635 |  | 12118 | 12119 |  |  | R | NV
| Max kW- Channel 5 | 5 | 6636 |  | 12120 | 12121 |  |  | R | NV
| Max kW- Channel 6 | 6 | 6637 |  | 12122 | 12123 |  |  | R | NV
| Max kW- Channel 7 | 7 | 6638 |  | 12124 | 12125 |  |  | R | NV
| Max kW- Channel 8 | 8 | 6639 |  | 12126 | 12127 |  |  | R | NV
| Max kW- Channel 9 | 9 | 6640 |  | 12128 | 12129 |  |  | R | NV
| Max kW- Channel 10 | 10 | 6641 |  | 12130 | 12131 |  |  | R | NV
| Max kW- Channel 11 | 11 | 6642 |  | 12132 | 12133 |  |  | R | NV
| Max kW- Channel 12 | 12 | 6643 |  | 12134 | 12135 |  |  | R | NV
| Max kW- Channel 13 | 13 | 6644 |  | 12136 | 12137 |  |  | R | NV
| Max kW- Channel 14 | 14 | 6645 |  | 12138 | 12139 |  |  | R | NV
| Max kW- Channel 15 | 15 | 6646 |  | 12140 | 12141 |  |  | R | NV
| Max kW- Channel 16 | 16 | 6647 |  | 12142 | 12143 |  |  | R | NV
| Max kW- Channel 17 | 17 | 6648 |  | 12144 | 12145 |  |  | R | NV
| Max kW- Channel 18 | 18 | 6649 |  | 12146 | 12147 |  |  | R | NV
| Max kW- Channel 19 | 19 | 6650 |  | 12148 | 12149 |  |  | R | NV
| Max kW- Channel 20 | 20 | 6651 |  | 12150 | 12151 |  |  | R | NV
| Max kW- Channel 21 | 21 | 6652 |  | 12152 | 12153 |  |  | R | NV
| Max kW- Channel 22 | 22 | 6653 |  | 12154 | 12155 |  |  | R | NV
| Max kW- Channel 23 | 23 | 6654 |  | 12156 | 12157 |  |  | R | NV
| Max kW- Channel 24 | 24 | 6655 |  | 12158 | 12159 |  |  | R | NV
| Max kW- Channel 25 | 25 | 6656 |  | 12160 | 12161 |  |  | R | NV
| Max kW- Channel 26 | 26 | 6657 |  | 12162 | 12163 |  |  | R | NV
| Max kW- Channel 27 | 27 | 6658 |  | 12164 | 12165 |  |  | R | NV
| Max kW- Channel 28 | 28 | 6659 |  | 12166 | 12167 |  |  | R | NV
| Max kW- Channel 29 | 29 | 6660 |  | 12168 | 12169 |  |  | R | NV
| Max kW- Channel 30 | 30 | 6661 |  | 12170 | 12171 |  |  | R | NV
| Max kW- Channel 31 | 31 | 6662 |  | 12172 | 12173 |  |  | R | NV
| Max kW- Channel 32 | 32 | 6663 |  | 12174 | 12175 |  |  | R | NV
| Max kW- Channel 33 | 33 | 6664 |  | 12176 | 12177 |  |  | R | NV
| Max kW- Channel 34 | 34 | 6665 |  | 12178 | 12179 |  |  | R | NV
| Max kW- Channel 35 | 35 | 6666 |  | 12180 | 12181 |  |  | R | NV
| Max kW- Channel 36 | 36 | 6667 |  | 12182 | 12183 |  |  | R | NV
| Max kW- Channel 37 | 37 | 6668 |  | 12184 | 12185 |  |  | R | NV
| Max kW- Channel 38 | 38 | 6669 |  | 12186 | 12187 |  |  | R | NV
| Max kW- Channel 39 | 39 | 6670 |  | 12188 | 12189 |  |  | R | NV
| Max kW- Channel 40 | 40 | 6671 |  | 12190 | 12191 |  |  | R | NV
| Max kW- Channel 41 | 41 | 6672 |  | 12192 | 12193 |  |  | R | NV
| Max kW- Channel 42 | 42 | 6673 |  | 12194 | 12195 |  |  | R | NV
| Max kW- Channel 43 | 43 | 6674 |  | 12196 | 12197 |  |  | R | NV
| Max kW- Channel 44 | 44 | 6675 |  | 12198 | 12199 |  |  | R | NV
| Max kW- Channel 45 | 45 | 6676 |  | 12200 | 12201 |  |  | R | NV
| Max kW- Channel 46 | 46 | 6677 |  | 12202 | 12203 |  |  | R | NV
| Max kW- Channel 47 | 47 | 6678 |  | 12204 | 12205 |  |  | R | NV
| Max kW- Channel 48 | 48 | 6679 |  | 12206 | 12207 |  |  | R | NV
| Max kW- Channel 49 | 49 | 6680 |  | 12208 | 12209 |  |  | R | NV
| Max kW- Channel 50 | 50 | 6681 |  | 12210 | 12211 |  |  | R | NV
| Max kW- Channel 51 | 51 | 6682 |  | 12212 | 12213 |  |  | R | NV
| Max kW- Channel 52 | 52 | 6683 |  | 12214 | 12215 |  |  | R | NV
| Max kW- Channel 53 | 53 | 6684 |  | 12216 | 12217 |  |  | R | NV
| Max kW- Channel 54 | 54 | 6685 |  | 12218 | 12219 |  |  | R | NV
| Max kW- Channel 55 | 55 | 6686 |  | 12220 | 12221 |  |  | R | NV
| Max kW- Channel 56 | 56 | 6687 |  | 12222 | 12223 |  |  | R | NV
| Max kW- Channel 57 | 57 | 6688 |  | 12224 | 12225 |  |  | R | NV
| Max kW- Channel 58 | 58 | 6689 |  | 12226 | 12227 |  |  | R | NV
| Max kW- Channel 59 | 59 | 6690 |  | 12228 | 12229 |  |  | R | NV
| Max kW- Channel 60 | 60 | 6691 |  | 12230 | 12231 |  |  | R | NV
| Max kW- Channel 61 | 61 | 6692 |  | 12232 | 12233 |  |  | R | NV
| Max kW- Channel 62 | 62 | 6693 |  | 12234 | 12235 |  |  | R | NV
| Max kW- Channel 63 | 63 | 6694 |  | 12236 | 12237 |  |  | R | NV
| Max kW- Channel 64 | 64 | 6695 |  | 12238 | 12239 |  |  | R | NV
| Max kW- Channel 65 | 65 | 6696 |  | 12240 | 12241 |  |  | R | NV
| Max kW- Channel 66 | 66 | 6697 |  | 12242 | 12243 |  |  | R | NV
| Max kW- Channel 67 | 67 | 6698 |  | 12244 | 12245 |  |  | R | NV
| Max kW- Channel 68 | 68 | 6699 |  | 12246 | 12247 |  |  | R | NV
| Max kW- Channel 69 | 69 | 6700 |  | 12248 | 12249 |  |  | R | NV
| Max kW- Channel 70 | 70 | 6701 |  | 12250 | 12251 |  |  | R | NV
| Max kW- Channel 71 | 71 | 6702 |  | 12252 | 12253 |  |  | R | NV
| Max kW- Channel 72 | 72 | 6703 |  | 12254 | 12255 |  |  | R | NV
| Max kW- Channel 73 | 73 | 6704 |  | 12256 | 12257 |  |  | R | NV
| Max kW- Channel 74 | 74 | 6705 |  | 12258 | 12259 |  |  | R | NV
| Max kW- Channel 75 | 75 | 6706 |  | 12260 | 12261 |  |  | R | NV
| Max kW- Channel 76 | 76 | 6707 |  | 12262 | 12263 |  |  | R | NV
| Max kW- Channel 77 | 77 | 6708 |  | 12264 | 12265 |  |  | R | NV
| Max kW- Channel 78 | 78 | 6709 |  | 12266 | 12267 |  |  | R | NV
| Max kW- Channel 79 | 79 | 6710 |  | 12268 | 12269 |  |  | R | NV
| Max kW- Channel 80 | 80 | 6711 |  | 12270 | 12271 |  |  | R | NV
| Max kW- Channel 81 | 81 | 6712 |  | 12272 | 12273 |  |  | R | NV
| Max kW- Channel 82 | 82 | 6713 |  | 12274 | 12275 |  |  | R | NV
| Max kW- Channel 83 | 83 | 6714 |  | 12276 | 12277 |  |  | R | NV
| Max kW- Channel 84 | 84 | 6715 |  | 12278 | 12279 |  |  | R | NV
| Max kW- Channel 85 | 85 | 6716 |  | 12280 | 12281 |  |  | R | NV
| Max kW- Channel 86 | 86 | 6717 |  | 12282 | 12283 |  |  | R | NV
| Max kW- Channel 87 | 87 | 6718 |  | 12284 | 12285 |  |  | R | NV
| Max kW- Channel 88 | 88 | 6719 |  | 12286 | 12287 |  |  | R | NV
| Max kW- Channel 89 | 89 | 6720 |  | 12288 | 12289 |  |  | R | NV
| Max kW- Channel 90 | 90 | 6721 |  | 12290 | 12291 |  |  | R | NV
| Max kW- Channel 91 | 91 | 6722 |  | 12292 | 12293 |  |  | R | NV
| Max kW- Channel 92 | 92 | 6723 |  | 12294 | 12295 |  |  | R | NV
| Max kW- Channel 93 | 93 | 6724 |  | 12296 | 12297 |  |  | R | NV
| Max kW- Channel 94 | 94 | 6725 |  | 12298 | 12299 |  |  | R | NV
| Max kW- Channel 95 | 95 | 6726 |  | 12300 | 12301 |  |  | R | NV
| Max kW- Channel 96 | 96 | 6727 |  | 12302 | 12303 |  |  | R | NV
| Current Demand |  | 6728 | 6823 | 12304 | 12495 |  |  | R
| Current Demand- Channel 1 | 1 | 6728 |  | 12304 | 12305 |  |  | R
| Current Demand- Channel 2 | 2 | 6729 |  | 12306 | 12307 |  |  | R
| Current Demand- Channel 3 | 3 | 6730 |  | 12308 | 12309 |  |  | R
| Current Demand- Channel 4 | 4 | 6731 |  | 12310 | 12311 |  |  | R
| Current Demand- Channel 5 | 5 | 6732 |  | 12312 | 12313 |  |  | R
| Current Demand- Channel 6 | 6 | 6733 |  | 12314 | 12315 |  |  | R
| Current Demand- Channel 7 | 7 | 6734 |  | 12316 | 12317 |  |  | R
| Current Demand- Channel 8 | 8 | 6735 |  | 12318 | 12319 |  |  | R
| Current Demand- Channel 9 | 9 | 6736 |  | 12320 | 12321 |  |  | R
| Current Demand- Channel 10 | 10 | 6737 |  | 12322 | 12323 |  |  | R
| Current Demand- Channel 11 | 11 | 6738 |  | 12324 | 12325 |  |  | R
| Current Demand- Channel 12 | 12 | 6739 |  | 12326 | 12327 |  |  | R
| Current Demand- Channel 13 | 13 | 6740 |  | 12328 | 12329 |  |  | R
| Current Demand- Channel 14 | 14 | 6741 |  | 12330 | 12331 |  |  | R
| Current Demand- Channel 15 | 15 | 6742 |  | 12332 | 12333 |  |  | R
| Current Demand- Channel 16 | 16 | 6743 |  | 12334 | 12335 |  |  | R
| Current Demand- Channel 17 | 17 | 6744 |  | 12336 | 12337 |  |  | R
| Current Demand- Channel 18 | 18 | 6745 |  | 12338 | 12339 |  |  | R
| Current Demand- Channel 19 | 19 | 6746 |  | 12340 | 12341 |  |  | R
| Current Demand- Channel 20 | 20 | 6747 |  | 12342 | 12343 |  |  | R
| Current Demand- Channel 21 | 21 | 6748 |  | 12344 | 12345 |  |  | R
| Current Demand- Channel 22 | 22 | 6749 |  | 12346 | 12347 |  |  | R
| Current Demand- Channel 23 | 23 | 6750 |  | 12348 | 12349 |  |  | R
| Current Demand- Channel 24 | 24 | 6751 |  | 12350 | 12351 |  |  | R
| Current Demand- Channel 25 | 25 | 6752 |  | 12352 | 12353 |  |  | R
| Current Demand- Channel 26 | 26 | 6753 |  | 12354 | 12355 |  |  | R
| Current Demand- Channel 27 | 27 | 6754 |  | 12356 | 12357 |  |  | R
| Current Demand- Channel 28 | 28 | 6755 |  | 12358 | 12359 |  |  | R
| Current Demand- Channel 29 | 29 | 6756 |  | 12360 | 12361 |  |  | R
| Current Demand- Channel 30 | 30 | 6757 |  | 12362 | 12363 |  |  | R
| Current Demand- Channel 31 | 31 | 6758 |  | 12364 | 12365 |  |  | R
| Current Demand- Channel 32 | 32 | 6759 |  | 12366 | 12367 |  |  | R
| Current Demand- Channel 33 | 33 | 6760 |  | 12368 | 12369 |  |  | R
| Current Demand- Channel 34 | 34 | 6761 |  | 12370 | 12371 |  |  | R
| Current Demand- Channel 35 | 35 | 6762 |  | 12372 | 12373 |  |  | R
| Current Demand- Channel 36 | 36 | 6763 |  | 12374 | 12375 |  |  | R
| Current Demand- Channel 37 | 37 | 6764 |  | 12376 | 12377 |  |  | R
| Current Demand- Channel 38 | 38 | 6765 |  | 12378 | 12379 |  |  | R
| Current Demand- Channel 39 | 39 | 6766 |  | 12380 | 12381 |  |  | R
| Current Demand- Channel 40 | 40 | 6767 |  | 12382 | 12383 |  |  | R
| Current Demand- Channel 41 | 41 | 6768 |  | 12384 | 12385 |  |  | R
| Current Demand- Channel 42 | 42 | 6769 |  | 12386 | 12387 |  |  | R
| Current Demand- Channel 43 | 43 | 6770 |  | 12388 | 12389 |  |  | R
| Current Demand- Channel 44 | 44 | 6771 |  | 12390 | 12391 |  |  | R
| Current Demand- Channel 45 | 45 | 6772 |  | 12392 | 12393 |  |  | R
| Current Demand- Channel 46 | 46 | 6773 |  | 12394 | 12395 |  |  | R
| Current Demand- Channel 47 | 47 | 6774 |  | 12396 | 12397 |  |  | R
| Current Demand- Channel 48 | 48 | 6775 |  | 12398 | 12399 |  |  | R
| Current Demand- Channel 49 | 49 | 6776 |  | 12400 | 12401 |  |  | R
| Current Demand- Channel 50 | 50 | 6777 |  | 12402 | 12403 |  |  | R
| Current Demand- Channel 51 | 51 | 6778 |  | 12404 | 12405 |  |  | R
| Current Demand- Channel 52 | 52 | 6779 |  | 12406 | 12407 |  |  | R
| Current Demand- Channel 53 | 53 | 6780 |  | 12408 | 12409 |  |  | R
| Current Demand- Channel 54 | 54 | 6781 |  | 12410 | 12411 |  |  | R
| Current Demand- Channel 55 | 55 | 6782 |  | 12412 | 12413 |  |  | R
| Current Demand- Channel 56 | 56 | 6783 |  | 12414 | 12415 |  |  | R
| Current Demand- Channel 57 | 57 | 6784 |  | 12416 | 12417 |  |  | R
| Current Demand- Channel 58 | 58 | 6785 |  | 12418 | 12419 |  |  | R
| Current Demand- Channel 59 | 59 | 6786 |  | 12420 | 12421 |  |  | R
| Current Demand- Channel 60 | 60 | 6787 |  | 12422 | 12423 |  |  | R
| Current Demand- Channel 61 | 61 | 6788 |  | 12424 | 12425 |  |  | R
| Current Demand- Channel 62 | 62 | 6789 |  | 12426 | 12427 |  |  | R
| Current Demand- Channel 63 | 63 | 6790 |  | 12428 | 12429 |  |  | R
| Current Demand- Channel 64 | 64 | 6791 |  | 12430 | 12431 |  |  | R
| Current Demand- Channel 65 | 65 | 6792 |  | 12432 | 12433 |  |  | R
| Current Demand- Channel 66 | 66 | 6793 |  | 12434 | 12435 |  |  | R
| Current Demand- Channel 67 | 67 | 6794 |  | 12436 | 12437 |  |  | R
| Current Demand- Channel 68 | 68 | 6795 |  | 12438 | 12439 |  |  | R
| Current Demand- Channel 69 | 69 | 6796 |  | 12440 | 12441 |  |  | R
| Current Demand- Channel 70 | 70 | 6797 |  | 12442 | 12443 |  |  | R
| Current Demand- Channel 71 | 71 | 6798 |  | 12444 | 12445 |  |  | R
| Current Demand- Channel 72 | 72 | 6799 |  | 12446 | 12447 |  |  | R
| Current Demand- Channel 73 | 73 | 6800 |  | 12448 | 12449 |  |  | R
| Current Demand- Channel 74 | 74 | 6801 |  | 12450 | 12451 |  |  | R
| Current Demand- Channel 75 | 75 | 6802 |  | 12452 | 12453 |  |  | R
| Current Demand- Channel 76 | 76 | 6803 |  | 12454 | 12455 |  |  | R
| Current Demand- Channel 77 | 77 | 6804 |  | 12456 | 12457 |  |  | R
| Current Demand- Channel 78 | 78 | 6805 |  | 12458 | 12459 |  |  | R
| Current Demand- Channel 79 | 79 | 6806 |  | 12460 | 12461 |  |  | R
| Current Demand- Channel 80 | 80 | 6807 |  | 12462 | 12463 |  |  | R
| Current Demand- Channel 81 | 81 | 6808 |  | 12464 | 12465 |  |  | R
| Current Demand- Channel 82 | 82 | 6809 |  | 12466 | 12467 |  |  | R
| Current Demand- Channel 83 | 83 | 6810 |  | 12468 | 12469 |  |  | R
| Current Demand- Channel 84 | 84 | 6811 |  | 12470 | 12471 |  |  | R
| Current Demand- Channel 85 | 85 | 6812 |  | 12472 | 12473 |  |  | R
| Current Demand- Channel 86 | 86 | 6813 |  | 12474 | 12475 |  |  | R
| Current Demand- Channel 87 | 87 | 6814 |  | 12476 | 12477 |  |  | R
| Current Demand- Channel 88 | 88 | 6815 |  | 12478 | 12479 |  |  | R
| Current Demand- Channel 89 | 89 | 6816 |  | 12480 | 12481 |  |  | R
| Current Demand- Channel 90 | 90 | 6817 |  | 12482 | 12483 |  |  | R
| Current Demand- Channel 91 | 91 | 6818 |  | 12484 | 12485 |  |  | R
| Current Demand- Channel 92 | 92 | 6819 |  | 12486 | 12487 |  |  | R
| Current Demand- Channel 93 | 93 | 6820 |  | 12488 | 12489 |  |  | R
| Current Demand- Channel 94 | 94 | 6821 |  | 12490 | 12491 |  |  | R
| Current Demand- Channel 95 | 95 | 6822 |  | 12492 | 12493 |  |  | R
| Current Demand- Channel 96 | 96 | 6823 |  | 12494 | 12495 |  |  | R
| kW Demand |  | 6824 | 6919 | 12496 | 12687 |  |  | R
| kW Demand- Channel 1 | 1 | 6824 |  | 12496 | 12497 |  |  | R
| kW Demand- Channel 2 | 2 | 6825 |  | 12498 | 12499 |  |  | R
| kW Demand- Channel 3 | 3 | 6826 |  | 12500 | 12501 |  |  | R
| kW Demand- Channel 4 | 4 | 6827 |  | 12502 | 12503 |  |  | R
| kW Demand- Channel 5 | 5 | 6828 |  | 12504 | 12505 |  |  | R
| kW Demand- Channel 6 | 6 | 6829 |  | 12506 | 12507 |  |  | R
| kW Demand- Channel 7 | 7 | 6830 |  | 12508 | 12509 |  |  | R
| kW Demand- Channel 8 | 8 | 6831 |  | 12510 | 12511 |  |  | R
| kW Demand- Channel 9 | 9 | 6832 |  | 12512 | 12513 |  |  | R
| kW Demand- Channel 10 | 10 | 6833 |  | 12514 | 12515 |  |  | R
| kW Demand- Channel 11 | 11 | 6834 |  | 12516 | 12517 |  |  | R
| kW Demand- Channel 12 | 12 | 6835 |  | 12518 | 12519 |  |  | R
| kW Demand- Channel 13 | 13 | 6836 |  | 12520 | 12521 |  |  | R
| kW Demand- Channel 14 | 14 | 6837 |  | 12522 | 12523 |  |  | R
| kW Demand- Channel 15 | 15 | 6838 |  | 12524 | 12525 |  |  | R
| kW Demand- Channel 16 | 16 | 6839 |  | 12526 | 12527 |  |  | R
| kW Demand- Channel 17 | 17 | 6840 |  | 12528 | 12529 |  |  | R
| kW Demand- Channel 18 | 18 | 6841 |  | 12530 | 12531 |  |  | R
| kW Demand- Channel 19 | 19 | 6842 |  | 12532 | 12533 |  |  | R
| kW Demand- Channel 20 | 20 | 6843 |  | 12534 | 12535 |  |  | R
| kW Demand- Channel 21 | 21 | 6844 |  | 12536 | 12537 |  |  | R
| kW Demand- Channel 22 | 22 | 6845 |  | 12538 | 12539 |  |  | R
| kW Demand- Channel 23 | 23 | 6846 |  | 12540 | 12541 |  |  | R
| kW Demand- Channel 24 | 24 | 6847 |  | 12542 | 12543 |  |  | R
| kW Demand- Channel 25 | 25 | 6848 |  | 12544 | 12545 |  |  | R
| kW Demand- Channel 26 | 26 | 6849 |  | 12546 | 12547 |  |  | R
| kW Demand- Channel 27 | 27 | 6850 |  | 12548 | 12549 |  |  | R
| kW Demand- Channel 28 | 28 | 6851 |  | 12550 | 12551 |  |  | R
| kW Demand- Channel 29 | 29 | 6852 |  | 12552 | 12553 |  |  | R
| kW Demand- Channel 30 | 30 | 6853 |  | 12554 | 12555 |  |  | R
| kW Demand- Channel 31 | 31 | 6854 |  | 12556 | 12557 |  |  | R
| kW Demand- Channel 32 | 32 | 6855 |  | 12558 | 12559 |  |  | R
| kW Demand- Channel 33 | 33 | 6856 |  | 12560 | 12561 |  |  | R
| kW Demand- Channel 34 | 34 | 6857 |  | 12562 | 12563 |  |  | R
| kW Demand- Channel 35 | 35 | 6858 |  | 12564 | 12565 |  |  | R
| kW Demand- Channel 36 | 36 | 6859 |  | 12566 | 12567 |  |  | R
| kW Demand- Channel 37 | 37 | 6860 |  | 12568 | 12569 |  |  | R
| kW Demand- Channel 38 | 38 | 6861 |  | 12570 | 12571 |  |  | R
| kW Demand- Channel 39 | 39 | 6862 |  | 12572 | 12573 |  |  | R
| kW Demand- Channel 40 | 40 | 6863 |  | 12574 | 12575 |  |  | R
| kW Demand- Channel 41 | 41 | 6864 |  | 12576 | 12577 |  |  | R
| kW Demand- Channel 42 | 42 | 6865 |  | 12578 | 12579 |  |  | R
| kW Demand- Channel 43 | 43 | 6866 |  | 12580 | 12581 |  |  | R
| kW Demand- Channel 44 | 44 | 6867 |  | 12582 | 12583 |  |  | R
| kW Demand- Channel 45 | 45 | 6868 |  | 12584 | 12585 |  |  | R
| kW Demand- Channel 46 | 46 | 6869 |  | 12586 | 12587 |  |  | R
| kW Demand- Channel 47 | 47 | 6870 |  | 12588 | 12589 |  |  | R
| kW Demand- Channel 48 | 48 | 6871 |  | 12590 | 12591 |  |  | R
| kW Demand- Channel 49 | 49 | 6872 |  | 12592 | 12593 |  |  | R
| kW Demand- Channel 50 | 50 | 6873 |  | 12594 | 12595 |  |  | R
| kW Demand- Channel 51 | 51 | 6874 |  | 12596 | 12597 |  |  | R
| kW Demand- Channel 52 | 52 | 6875 |  | 12598 | 12599 |  |  | R
| kW Demand- Channel 53 | 53 | 6876 |  | 12600 | 12601 |  |  | R
| kW Demand- Channel 54 | 54 | 6877 |  | 12602 | 12603 |  |  | R
| kW Demand- Channel 55 | 55 | 6878 |  | 12604 | 12605 |  |  | R
| kW Demand- Channel 56 | 56 | 6879 |  | 12606 | 12607 |  |  | R
| kW Demand- Channel 57 | 57 | 6880 |  | 12608 | 12609 |  |  | R
| kW Demand- Channel 58 | 58 | 6881 |  | 12610 | 12611 |  |  | R
| kW Demand- Channel 59 | 59 | 6882 |  | 12612 | 12613 |  |  | R
| kW Demand- Channel 60 | 60 | 6883 |  | 12614 | 12615 |  |  | R
| kW Demand- Channel 61 | 61 | 6884 |  | 12616 | 12617 |  |  | R
| kW Demand- Channel 62 | 62 | 6885 |  | 12618 | 12619 |  |  | R
| kW Demand- Channel 63 | 63 | 6886 |  | 12620 | 12621 |  |  | R
| kW Demand- Channel 64 | 64 | 6887 |  | 12622 | 12623 |  |  | R
| kW Demand- Channel 65 | 65 | 6888 |  | 12624 | 12625 |  |  | R
| kW Demand- Channel 66 | 66 | 6889 |  | 12626 | 12627 |  |  | R
| kW Demand- Channel 67 | 67 | 6890 |  | 12628 | 12629 |  |  | R
| kW Demand- Channel 68 | 68 | 6891 |  | 12630 | 12631 |  |  | R
| kW Demand- Channel 69 | 69 | 6892 |  | 12632 | 12633 |  |  | R
| kW Demand- Channel 70 | 70 | 6893 |  | 12634 | 12635 |  |  | R
| kW Demand- Channel 71 | 71 | 6894 |  | 12636 | 12637 |  |  | R
| kW Demand- Channel 72 | 72 | 6895 |  | 12638 | 12639 |  |  | R
| kW Demand- Channel 73 | 73 | 6896 |  | 12640 | 12641 |  |  | R
| kW Demand- Channel 74 | 74 | 6897 |  | 12642 | 12643 |  |  | R
| kW Demand- Channel 75 | 75 | 6898 |  | 12644 | 12645 |  |  | R
| kW Demand- Channel 76 | 76 | 6899 |  | 12646 | 12647 |  |  | R
| kW Demand- Channel 77 | 77 | 6900 |  | 12648 | 12649 |  |  | R
| kW Demand- Channel 78 | 78 | 6901 |  | 12650 | 12651 |  |  | R
| kW Demand- Channel 79 | 79 | 6902 |  | 12652 | 12653 |  |  | R
| kW Demand- Channel 80 | 80 | 6903 |  | 12654 | 12655 |  |  | R
| kW Demand- Channel 81 | 81 | 6904 |  | 12656 | 12657 |  |  | R
| kW Demand- Channel 82 | 82 | 6905 |  | 12658 | 12659 |  |  | R
| kW Demand- Channel 83 | 83 | 6906 |  | 12660 | 12661 |  |  | R
| kW Demand- Channel 84 | 84 | 6907 |  | 12662 | 12663 |  |  | R
| kW Demand- Channel 85 | 85 | 6908 |  | 12664 | 12665 |  |  | R
| kW Demand- Channel 86 | 86 | 6909 |  | 12666 | 12667 |  |  | R
| kW Demand- Channel 87 | 87 | 6910 |  | 12668 | 12669 |  |  | R
| kW Demand- Channel 88 | 88 | 6911 |  | 12670 | 12671 |  |  | R
| kW Demand- Channel 89 | 89 | 6912 |  | 12672 | 12673 |  |  | R
| kW Demand- Channel 90 | 90 | 6913 |  | 12674 | 12675 |  |  | R
| kW Demand- Channel 91 | 91 | 6914 |  | 12676 | 12677 |  |  | R
| kW Demand- Channel 92 | 92 | 6915 |  | 12678 | 12679 |  |  | R
| kW Demand- Channel 93 | 93 | 6916 |  | 12680 | 12681 |  |  | R
| kW Demand- Channel 94 | 94 | 6917 |  | 12682 | 12683 |  |  | R
| kW Demand- Channel 95 | 95 | 6918 |  | 12684 | 12685 |  |  | R
| kW Demand- Channel 96 | 96 | 6919 |  | 12686 | 12687 |  |  | R
| Max Current Demand |  | 6920 | 7015 | 12688 | 12879 |  |  | R | NV
| Max Current Demand - Channel 1 | 1 | 6920 |  | 12688 | 12689 |  |  | R | NV
| Max Current Demand - Channel 2 | 2 | 6921 |  | 12690 | 12691 |  |  | R | NV
| Max Current Demand - Channel 3 | 3 | 6922 |  | 12692 | 12693 |  |  | R | NV
| Max Current Demand - Channel 4 | 4 | 6923 |  | 12694 | 12695 |  |  | R | NV
| Max Current Demand - Channel 5 | 5 | 6924 |  | 12696 | 12697 |  |  | R | NV
| Max Current Demand - Channel 6 | 6 | 6925 |  | 12698 | 12699 |  |  | R | NV
| Max Current Demand - Channel 7 | 7 | 6926 |  | 12700 | 12701 |  |  | R | NV
| Max Current Demand - Channel 8 | 8 | 6927 |  | 12702 | 12703 |  |  | R | NV
| Max Current Demand - Channel 9 | 9 | 6928 |  | 12704 | 12705 |  |  | R | NV
| Max Current Demand - Channel 10 | 10 | 6929 |  | 12706 | 12707 |  |  | R | NV
| Max Current Demand - Channel 11 | 11 | 6930 |  | 12708 | 12709 |  |  | R | NV
| Max Current Demand - Channel 12 | 12 | 6931 |  | 12710 | 12711 |  |  | R | NV
| Max Current Demand - Channel 13 | 13 | 6932 |  | 12712 | 12713 |  |  | R | NV
| Max Current Demand - Channel 14 | 14 | 6933 |  | 12714 | 12715 |  |  | R | NV
| Max Current Demand - Channel 15 | 15 | 6934 |  | 12716 | 12717 |  |  | R | NV
| Max Current Demand - Channel 16 | 16 | 6935 |  | 12718 | 12719 |  |  | R | NV
| Max Current Demand - Channel 17 | 17 | 6936 |  | 12720 | 12721 |  |  | R | NV
| Max Current Demand - Channel 18 | 18 | 6937 |  | 12722 | 12723 |  |  | R | NV
| Max Current Demand - Channel 19 | 19 | 6938 |  | 12724 | 12725 |  |  | R | NV
| Max Current Demand - Channel 20 | 20 | 6939 |  | 12726 | 12727 |  |  | R | NV
| Max Current Demand - Channel 21 | 21 | 6940 |  | 12728 | 12729 |  |  | R | NV
| Max Current Demand - Channel 22 | 22 | 6941 |  | 12730 | 12731 |  |  | R | NV
| Max Current Demand - Channel 23 | 23 | 6942 |  | 12732 | 12733 |  |  | R | NV
| Max Current Demand - Channel 24 | 24 | 6943 |  | 12734 | 12735 |  |  | R | NV
| Max Current Demand - Channel 25 | 25 | 6944 |  | 12736 | 12737 |  |  | R | NV
| Max Current Demand - Channel 26 | 26 | 6945 |  | 12738 | 12739 |  |  | R | NV
| Max Current Demand - Channel 27 | 27 | 6946 |  | 12740 | 12741 |  |  | R | NV
| Max Current Demand - Channel 28 | 28 | 6947 |  | 12742 | 12743 |  |  | R | NV
| Max Current Demand - Channel 29 | 29 | 6948 |  | 12744 | 12745 |  |  | R | NV
| Max Current Demand - Channel 30 | 30 | 6949 |  | 12746 | 12747 |  |  | R | NV
| Max Current Demand - Channel 31 | 31 | 6950 |  | 12748 | 12749 |  |  | R | NV
| Max Current Demand - Channel 32 | 32 | 6951 |  | 12750 | 12751 |  |  | R | NV
| Max Current Demand - Channel 33 | 33 | 6952 |  | 12752 | 12753 |  |  | R | NV
| Max Current Demand - Channel 34 | 34 | 6953 |  | 12754 | 12755 |  |  | R | NV
| Max Current Demand - Channel 35 | 35 | 6954 |  | 12756 | 12757 |  |  | R | NV
| Max Current Demand - Channel 36 | 36 | 6955 |  | 12758 | 12759 |  |  | R | NV
| Max Current Demand - Channel 37 | 37 | 6956 |  | 12760 | 12761 |  |  | R | NV
| Max Current Demand - Channel 38 | 38 | 6957 |  | 12762 | 12763 |  |  | R | NV
| Max Current Demand - Channel 39 | 39 | 6958 |  | 12764 | 12765 |  |  | R | NV
| Max Current Demand - Channel 40 | 40 | 6959 |  | 12766 | 12767 |  |  | R | NV
| Max Current Demand - Channel 41 | 41 | 6960 |  | 12768 | 12769 |  |  | R | NV
| Max Current Demand - Channel 42 | 42 | 6961 |  | 12770 | 12771 |  |  | R | NV
| Max Current Demand - Channel 43 | 43 | 6962 |  | 12772 | 12773 |  |  | R | NV
| Max Current Demand - Channel 44 | 44 | 6963 |  | 12774 | 12775 |  |  | R | NV
| Max Current Demand - Channel 45 | 45 | 6964 |  | 12776 | 12777 |  |  | R | NV
| Max Current Demand - Channel 46 | 46 | 6965 |  | 12778 | 12779 |  |  | R | NV
| Max Current Demand - Channel 47 | 47 | 6966 |  | 12780 | 12781 |  |  | R | NV
| Max Current Demand - Channel 48 | 48 | 6967 |  | 12782 | 12783 |  |  | R | NV
| Max Current Demand - Channel 49 | 49 | 6968 |  | 12784 | 12785 |  |  | R | NV
| Max Current Demand - Channel 50 | 50 | 6969 |  | 12786 | 12787 |  |  | R | NV
| Max Current Demand - Channel 51 | 51 | 6970 |  | 12788 | 12789 |  |  | R | NV
| Max Current Demand - Channel 52 | 52 | 6971 |  | 12790 | 12791 |  |  | R | NV
| Max Current Demand - Channel 53 | 53 | 6972 |  | 12792 | 12793 |  |  | R | NV
| Max Current Demand - Channel 54 | 54 | 6973 |  | 12794 | 12795 |  |  | R | NV
| Max Current Demand - Channel 55 | 55 | 6974 |  | 12796 | 12797 |  |  | R | NV
| Max Current Demand - Channel 56 | 56 | 6975 |  | 12798 | 12799 |  |  | R | NV
| Max Current Demand - Channel 57 | 57 | 6976 |  | 12800 | 12801 |  |  | R | NV
| Max Current Demand - Channel 58 | 58 | 6977 |  | 12802 | 12803 |  |  | R | NV
| Max Current Demand - Channel 59 | 59 | 6978 |  | 12804 | 12805 |  |  | R | NV
| Max Current Demand - Channel 60 | 60 | 6979 |  | 12806 | 12807 |  |  | R | NV
| Max Current Demand - Channel 61 | 61 | 6980 |  | 12808 | 12809 |  |  | R | NV
| Max Current Demand - Channel 62 | 62 | 6981 |  | 12810 | 12811 |  |  | R | NV
| Max Current Demand - Channel 63 | 63 | 6982 |  | 12812 | 12813 |  |  | R | NV
| Max Current Demand - Channel 64 | 64 | 6983 |  | 12814 | 12815 |  |  | R | NV
| Max Current Demand - Channel 65 | 65 | 6984 |  | 12816 | 12817 |  |  | R | NV
| Max Current Demand - Channel 66 | 66 | 6985 |  | 12818 | 12819 |  |  | R | NV
| Max Current Demand - Channel 67 | 67 | 6986 |  | 12820 | 12821 |  |  | R | NV
| Max Current Demand - Channel 68 | 68 | 6987 |  | 12822 | 12823 |  |  | R | NV
| Max Current Demand - Channel 69 | 69 | 6988 |  | 12824 | 12825 |  |  | R | NV
| Max Current Demand - Channel 70 | 70 | 6989 |  | 12826 | 12827 |  |  | R | NV
| Max Current Demand - Channel 71 | 71 | 6990 |  | 12828 | 12829 |  |  | R | NV
| Max Current Demand - Channel 72 | 72 | 6991 |  | 12830 | 12831 |  |  | R | NV
| Max Current Demand - Channel 73 | 73 | 6992 |  | 12832 | 12833 |  |  | R | NV
| Max Current Demand - Channel 74 | 74 | 6993 |  | 12834 | 12835 |  |  | R | NV
| Max Current Demand - Channel 75 | 75 | 6994 |  | 12836 | 12837 |  |  | R | NV
| Max Current Demand - Channel 76 | 76 | 6995 |  | 12838 | 12839 |  |  | R | NV
| Max Current Demand - Channel 77 | 77 | 6996 |  | 12840 | 12841 |  |  | R | NV
| Max Current Demand - Channel 78 | 78 | 6997 |  | 12842 | 12843 |  |  | R | NV
| Max Current Demand - Channel 79 | 79 | 6998 |  | 12844 | 12845 |  |  | R | NV
| Max Current Demand - Channel 80 | 80 | 6999 |  | 12846 | 12847 |  |  | R | NV
| Max Current Demand - Channel 81 | 81 | 7000 |  | 12848 | 12849 |  |  | R | NV
| Max Current Demand - Channel 82 | 82 | 7001 |  | 12850 | 12851 |  |  | R | NV
| Max Current Demand - Channel 83 | 83 | 7002 |  | 12852 | 12853 |  |  | R | NV
| Max Current Demand - Channel 84 | 84 | 7003 |  | 12854 | 12855 |  |  | R | NV
| Max Current Demand - Channel 85 | 85 | 7004 |  | 12856 | 12857 |  |  | R | NV
| Max Current Demand - Channel 86 | 86 | 7005 |  | 12858 | 12859 |  |  | R | NV
| Max Current Demand - Channel 87 | 87 | 7006 |  | 12860 | 12861 |  |  | R | NV
| Max Current Demand - Channel 88 | 88 | 7007 |  | 12862 | 12863 |  |  | R | NV
| Max Current Demand - Channel 89 | 89 | 7008 |  | 12864 | 12865 |  |  | R | NV
| Max Current Demand - Channel 90 | 90 | 7009 |  | 12866 | 12867 |  |  | R | NV
| Max Current Demand - Channel 91 | 91 | 7010 |  | 12868 | 12869 |  |  | R | NV
| Max Current Demand - Channel 92 | 92 | 7011 |  | 12870 | 12871 |  |  | R | NV
| Max Current Demand - Channel 93 | 93 | 7012 |  | 12872 | 12873 |  |  | R | NV
| Max Current Demand - Channel 94 | 94 | 7013 |  | 12874 | 12875 |  |  | R | NV
| Max Current Demand - Channel 95 | 95 | 7014 |  | 12876 | 12877 |  |  | R | NV
| Max Current Demand - Channel 96 | 96 | 7015 |  | 12878 | 12879 |  |  | R | NV
| Max kW Demand |  | 7016 | 7111 | 12880 | 13071 |  |  | R | NV
| Max kW Demand - Channel 1 | 1 | 7016 |  | 12880 | 12881 |  |  | R | NV
| Max kW Demand - Channel 2 | 2 | 7017 |  | 12882 | 12883 |  |  | R | NV
| Max kW Demand - Channel 3 | 3 | 7018 |  | 12884 | 12885 |  |  | R | NV
| Max kW Demand - Channel 4 | 4 | 7019 |  | 12886 | 12887 |  |  | R | NV
| Max kW Demand - Channel 5 | 5 | 7020 |  | 12888 | 12889 |  |  | R | NV
| Max kW Demand - Channel 6 | 6 | 7021 |  | 12890 | 12891 |  |  | R | NV
| Max kW Demand - Channel 7 | 7 | 7022 |  | 12892 | 12893 |  |  | R | NV
| Max kW Demand - Channel 8 | 8 | 7023 |  | 12894 | 12895 |  |  | R | NV
| Max kW Demand - Channel 9 | 9 | 7024 |  | 12896 | 12897 |  |  | R | NV
| Max kW Demand - Channel 10 | 10 | 7025 |  | 12898 | 12899 |  |  | R | NV
| Max kW Demand - Channel 11 | 11 | 7026 |  | 12900 | 12901 |  |  | R | NV
| Max kW Demand - Channel 12 | 12 | 7027 |  | 12902 | 12903 |  |  | R | NV
| Max kW Demand - Channel 13 | 13 | 7028 |  | 12904 | 12905 |  |  | R | NV
| Max kW Demand - Channel 14 | 14 | 7029 |  | 12906 | 12907 |  |  | R | NV
| Max kW Demand - Channel 15 | 15 | 7030 |  | 12908 | 12909 |  |  | R | NV
| Max kW Demand - Channel 16 | 16 | 7031 |  | 12910 | 12911 |  |  | R | NV
| Max kW Demand - Channel 17 | 17 | 7032 |  | 12912 | 12913 |  |  | R | NV
| Max kW Demand - Channel 18 | 18 | 7033 |  | 12914 | 12915 |  |  | R | NV
| Max kW Demand - Channel 19 | 19 | 7034 |  | 12916 | 12917 |  |  | R | NV
| Max kW Demand - Channel 20 | 20 | 7035 |  | 12918 | 12919 |  |  | R | NV
| Max kW Demand - Channel 21 | 21 | 7036 |  | 12920 | 12921 |  |  | R | NV
| Max kW Demand - Channel 22 | 22 | 7037 |  | 12922 | 12923 |  |  | R | NV
| Max kW Demand - Channel 23 | 23 | 7038 |  | 12924 | 12925 |  |  | R | NV
| Max kW Demand - Channel 24 | 24 | 7039 |  | 12926 | 12927 |  |  | R | NV
| Max kW Demand - Channel 25 | 25 | 7040 |  | 12928 | 12929 |  |  | R | NV
| Max kW Demand - Channel 26 | 26 | 7041 |  | 12930 | 12931 |  |  | R | NV
| Max kW Demand - Channel 27 | 27 | 7042 |  | 12932 | 12933 |  |  | R | NV
| Max kW Demand - Channel 28 | 28 | 7043 |  | 12934 | 12935 |  |  | R | NV
| Max kW Demand - Channel 29 | 29 | 7044 |  | 12936 | 12937 |  |  | R | NV
| Max kW Demand - Channel 30 | 30 | 7045 |  | 12938 | 12939 |  |  | R | NV
| Max kW Demand - Channel 31 | 31 | 7046 |  | 12940 | 12941 |  |  | R | NV
| Max kW Demand - Channel 32 | 32 | 7047 |  | 12942 | 12943 |  |  | R | NV
| Max kW Demand - Channel 33 | 33 | 7048 |  | 12944 | 12945 |  |  | R | NV
| Max kW Demand - Channel 34 | 34 | 7049 |  | 12946 | 12947 |  |  | R | NV
| Max kW Demand - Channel 35 | 35 | 7050 |  | 12948 | 12949 |  |  | R | NV
| Max kW Demand - Channel 36 | 36 | 7051 |  | 12950 | 12951 |  |  | R | NV
| Max kW Demand - Channel 37 | 37 | 7052 |  | 12952 | 12953 |  |  | R | NV
| Max kW Demand - Channel 38 | 38 | 7053 |  | 12954 | 12955 |  |  | R | NV
| Max kW Demand - Channel 39 | 39 | 7054 |  | 12956 | 12957 |  |  | R | NV
| Max kW Demand - Channel 40 | 40 | 7055 |  | 12958 | 12959 |  |  | R | NV
| Max kW Demand - Channel 41 | 41 | 7056 |  | 12960 | 12961 |  |  | R | NV
| Max kW Demand - Channel 42 | 42 | 7057 |  | 12962 | 12963 |  |  | R | NV
| Max kW Demand - Channel 43 | 43 | 7058 |  | 12964 | 12965 |  |  | R | NV
| Max kW Demand - Channel 44 | 44 | 7059 |  | 12966 | 12967 |  |  | R | NV
| Max kW Demand - Channel 45 | 45 | 7060 |  | 12968 | 12969 |  |  | R | NV
| Max kW Demand - Channel 46 | 46 | 7061 |  | 12970 | 12971 |  |  | R | NV
| Max kW Demand - Channel 47 | 47 | 7062 |  | 12972 | 12973 |  |  | R | NV
| Max kW Demand - Channel 48 | 48 | 7063 |  | 12974 | 12975 |  |  | R | NV
| Max kW Demand - Channel 49 | 49 | 7064 |  | 12976 | 12977 |  |  | R | NV
| Max kW Demand - Channel 50 | 50 | 7065 |  | 12978 | 12979 |  |  | R | NV
| Max kW Demand - Channel 51 | 51 | 7066 |  | 12980 | 12981 |  |  | R | NV
| Max kW Demand - Channel 52 | 52 | 7067 |  | 12982 | 12983 |  |  | R | NV
| Max kW Demand - Channel 53 | 53 | 7068 |  | 12984 | 12985 |  |  | R | NV
| Max kW Demand - Channel 54 | 54 | 7069 |  | 12986 | 12987 |  |  | R | NV
| Max kW Demand - Channel 55 | 55 | 7070 |  | 12988 | 12989 |  |  | R | NV
| Max kW Demand - Channel 56 | 56 | 7071 |  | 12990 | 12991 |  |  | R | NV
| Max kW Demand - Channel 57 | 57 | 7072 |  | 12992 | 12993 |  |  | R | NV
| Max kW Demand - Channel 58 | 58 | 7073 |  | 12994 | 12995 |  |  | R | NV
| Max kW Demand - Channel 59 | 59 | 7074 |  | 12996 | 12997 |  |  | R | NV
| Max kW Demand - Channel 60 | 60 | 7075 |  | 12998 | 12999 |  |  | R | NV
| Max kW Demand - Channel 61 | 61 | 7076 |  | 13000 | 13001 |  |  | R | NV
| Max kW Demand - Channel 62 | 62 | 7077 |  | 13002 | 13003 |  |  | R | NV
| Max kW Demand - Channel 63 | 63 | 7078 |  | 13004 | 13005 |  |  | R | NV
| Max kW Demand - Channel 64 | 64 | 7079 |  | 13006 | 13007 |  |  | R | NV
| Max kW Demand - Channel 65 | 65 | 7080 |  | 13008 | 13009 |  |  | R | NV
| Max kW Demand - Channel 66 | 66 | 7081 |  | 13010 | 13011 |  |  | R | NV
| Max kW Demand - Channel 67 | 67 | 7082 |  | 13012 | 13013 |  |  | R | NV
| Max kW Demand - Channel 68 | 68 | 7083 |  | 13014 | 13015 |  |  | R | NV
| Max kW Demand - Channel 69 | 69 | 7084 |  | 13016 | 13017 |  |  | R | NV
| Max kW Demand - Channel 70 | 70 | 7085 |  | 13018 | 13019 |  |  | R | NV
| Max kW Demand - Channel 71 | 71 | 7086 |  | 13020 | 13021 |  |  | R | NV
| Max kW Demand - Channel 72 | 72 | 7087 |  | 13022 | 13023 |  |  | R | NV
| Max kW Demand - Channel 73 | 73 | 7088 |  | 13024 | 13025 |  |  | R | NV
| Max kW Demand - Channel 74 | 74 | 7089 |  | 13026 | 13027 |  |  | R | NV
| Max kW Demand - Channel 75 | 75 | 7090 |  | 13028 | 13029 |  |  | R | NV
| Max kW Demand - Channel 76 | 76 | 7091 |  | 13030 | 13031 |  |  | R | NV
| Max kW Demand - Channel 77 | 77 | 7092 |  | 13032 | 13033 |  |  | R | NV
| Max kW Demand - Channel 78 | 78 | 7093 |  | 13034 | 13035 |  |  | R | NV
| Max kW Demand - Channel 79 | 79 | 7094 |  | 13036 | 13037 |  |  | R | NV
| Max kW Demand - Channel 80 | 80 | 7095 |  | 13038 | 13039 |  |  | R | NV
| Max kW Demand - Channel 81 | 81 | 7096 |  | 13040 | 13041 |  |  | R | NV
| Max kW Demand - Channel 82 | 82 | 7097 |  | 13042 | 13043 |  |  | R | NV
| Max kW Demand - Channel 83 | 83 | 7098 |  | 13044 | 13045 |  |  | R | NV
| Max kW Demand - Channel 84 | 84 | 7099 |  | 13046 | 13047 |  |  | R | NV
| Max kW Demand - Channel 85 | 85 | 7100 |  | 13048 | 13049 |  |  | R | NV
| Max kW Demand - Channel 86 | 86 | 7101 |  | 13050 | 13051 |  |  | R | NV
| Max kW Demand - Channel 87 | 87 | 7102 |  | 13052 | 13053 |  |  | R | NV
| Max kW Demand - Channel 88 | 88 | 7103 |  | 13054 | 13055 |  |  | R | NV
| Max kW Demand - Channel 89 | 89 | 7104 |  | 13056 | 13057 |  |  | R | NV
| Max kW Demand - Channel 90 | 90 | 7105 |  | 13058 | 13059 |  |  | R | NV
| Max kW Demand - Channel 91 | 91 | 7106 |  | 13060 | 13061 |  |  | R | NV
| Max kW Demand - Channel 92 | 92 | 7107 |  | 13062 | 13063 |  |  | R | NV
| Max kW Demand - Channel 93 | 93 | 7108 |  | 13064 | 13065 |  |  | R | NV
| Max kW Demand - Channel 94 | 94 | 7109 |  | 13066 | 13067 |  |  | R | NV
| Max kW Demand - Channel 95 | 95 | 7110 |  | 13068 | 13069 |  |  | R | NV
| Max kW Demand - Channel 96 | 96 | 7111 |  | 13070 | 13071 |  |  | R | NV
| KWH Snapshot |  | 7112 | 7303 | 13072 | 13263 |  |  | R |  |  |  | 32 bit unsigned integer
| KWH Snapshot - Channel 1 | 1 | 7112 | 7113 | 13072 | 13073 |  |  | R
| KWH Snapshot - Channel 2 | 2 | 7114 | 7115 | 13074 | 13075 |  |  | R
| KWH Snapshot - Channel 3 | 3 | 7116 | 7117 | 13076 | 13077 |  |  | R
| KWH Snapshot - Channel 4 | 4 | 7118 | 7119 | 13078 | 13079 |  |  | R
| KWH Snapshot - Channel 5 | 5 | 7120 | 7121 | 13080 | 13081 |  |  | R
| KWH Snapshot - Channel 6 | 6 | 7122 | 7123 | 13082 | 13083 |  |  | R
| KWH Snapshot - Channel 7 | 7 | 7124 | 7125 | 13084 | 13085 |  |  | R
| KWH Snapshot - Channel 8 | 8 | 7126 | 7127 | 13086 | 13087 |  |  | R
| KWH Snapshot - Channel 9 | 9 | 7128 | 7129 | 13088 | 13089 |  |  | R
| KWH Snapshot - Channel 10 | 10 | 7130 | 7131 | 13090 | 13091 |  |  | R
| KWH Snapshot - Channel 11 | 11 | 7132 | 7133 | 13092 | 13093 |  |  | R
| KWH Snapshot - Channel 12 | 12 | 7134 | 7135 | 13094 | 13095 |  |  | R
| KWH Snapshot - Channel 13 | 13 | 7136 | 7137 | 13096 | 13097 |  |  | R
| KWH Snapshot - Channel 14 | 14 | 7138 | 7139 | 13098 | 13099 |  |  | R
| KWH Snapshot - Channel 15 | 15 | 7140 | 7141 | 13100 | 13101 |  |  | R
| KWH Snapshot - Channel 16 | 16 | 7142 | 7143 | 13102 | 13103 |  |  | R
| KWH Snapshot - Channel 17 | 17 | 7144 | 7145 | 13104 | 13105 |  |  | R
| KWH Snapshot - Channel 18 | 18 | 7146 | 7147 | 13106 | 13107 |  |  | R
| KWH Snapshot - Channel 19 | 19 | 7148 | 7149 | 13108 | 13109 |  |  | R
| KWH Snapshot - Channel 20 | 20 | 7150 | 7151 | 13110 | 13111 |  |  | R
| KWH Snapshot - Channel 21 | 21 | 7152 | 7153 | 13112 | 13113 |  |  | R
| KWH Snapshot - Channel 22 | 22 | 7154 | 7155 | 13114 | 13115 |  |  | R
| KWH Snapshot - Channel 23 | 23 | 7156 | 7157 | 13116 | 13117 |  |  | R
| KWH Snapshot - Channel 24 | 24 | 7158 | 7159 | 13118 | 13119 |  |  | R
| KWH Snapshot - Channel 25 | 25 | 7160 | 7161 | 13120 | 13121 |  |  | R
| KWH Snapshot - Channel 26 | 26 | 7162 | 7163 | 13122 | 13123 |  |  | R
| KWH Snapshot - Channel 27 | 27 | 7164 | 7165 | 13124 | 13125 |  |  | R
| KWH Snapshot - Channel 28 | 28 | 7166 | 7167 | 13126 | 13127 |  |  | R
| KWH Snapshot - Channel 29 | 29 | 7168 | 7169 | 13128 | 13129 |  |  | R
| KWH Snapshot - Channel 30 | 30 | 7170 | 7171 | 13130 | 13131 |  |  | R
| KWH Snapshot - Channel 31 | 31 | 7172 | 7173 | 13132 | 13133 |  |  | R
| KWH Snapshot - Channel 32 | 32 | 7174 | 7175 | 13134 | 13135 |  |  | R
| KWH Snapshot - Channel 33 | 33 | 7176 | 7177 | 13136 | 13137 |  |  | R
| KWH Snapshot - Channel 34 | 34 | 7178 | 7179 | 13138 | 13139 |  |  | R
| KWH Snapshot - Channel 35 | 35 | 7180 | 7181 | 13140 | 13141 |  |  | R
| KWH Snapshot - Channel 36 | 36 | 7182 | 7183 | 13142 | 13143 |  |  | R
| KWH Snapshot - Channel 37 | 37 | 7184 | 7185 | 13144 | 13145 |  |  | R
| KWH Snapshot - Channel 38 | 38 | 7186 | 7187 | 13146 | 13147 |  |  | R
| KWH Snapshot - Channel 39 | 39 | 7188 | 7189 | 13148 | 13149 |  |  | R
| KWH Snapshot - Channel 40 | 40 | 7190 | 7191 | 13150 | 13151 |  |  | R
| KWH Snapshot - Channel 41 | 41 | 7192 | 7193 | 13152 | 13153 |  |  | R
| KWH Snapshot - Channel 42 | 42 | 7194 | 7195 | 13154 | 13155 |  |  | R
| KWH Snapshot - Channel 43 | 43 | 7196 | 7197 | 13156 | 13157 |  |  | R
| KWH Snapshot - Channel 44 | 44 | 7198 | 7199 | 13158 | 13159 |  |  | R
| KWH Snapshot - Channel 45 | 45 | 7200 | 7201 | 13160 | 13161 |  |  | R
| KWH Snapshot - Channel 46 | 46 | 7202 | 7203 | 13162 | 13163 |  |  | R
| KWH Snapshot - Channel 47 | 47 | 7204 | 7205 | 13164 | 13165 |  |  | R
| KWH Snapshot - Channel 48 | 48 | 7206 | 7207 | 13166 | 13167 |  |  | R
| KWH Snapshot - Channel 49 | 49 | 7208 | 7209 | 13168 | 13169 |  |  | R
| KWH Snapshot - Channel 50 | 50 | 7210 | 7211 | 13170 | 13171 |  |  | R
| KWH Snapshot - Channel 51 | 51 | 7212 | 7213 | 13172 | 13173 |  |  | R
| KWH Snapshot - Channel 52 | 52 | 7214 | 7215 | 13174 | 13175 |  |  | R
| KWH Snapshot - Channel 53 | 53 | 7216 | 7217 | 13176 | 13177 |  |  | R
| KWH Snapshot - Channel 54 | 54 | 7218 | 7219 | 13178 | 13179 |  |  | R
| KWH Snapshot - Channel 55 | 55 | 7220 | 7221 | 13180 | 13181 |  |  | R
| KWH Snapshot - Channel 56 | 56 | 7222 | 7223 | 13182 | 13183 |  |  | R
| KWH Snapshot - Channel 57 | 57 | 7224 | 7225 | 13184 | 13185 |  |  | R
| KWH Snapshot - Channel 58 | 58 | 7226 | 7227 | 13186 | 13187 |  |  | R
| KWH Snapshot - Channel 59 | 59 | 7228 | 7229 | 13188 | 13189 |  |  | R
| KWH Snapshot - Channel 60 | 60 | 7230 | 7231 | 13190 | 13191 |  |  | R
| KWH Snapshot - Channel 61 | 61 | 7232 | 7233 | 13192 | 13193 |  |  | R
| KWH Snapshot - Channel 62 | 62 | 7234 | 7235 | 13194 | 13195 |  |  | R
| KWH Snapshot - Channel 63 | 63 | 7236 | 7237 | 13196 | 13197 |  |  | R
| KWH Snapshot - Channel 64 | 64 | 7238 | 7239 | 13198 | 13199 |  |  | R
| KWH Snapshot - Channel 65 | 65 | 7240 | 7241 | 13200 | 13201 |  |  | R
| KWH Snapshot - Channel 66 | 66 | 7242 | 7243 | 13202 | 13203 |  |  | R
| KWH Snapshot - Channel 67 | 67 | 7244 | 7245 | 13204 | 13205 |  |  | R
| KWH Snapshot - Channel 68 | 68 | 7246 | 7247 | 13206 | 13207 |  |  | R
| KWH Snapshot - Channel 69 | 69 | 7248 | 7249 | 13208 | 13209 |  |  | R
| KWH Snapshot - Channel 70 | 70 | 7250 | 7251 | 13210 | 13211 |  |  | R
| KWH Snapshot - Channel 71 | 71 | 7252 | 7253 | 13212 | 13213 |  |  | R
| KWH Snapshot - Channel 72 | 72 | 7254 | 7255 | 13214 | 13215 |  |  | R
| KWH Snapshot - Channel 73 | 73 | 7256 | 7257 | 13216 | 13217 |  |  | R
| KWH Snapshot - Channel 74 | 74 | 7258 | 7259 | 13218 | 13219 |  |  | R
| KWH Snapshot - Channel 75 | 75 | 7260 | 7261 | 13220 | 13221 |  |  | R
| KWH Snapshot - Channel 76 | 76 | 7262 | 7263 | 13222 | 13223 |  |  | R
| KWH Snapshot - Channel 77 | 77 | 7264 | 7265 | 13224 | 13225 |  |  | R
| KWH Snapshot - Channel 78 | 78 | 7266 | 7267 | 13226 | 13227 |  |  | R
| KWH Snapshot - Channel 79 | 79 | 7268 | 7269 | 13228 | 13229 |  |  | R
| KWH Snapshot - Channel 80 | 80 | 7270 | 7271 | 13230 | 13231 |  |  | R
| KWH Snapshot - Channel 81 | 81 | 7272 | 7273 | 13232 | 13233 |  |  | R
| KWH Snapshot - Channel 82 | 82 | 7274 | 7275 | 13234 | 13235 |  |  | R
| KWH Snapshot - Channel 83 | 83 | 7276 | 7277 | 13236 | 13237 |  |  | R
| KWH Snapshot - Channel 84 | 84 | 7278 | 7279 | 13238 | 13239 |  |  | R
| KWH Snapshot - Channel 85 | 85 | 7280 | 7281 | 13240 | 13241 |  |  | R
| KWH Snapshot - Channel 86 | 86 | 7282 | 7283 | 13242 | 13243 |  |  | R
| KWH Snapshot - Channel 87 | 87 | 7284 | 7285 | 13244 | 13245 |  |  | R
| KWH Snapshot - Channel 88 | 88 | 7286 | 7287 | 13246 | 13247 |  |  | R
| KWH Snapshot - Channel 89 | 89 | 7288 | 7289 | 13248 | 13249 |  |  | R
| KWH Snapshot - Channel 90 | 90 | 7290 | 7291 | 13250 | 13251 |  |  | R
| KWH Snapshot - Channel 91 | 91 | 7292 | 7293 | 13252 | 13253 |  |  | R
| KWH Snapshot - Channel 92 | 92 | 7294 | 7295 | 13254 | 13255 |  |  | R
| KWH Snapshot - Channel 93 | 93 | 7296 | 7297 | 13256 | 13257 |  |  | R
| KWH Snapshot - Channel 94 | 94 | 7298 | 7299 | 13258 | 13259 |  |  | R
| KWH Snapshot - Channel 95 | 95 | 7300 | 7301 | 13260 | 13261 |  |  | R
| KWH Snapshot - Channel 96 | 96 | 7302 | 7303 | 13262 | 13263 |  |  | R
| Reserved for Creset Factor |  | 7303 | 7398 | 11920 | 12111 |  |  | R
| Crest Factor - Channel 1 | 1 | 7303 |  | 11920 | 11921 |  |  | R
| Crest Factor - Channel 2 | 2 | 7304 |  | 11922 | 11923 |  |  | R
| Crest Factor - Channel 3 | 3 | 7305 |  | 11924 | 11925 |  |  | R
| Crest Factor - Channel 4 | 4 | 7306 |  | 11926 | 11927 |  |  | R
| Crest Factor - Channel 5 | 5 | 7307 |  | 11928 | 11929 |  |  | R
| Crest Factor - Channel 6 | 6 | 7308 |  | 11930 | 11931 |  |  | R
| Crest Factor - Channel 7 | 7 | 7309 |  | 11932 | 11933 |  |  | R
| Crest Factor - Channel 8 | 8 | 7310 |  | 11934 | 11935 |  |  | R
| Crest Factor - Channel 9 | 9 | 7311 |  | 11936 | 11937 |  |  | R
| Crest Factor - Channel 10 | 10 | 7312 |  | 11938 | 11939 |  |  | R
| Crest Factor - Channel 11 | 11 | 7313 |  | 11940 | 11941 |  |  | R
| Crest Factor - Channel 12 | 12 | 7314 |  | 11942 | 11943 |  |  | R
| Crest Factor - Channel 13 | 13 | 7315 |  | 11944 | 11945 |  |  | R
| Crest Factor - Channel 14 | 14 | 7316 |  | 11946 | 11947 |  |  | R
| Crest Factor - Channel 15 | 15 | 7317 |  | 11948 | 11949 |  |  | R
| Crest Factor - Channel 16 | 16 | 7318 |  | 11950 | 11951 |  |  | R
| Crest Factor - Channel 17 | 17 | 7319 |  | 11952 | 11953 |  |  | R
| Crest Factor - Channel 18 | 18 | 7320 |  | 11954 | 11955 |  |  | R
| Crest Factor - Channel 19 | 19 | 7321 |  | 11956 | 11957 |  |  | R
| Crest Factor - Channel 20 | 20 | 7322 |  | 11958 | 11959 |  |  | R
| Crest Factor - Channel 21 | 21 | 7323 |  | 11960 | 11961 |  |  | R
| Crest Factor - Channel 22 | 22 | 7324 |  | 11962 | 11963 |  |  | R
| Crest Factor - Channel 23 | 23 | 7325 |  | 11964 | 11965 |  |  | R
| Crest Factor - Channel 24 | 24 | 7326 |  | 11966 | 11967 |  |  | R
| Crest Factor - Channel 25 | 25 | 7327 |  | 11968 | 11969 |  |  | R
| Crest Factor - Channel 26 | 26 | 7328 |  | 11970 | 11971 |  |  | R
| Crest Factor - Channel 27 | 27 | 7329 |  | 11972 | 11973 |  |  | R
| Crest Factor - Channel 28 | 28 | 7330 |  | 11974 | 11975 |  |  | R
| Crest Factor - Channel 29 | 29 | 7331 |  | 11976 | 11977 |  |  | R
| Crest Factor - Channel 30 | 30 | 7332 |  | 11978 | 11979 |  |  | R
| Crest Factor - Channel 31 | 31 | 7333 |  | 11980 | 11981 |  |  | R
| Crest Factor - Channel 32 | 32 | 7334 |  | 11982 | 11983 |  |  | R
| Crest Factor - Channel 33 | 33 | 7335 |  | 11984 | 11985 |  |  | R
| Crest Factor - Channel 34 | 34 | 7336 |  | 11986 | 11987 |  |  | R
| Crest Factor - Channel 35 | 35 | 7337 |  | 11988 | 11989 |  |  | R
| Crest Factor - Channel 36 | 36 | 7338 |  | 11990 | 11991 |  |  | R
| Crest Factor - Channel 37 | 37 | 7339 |  | 11992 | 11993 |  |  | R
| Crest Factor - Channel 38 | 38 | 7340 |  | 11994 | 11995 |  |  | R
| Crest Factor - Channel 39 | 39 | 7341 |  | 11996 | 11997 |  |  | R
| Crest Factor - Channel 40 | 40 | 7342 |  | 11998 | 11999 |  |  | R
| Crest Factor - Channel 41 | 41 | 7343 |  | 12000 | 12001 |  |  | R
| Crest Factor - Channel 42 | 42 | 7344 |  | 12002 | 12003 |  |  | R
| Crest Factor - Channel 43 | 43 | 7345 |  | 12004 | 12005 |  |  | R
| Crest Factor - Channel 44 | 44 | 7346 |  | 12006 | 12007 |  |  | R
| Crest Factor - Channel 45 | 45 | 7347 |  | 12008 | 12009 |  |  | R
| Crest Factor - Channel 46 | 46 | 7348 |  | 12010 | 12011 |  |  | R
| Crest Factor - Channel 47 | 47 | 7349 |  | 12012 | 12013 |  |  | R
| Crest Factor - Channel 48 | 48 | 7350 |  | 12014 | 12015 |  |  | R
| Crest Factor - Channel 49 | 49 | 7351 |  | 12016 | 12017 |  |  | R
| Crest Factor - Channel 50 | 50 | 7352 |  | 12018 | 12019 |  |  | R
| Crest Factor - Channel 51 | 51 | 7353 |  | 12020 | 12021 |  |  | R
| Crest Factor - Channel 52 | 52 | 7354 |  | 12022 | 12023 |  |  | R
| Crest Factor - Channel 53 | 53 | 7355 |  | 12024 | 12025 |  |  | R
| Crest Factor - Channel 54 | 54 | 7356 |  | 12026 | 12027 |  |  | R
| Crest Factor - Channel 55 | 55 | 7357 |  | 12028 | 12029 |  |  | R
| Crest Factor - Channel 56 | 56 | 7358 |  | 12030 | 12031 |  |  | R
| Crest Factor - Channel 57 | 57 | 7359 |  | 12032 | 12033 |  |  | R
| Crest Factor - Channel 58 | 58 | 7360 |  | 12034 | 12035 |  |  | R
| Crest Factor - Channel 59 | 59 | 7361 |  | 12036 | 12037 |  |  | R
| Crest Factor - Channel 60 | 60 | 7362 |  | 12038 | 12039 |  |  | R
| Crest Factor - Channel 61 | 61 | 7363 |  | 12040 | 12041 |  |  | R
| Crest Factor - Channel 62 | 62 | 7364 |  | 12042 | 12043 |  |  | R
| Crest Factor - Channel 63 | 63 | 7365 |  | 12044 | 12045 |  |  | R
| Crest Factor - Channel 64 | 64 | 7366 |  | 12046 | 12047 |  |  | R
| Crest Factor - Channel 65 | 65 | 7367 |  | 12048 | 12049 |  |  | R
| Crest Factor - Channel 66 | 66 | 7368 |  | 12050 | 12051 |  |  | R
| Crest Factor - Channel 67 | 67 | 7369 |  | 12052 | 12053 |  |  | R
| Crest Factor - Channel 68 | 68 | 7370 |  | 12054 | 12055 |  |  | R
| Crest Factor - Channel 69 | 69 | 7371 |  | 12056 | 12057 |  |  | R
| Crest Factor - Channel 70 | 70 | 7372 |  | 12058 | 12059 |  |  | R
| Crest Factor - Channel 71 | 71 | 7373 |  | 12060 | 12061 |  |  | R
| Crest Factor - Channel 72 | 72 | 7374 |  | 12062 | 12063 |  |  | R
| Crest Factor - Channel 73 | 73 | 7375 |  | 12064 | 12065 |  |  | R
| Crest Factor - Channel 74 | 74 | 7376 |  | 12066 | 12067 |  |  | R
| Crest Factor - Channel 75 | 75 | 7377 |  | 12068 | 12069 |  |  | R
| Crest Factor - Channel 76 | 76 | 7378 |  | 12070 | 12071 |  |  | R
| Crest Factor - Channel 77 | 77 | 7379 |  | 12072 | 12073 |  |  | R
| Crest Factor - Channel 78 | 78 | 7380 |  | 12074 | 12075 |  |  | R
| Crest Factor - Channel 79 | 79 | 7381 |  | 12076 | 12077 |  |  | R
| Crest Factor - Channel 80 | 80 | 7382 |  | 12078 | 12079 |  |  | R
| Crest Factor - Channel 81 | 81 | 7383 |  | 12080 | 12081 |  |  | R
| Crest Factor - Channel 82 | 82 | 7384 |  | 12082 | 12083 |  |  | R
| Crest Factor - Channel 83 | 83 | 7385 |  | 12084 | 12085 |  |  | R
| Crest Factor - Channel 84 | 84 | 7386 |  | 12086 | 12087 |  |  | R
| Crest Factor - Channel 85 | 85 | 7387 |  | 12088 | 12089 |  |  | R
| Crest Factor - Channel 86 | 86 | 7388 |  | 12090 | 12091 |  |  | R
| Crest Factor - Channel 87 | 87 | 7389 |  | 12092 | 12093 |  |  | R
| Crest Factor - Channel 88 | 88 | 7390 |  | 12094 | 12095 |  |  | R
| Crest Factor - Channel 89 | 89 | 7391 |  | 12096 | 12097 |  |  | R
| Crest Factor - Channel 90 | 90 | 7392 |  | 12098 | 12099 |  |  | R
| Crest Factor - Channel 91 | 91 | 7393 |  | 12100 | 12101 |  |  | R
| Crest Factor - Channel 92 | 92 | 7394 |  | 12102 | 12103 |  |  | R
| Crest Factor - Channel 93 | 93 | 7395 |  | 12104 | 12105 |  |  | R
| Crest Factor - Channel 94 | 94 | 7396 |  | 12106 | 12107 |  |  | R
| Crest Factor - Channel 95 | 95 | 7397 |  | 12108 | 12109 |  |  | R
| Crest Factor - Channel 96 | 96 | 7398 |  | 12110 | 12111 |  |  | R
| Reserved for Temperature |  | 7399 | 7494 | 12112 | 12303 |  |  | R
| Temperature - Channel 1 | 1 | 7399 |  | 12112 | 12113 |  |  | R
| Temperature - Channel 2 | 2 | 7400 |  | 12114 | 12115 |  |  | R
| Temperature - Channel 3 | 3 | 7401 |  | 12116 | 12117 |  |  | R
| Temperature - Channel 4 | 4 | 7402 |  | 12118 | 12119 |  |  | R
| Temperature - Channel 5 | 5 | 7403 |  | 12120 | 12121 |  |  | R
| Temperature - Channel 6 | 6 | 7404 |  | 12122 | 12123 |  |  | R
| Temperature - Channel 7 | 7 | 7405 |  | 12124 | 12125 |  |  | R
| Temperature - Channel 8 | 8 | 7406 |  | 12126 | 12127 |  |  | R
| Temperature - Channel 9 | 9 | 7407 |  | 12128 | 12129 |  |  | R
| Temperature - Channel 10 | 10 | 7408 |  | 12130 | 12131 |  |  | R
| Temperature - Channel 11 | 11 | 7409 |  | 12132 | 12133 |  |  | R
| Temperature - Channel 12 | 12 | 7410 |  | 12134 | 12135 |  |  | R
| Temperature - Channel 13 | 13 | 7411 |  | 12136 | 12137 |  |  | R
| Temperature - Channel 14 | 14 | 7412 |  | 12138 | 12139 |  |  | R
| Temperature - Channel 15 | 15 | 7413 |  | 12140 | 12141 |  |  | R
| Temperature - Channel 16 | 16 | 7414 |  | 12142 | 12143 |  |  | R
| Temperature - Channel 17 | 17 | 7415 |  | 12144 | 12145 |  |  | R
| Temperature - Channel 18 | 18 | 7416 |  | 12146 | 12147 |  |  | R
| Temperature - Channel 19 | 19 | 7417 |  | 12148 | 12149 |  |  | R
| Temperature - Channel 20 | 20 | 7418 |  | 12150 | 12151 |  |  | R
| Temperature - Channel 21 | 21 | 7419 |  | 12152 | 12153 |  |  | R
| Temperature - Channel 22 | 22 | 7420 |  | 12154 | 12155 |  |  | R
| Temperature - Channel 23 | 23 | 7421 |  | 12156 | 12157 |  |  | R
| Temperature - Channel 24 | 24 | 7422 |  | 12158 | 12159 |  |  | R
| Temperature - Channel 25 | 25 | 7423 |  | 12160 | 12161 |  |  | R
| Temperature - Channel 26 | 26 | 7424 |  | 12162 | 12163 |  |  | R
| Temperature - Channel 27 | 27 | 7425 |  | 12164 | 12165 |  |  | R
| Temperature - Channel 28 | 28 | 7426 |  | 12166 | 12167 |  |  | R
| Temperature - Channel 29 | 29 | 7427 |  | 12168 | 12169 |  |  | R
| Temperature - Channel 30 | 30 | 7428 |  | 12170 | 12171 |  |  | R
| Temperature - Channel 31 | 31 | 7429 |  | 12172 | 12173 |  |  | R
| Temperature - Channel 32 | 32 | 7430 |  | 12174 | 12175 |  |  | R
| Temperature - Channel 33 | 33 | 7431 |  | 12176 | 12177 |  |  | R
| Temperature - Channel 34 | 34 | 7432 |  | 12178 | 12179 |  |  | R
| Temperature - Channel 35 | 35 | 7433 |  | 12180 | 12181 |  |  | R
| Temperature - Channel 36 | 36 | 7434 |  | 12182 | 12183 |  |  | R
| Temperature - Channel 37 | 37 | 7435 |  | 12184 | 12185 |  |  | R
| Temperature - Channel 38 | 38 | 7436 |  | 12186 | 12187 |  |  | R
| Temperature - Channel 39 | 39 | 7437 |  | 12188 | 12189 |  |  | R
| Temperature - Channel 40 | 40 | 7438 |  | 12190 | 12191 |  |  | R
| Temperature - Channel 41 | 41 | 7439 |  | 12192 | 12193 |  |  | R
| Temperature - Channel 42 | 42 | 7440 |  | 12194 | 12195 |  |  | R
| Temperature - Channel 43 | 43 | 7441 |  | 12196 | 12197 |  |  | R
| Temperature - Channel 44 | 44 | 7442 |  | 12198 | 12199 |  |  | R
| Temperature - Channel 45 | 45 | 7443 |  | 12200 | 12201 |  |  | R
| Temperature - Channel 46 | 46 | 7444 |  | 12202 | 12203 |  |  | R
| Temperature - Channel 47 | 47 | 7445 |  | 12204 | 12205 |  |  | R
| Temperature - Channel 48 | 48 | 7446 |  | 12206 | 12207 |  |  | R
| Temperature - Channel 49 | 49 | 7447 |  | 12208 | 12209 |  |  | R
| Temperature - Channel 50 | 50 | 7448 |  | 12210 | 12211 |  |  | R
| Temperature - Channel 51 | 51 | 7449 |  | 12212 | 12213 |  |  | R
| Temperature - Channel 52 | 52 | 7450 |  | 12214 | 12215 |  |  | R
| Temperature - Channel 53 | 53 | 7451 |  | 12216 | 12217 |  |  | R
| Temperature - Channel 54 | 54 | 7452 |  | 12218 | 12219 |  |  | R
| Temperature - Channel 55 | 55 | 7453 |  | 12220 | 12221 |  |  | R
| Temperature - Channel 56 | 56 | 7454 |  | 12222 | 12223 |  |  | R
| Temperature - Channel 57 | 57 | 7455 |  | 12224 | 12225 |  |  | R
| Temperature - Channel 58 | 58 | 7456 |  | 12226 | 12227 |  |  | R
| Temperature - Channel 59 | 59 | 7457 |  | 12228 | 12229 |  |  | R
| Temperature - Channel 60 | 60 | 7458 |  | 12230 | 12231 |  |  | R
| Temperature - Channel 61 | 61 | 7459 |  | 12232 | 12233 |  |  | R
| Temperature - Channel 62 | 62 | 7460 |  | 12234 | 12235 |  |  | R
| Temperature - Channel 63 | 63 | 7461 |  | 12236 | 12237 |  |  | R
| Temperature - Channel 64 | 64 | 7462 |  | 12238 | 12239 |  |  | R
| Temperature - Channel 65 | 65 | 7463 |  | 12240 | 12241 |  |  | R
| Temperature - Channel 66 | 66 | 7464 |  | 12242 | 12243 |  |  | R
| Temperature - Channel 67 | 67 | 7465 |  | 12244 | 12245 |  |  | R
| Temperature - Channel 68 | 68 | 7466 |  | 12246 | 12247 |  |  | R
| Temperature - Channel 69 | 69 | 7467 |  | 12248 | 12249 |  |  | R
| Temperature - Channel 70 | 70 | 7468 |  | 12250 | 12251 |  |  | R
| Temperature - Channel 71 | 71 | 7469 |  | 12252 | 12253 |  |  | R
| Temperature - Channel 72 | 72 | 7470 |  | 12254 | 12255 |  |  | R
| Temperature - Channel 73 | 73 | 7471 |  | 12256 | 12257 |  |  | R
| Temperature - Channel 74 | 74 | 7472 |  | 12258 | 12259 |  |  | R
| Temperature - Channel 75 | 75 | 7473 |  | 12260 | 12261 |  |  | R
| Temperature - Channel 76 | 76 | 7474 |  | 12262 | 12263 |  |  | R
| Temperature - Channel 77 | 77 | 7475 |  | 12264 | 12265 |  |  | R
| Temperature - Channel 78 | 78 | 7476 |  | 12266 | 12267 |  |  | R
| Temperature - Channel 79 | 79 | 7477 |  | 12268 | 12269 |  |  | R
| Temperature - Channel 80 | 80 | 7478 |  | 12270 | 12271 |  |  | R
| Temperature - Channel 81 | 81 | 7479 |  | 12272 | 12273 |  |  | R
| Temperature - Channel 82 | 82 | 7480 |  | 12274 | 12275 |  |  | R
| Temperature - Channel 83 | 83 | 7481 |  | 12276 | 12277 |  |  | R
| Temperature - Channel 84 | 84 | 7482 |  | 12278 | 12279 |  |  | R
| Temperature - Channel 85 | 85 | 7483 |  | 12280 | 12281 |  |  | R
| Temperature - Channel 86 | 86 | 7484 |  | 12282 | 12283 |  |  | R
| Temperature - Channel 87 | 87 | 7485 |  | 12284 | 12285 |  |  | R
| Temperature - Channel 88 | 88 | 7486 |  | 12286 | 12287 |  |  | R
| Temperature - Channel 89 | 89 | 7487 |  | 12288 | 12289 |  |  | R
| Temperature - Channel 90 | 90 | 7488 |  | 12290 | 12291 |  |  | R
| Temperature - Channel 91 | 91 | 7489 |  | 12292 | 12293 |  |  | R
| Temperature - Channel 92 | 92 | 7490 |  | 12294 | 12295 |  |  | R
| Temperature - Channel 93 | 93 | 7491 |  | 12296 | 12297 |  |  | R
| Temperature - Channel 94 | 94 | 7492 |  | 12298 | 12299 |  |  | R
| Temperature - Channel 95 | 95 | 7493 |  | 12300 | 12301 |  |  | R
| Temperature - Channel 96 | 96 | 7494 |  | 12302 | 12303 |  |  | R
Reading by Circuit | Circuit #1 | 1 | 15000 | 15276 | 15300 | 15489 | [6 empty] | Add 500 for next Circuit
Circuit Configuration
| Circuit Name (32 Register) |  | 15000 | 15031
| # of Channels Assigned |  | 15032
| Assigned Channel |  | 15033 | 15035
| Channel 1 |  | 15033
| Channel 2 |  | 15034
| Channel 3 |  | 15035
| CT Size |  | 15036 | 15038
| CT Size - Assigned Channel 1 |  | 15036
| CT Size - Assigned Channel 2 |  | 15037
| CT Size - Assigned Channel 3 |  | 15038
| Breaker Size |  | 15039 | 15041
| Breaker Size - Assigned Channel 1 |  | 15039
| Breaker Size - Assigned Channel 2 |  | 15040
| Breaker Size - Assigned Channel 3 |  | 15041
| Voltage Phase |  | 15042 | 15044
| Voltage Phase - Assigned Channel 1 |  | 15042
| Voltage Phase - Assigned Channel 2 |  | 15043
| Voltage Phase - Assigned Channel 3 |  | 15044
| Reset/Command All Phases |  | 15045
| Reset/Command |  | 15046 | 15048
| Reset/Command - Assigned Channel 1 |  | 15046
| Reset/Command - Assigned Channel 2 |  | 15047
| Reset/Command - Assigned Channel 3 |  | 15048
| CT Type/Compensation |  | 15049 | 15051
| CT Type/Compensation - Assigned Channel 1 |  | 15049
| CT Type/Compensation - Assigned Channel 2 |  | 15050
| CT Type/Compensation - Assigned Channel 3 |  | 15051
Circuit #1 Total |  |  | 15100
| Energy Scale |  | 15100
| Power Scale |  | 15101
| Current Scale |  | 15102
| Voltage Scale |  | 15103
| Alarm Status - Latching |  | 15104
| Alarm Status - Non-Latching |  | 15105
| Frequency |  | 15106 |  | 15300 | 15301
| Voltages LN Average |  | 15107 |  | 15302 | 15303
| Voltage LL Average |  | 15108 |  | 15304 | 15305
| kWh |  | 15109 | 15110 | 15306 | 15307
| kVARh |  | 15111 | 15112 | 15308 | 15309
| kVAh |  | 15113 | 15114 | 15310 | 15311
| kW |  | 15114 |  | 15312 | 15313
| kVAR |  | 15115 |  | 15314 | 15315
| kVA |  | 15116 |  | 15316 | 15317
| Current |  | 15117 |  | 15318 | 15319
| Power Factor |  | 15118 |  | 15320 | 15321
| Current Angle |  | 15119 |  | 15322 | 15323
| Percent THD |  | 15120 |  | 15324 | 15325
| Max Current |  | 15121 |  | 15326 | 15327
| Max kW |  | 15122 |  | 15328 | 15329
| Current Demand |  | 15123 |  | 15330 | 15331
| kW Demand |  | 15124 |  | 15332 | 15333
| Max Current Demand |  | 15125 |  | 15334 | 15335
| Max kW Demand |  | 15126 |  | 15336 | 15337
| KWH Snapshot |  | 15127 | 15128 | 15338 | 15339
| Reserved for Creset Factor |  | 15128 |  | 15340 | 15341
| Reserved for Zero Current |  | 15129 |  | 15342 | 15343
| Reserved for Temperature |  | 15130 |  | 15344 | 15345
Circuit #1 Channel 1
| Energy Scale |  | 15150
| Power Scale |  | 15150
| Current Scale |  | 15151
| Voltage Scale |  | 15152
| Alarm Status - Latching |  | 15153
| Alarm Status - Non-Latching |  | 15154
| kWh |  | 15155 | 15156 | 15350 | 15351
| kVARh |  | 15157 | 15158 | 15352 | 15353
| kVAh |  | 15159 | 15160 | 15354 | 15355
| kW |  | 15160 |  | 15356 | 15357
| kVAR |  | 15161 |  | 15358 | 15359
| kVA |  | 15162 |  | 15360 | 15361
| Current |  | 15163 |  | 15362 | 15363
| Power Factor |  | 15164 |  | 15364 | 15365
| Current Angle |  | 15165 |  | 15366 | 15367
| Percent THD |  | 15166 |  | 15368 | 15369
| Max Current |  | 15167 |  | 15370 | 15371
| Max kW |  | 15168 |  | 15372 | 15373
| Current Demand |  | 15169 |  | 15374 | 15375
| kW Demand |  | 15170 |  | 15376 | 15377
| Max Current Demand |  | 15171 |  | 15378 | 15379
| Max kW Demand |  | 15172 |  | 15380 | 15381
| KWH Snapshot |  | 15173 | 15174 | 15382 | 15383
| Reserved for Creset Factor |  | 15174 |  | 15384 | 15385
| Reserved for Zero Current |  | 15175 |  | 15386 | 15387
| Reserved for Temperature |  | 15176 |  | 15388 | 15389
Circuit #1 Channel 2
| Energy Scale |  | 15200
| Power Scale |  | 15200
| Current Scale |  | 15201
| Voltage Scale |  | 15202
| Alarm Status - Latching |  | 15203
| Alarm Status - Non-Latching |  | 15204
| kWh |  | 15205 | 15206 | 15400 | 15401
| kVARh |  | 15207 | 15208 | 15402 | 15403
| kVAh |  | 15209 | 15210 | 15404 | 15405
| kW |  | 15210 |  | 15406 | 15407
| kVAR |  | 15211 |  | 15408 | 15409
| kVA |  | 15212 |  | 15410 | 15411
| Current |  | 15213 |  | 15412 | 15413
| Power Factor |  | 15214 |  | 15414 | 15415
| Current Angle |  | 15215 |  | 15416 | 15417
| Percent THD |  | 15216 |  | 15418 | 15419
| Max Current |  | 15217 |  | 15420 | 15421
| Max kW |  | 15218 |  | 15422 | 15423
| Current Demand |  | 15219 |  | 15424 | 15425
| kW Demand |  | 15220 |  | 15426 | 15427
| Max Current Demand |  | 15221 |  | 15428 | 15429
| Max kW Demand |  | 15222 |  | 15430 | 15431
| KWH Snapshot |  | 15223 | 15224 | 15432 | 15433
| Reserved for Creset Factor |  | 15224 |  | 15434 | 15435
| Reserved for Zero Current |  | 15225 |  | 15436 | 15437
| Reserved for Temperature |  | 15226 |  | 15438 | 15439
Circuit #1 Channel 3
| Energy Scale |  | 15250
| Power Scale |  | 15250
| Current Scale |  | 15251
| Voltage Scale |  | 15252
| Alarm Status - Latching |  | 15253
| Alarm Status - Non-Latching |  | 15254
| kWh |  | 15255 | 15256 | 15450 | 15451
| kVARh |  | 15257 | 15258 | 15452 | 15453
| kVAh |  | 15259 | 15260 | 15454 | 15455
| kW |  | 15260 |  | 15456 | 15457
| kVAR |  | 15261 |  | 15458 | 15459
| kVA |  | 15262 |  | 15460 | 15461
| Current |  | 15263 |  | 15462 | 15463
| Power Factor |  | 15264 |  | 15464 | 15465
| Current Angle |  | 15265 |  | 15466 | 15467
| Percent THD |  | 15266 |  | 15468 | 15469
| Max Current |  | 15267 |  | 15470 | 15471
| Max kW |  | 15268 |  | 15472 | 15473
| Current Demand |  | 15269 |  | 15474 | 15475
| kW Demand |  | 15270 |  | 15476 | 15477
| Max Current Demand |  | 15271 |  | 15478 | 15479
| Max kW Demand |  | 15272 |  | 15480 | 15481
| KWH Snapshot |  | 15273 | 15274 | 15482 | 15483
| Reserved for Creset Factor |  | 15274 |  | 15484 | 15485
| Reserved for Zero Current |  | 15275 |  | 15486 | 15487
| Reserved for Temperature |  | 15276 |  | 15488 | 15489
| Circuit #2 | 2 | 15500 | 15776 | 15800 | 15989
| Circuit #3 | 3 | 16000 | 16276 | 16300 | 16489
| Circuit #4 | 4 | 16500 | 16776 | 16800 | 16989
| Circuit #5 | 5 | 17000 | 17276 | 17300 | 17489
| Circuit #6 | 6 | 17500 | 17776 | 17800 | 17989
| Circuit #7 | 7 | 18000 | 18276 | 18300 | 18489
| Circuit #8 | 8 | 18500 | 18776 | 18800 | 18989
| Circuit #9 | 9 | 19000 | 19276 | 19300 | 19489
| Circuit #10 | 10 | 19500 | 19776 | 19800 | 19989
| Circuit #11 | 11 | 20000 | 20276 | 20300 | 20489
| Circuit #12 | 12 | 20500 | 20776 | 20800 | 20989
| Circuit #13 | 13 | 21000 | 21276 | 21300 | 21489
| Circuit #14 | 14 | 21500 | 21776 | 21800 | 21989
| Circuit #15 | 15 | 22000 | 22276 | 22300 | 22489
| Circuit #16 | 16 | 22500 | 22776 | 22800 | 22989
| Circuit #17 | 17 | 23000 | 23276 | 23300 | 23489
| Circuit #18 | 18 | 23500 | 23776 | 23800 | 23989
| Circuit #19 | 19 | 24000 | 24276 | 24300 | 24489
| Circuit #20 | 20 | 24500 | 24776 | 24800 | 24989
| Circuit #21 | 21 | 25000 | 25276 | 25300 | 25489
| Circuit #22 | 22 | 25500 | 25776 | 25800 | 25989
| Circuit #23 | 23 | 26000 | 26276 | 26300 | 26489
| Circuit #24 | 24 | 26500 | 26776 | 26800 | 26989
| Circuit #25 | 25 | 27000 | 27276 | 27300 | 27489
| Circuit #26 | 26 | 27500 | 27776 | 27800 | 27989
| Circuit #27 | 27 | 28000 | 28276 | 28300 | 28489
| Circuit #28 | 28 | 28500 | 28776 | 28800 | 28989
| Circuit #29 | 29 | 29000 | 29276 | 29300 | 29489
| Circuit #30 | 30 | 29500 | 29776 | 29800 | 29989
| Circuit #31 | 31 | 30000 | 30276 | 30300 | 30489
| Circuit #32 | 32 | 30500 | 30776 | 30800 | 30989
| Circuit #33 | 33 | 31000 | 31276 | 31300 | 31489
| Circuit #34 | 34 | 31500 | 31776 | 31800 | 31989
| Circuit #35 | 35 | 32000 | 32276 | 32300 | 32489
| Circuit #36 | 36 | 32500 | 32776 | 32800 | 32989
| Circuit #37 | 37 | 33000 | 33276 | 33300 | 33489
| Circuit #38 | 38 | 33500 | 33776 | 33800 | 33989
| Circuit #39 | 39 | 34000 | 34276 | 34300 | 34489
| Circuit #40 | 40 | 34500 | 34776 | 34800 | 34989
| Circuit #41 | 41 | 35000 | 35276 | 35300 | 35489
| Circuit #42 | 42 | 35500 | 35776 | 35800 | 35989
| Circuit #43 | 43 | 36000 | 36276 | 36300 | 36489
| Circuit #44 | 44 | 36500 | 36776 | 36800 | 36989
| Circuit #45 | 45 | 37000 | 37276 | 37300 | 37489
| Circuit #46 | 46 | 37500 | 37776 | 37800 | 37989
| Circuit #47 | 47 | 38000 | 38276 | 38300 | 38489
| Circuit #48 | 48 | 38500 | 38776 | 38800 | 38989
| Circuit #49 | 49 | 39000 | 39276 | 39300 | 39489
| Circuit #50 | 50 | 39500 | 39776 | 39800 | 39989
| Circuit #51 | 51 | 40000 | 40276 | 40300 | 40489
| Circuit #52 | 52 | 40500 | 40776 | 40800 | 40989
| Circuit #53 | 53 | 41000 | 41276 | 41300 | 41489
| Circuit #54 | 54 | 41500 | 41776 | 41800 | 41989
| Circuit #55 | 55 | 42000 | 42276 | 42300 | 42489
| Circuit #56 | 56 | 42500 | 42776 | 42800 | 42989
| Circuit #57 | 57 | 43000 | 43276 | 43300 | 43489
| Circuit #58 | 58 | 43500 | 43776 | 43800 | 43989
| Circuit #59 | 59 | 44000 | 44276 | 44300 | 44489
| Circuit #60 | 60 | 44500 | 44776 | 44800 | 44989
| Circuit #61 | 61 | 45000 | 45276 | 45300 | 45489
| Circuit #62 | 62 | 45500 | 45776 | 45800 | 45989
| Circuit #63 | 63 | 46000 | 46276 | 46300 | 46489
| Circuit #64 | 64 | 46500 | 46776 | 46800 | 46989
| Circuit #65 | 65 | 47000 | 47276 | 47300 | 47489
| Circuit #66 | 66 | 47500 | 47776 | 47800 | 47989
| Circuit #67 | 67 | 48000 | 48276 | 48300 | 48489
| Circuit #68 | 68 | 48500 | 48776 | 48800 | 48989
| Circuit #69 | 69 | 49000 | 49276 | 49300 | 49489
| Circuit #70 | 70 | 49500 | 49776 | 49800 | 49989
| Circuit #71 | 71 | 50000 | 50276 | 50300 | 50489
| Circuit #72 | 72 | 50500 | 50776 | 50800 | 50989
| Circuit #73 | 73 | 51000 | 51276 | 51300 | 51489
| Circuit #74 | 74 | 51500 | 51776 | 51800 | 51989
| Circuit #75 | 75 | 52000 | 52276 | 52300 | 52489
| Circuit #76 | 76 | 52500 | 52776 | 52800 | 52989
| Circuit #77 | 77 | 53000 | 53276 | 53300 | 53489
| Circuit #78 | 78 | 53500 | 53776 | 53800 | 53989
| Circuit #79 | 79 | 54000 | 54276 | 54300 | 54489
| Circuit #80 | 80 | 54500 | 54776 | 54800 | 54989
| Circuit #81 | 81 | 55000 | 55276 | 55300 | 55489
| Circuit #82 | 82 | 55500 | 55776 | 55800 | 55989
| Circuit #83 | 83 | 56000 | 56276 | 56300 | 56489
| Circuit #84 | 84 | 56500 | 56776 | 56800 | 56989
| Circuit #85 | 85 | 57000 | 57276 | 57300 | 57489
| Circuit #86 | 86 | 57500 | 57776 | 57800 | 57989
| Circuit #87 | 87 | 58000 | 58276 | 58300 | 58489
| Circuit #88 | 88 | 58500 | 58776 | 58800 | 58989
| Circuit #89 | 89 | 59000 | 59276 | 59300 | 59489
| Circuit #90 | 90 | 59500 | 59776 | 59800 | 59989
| Circuit #91 | 91 | 60000 | 60276 | 60300 | 60489
| Circuit #92 | 92 | 60500 | 60776 | 60800 | 60989
| Circuit #93 | 93 | 61000 | 61276 | 61300 | 61489
| Circuit #94 | 94 | 61500 | 61776 | 61800 | 61989
| Circuit #95 | 95 | 62000 | 62276 | 62300 | 62489
| Circuit #96 | 96 | 62500 | 62776 | 62800 | 62989

## Sheet1
Non-Latching Alarm Status
Global Reset
Branch Alarm Status
High High Latching Alarm Counter
High Latching Alarm Counter
Low Latching Alarm Counter
Low Low Latching Alarm Counter
Latching Alarm Off State Counter
Zero Current