## Summary
Pointmap Section | Start Register | End Register
Meter Information | 1 | 200
Meter Configuration | 201 | 600
Global Config | 601 | 700
Channel Config | 701 | 2000
Alarming | 2001 | 5000
Voltage Readings | 5001 | 7000
Reading by Type | 7001 | 15000
Reading by Circuit | 15001 | 63000
Reserved for Factory Info | 63001 | 65536

## Detailed
Section | Description | # of Regs | Register # | Comment
Info
| Serial Number | 2 | 1
| Bootloader Version | 1 | 3
| Firmware Version | 1 | 4
| Product ID | 1 | 5
| Power Up Counter | 1 | 6
| Device Health | 1 | 7
| Smart Port | 4 | 8
| MAC Address | 8 | 12
| Model Name | 32 | 20
| Brand Name | 16 | 52
68
Meter Configuration
| Panel Type | 2 | 201
| Demand # of Sub-Intervals | 1 | 203
| Demand Sub-Interval Length | 1 | 204
| Demand TimeStamp | 9 | 205
| Panel Locations | 128 | 214 | 2 - 128 Byte Strings
| RTC | 9 | 342
| Modbus Address | 1 | 351
| Baudrate | 2 | 352
| Parity | 1 | 354
| Stop Bits | 1 | 355
| Dip Switch Enabled | 1 | 356
| Dips Switch Value | 1 | 357
| Modbus TCP Port | 1 | 358
| IP Address | 2 | 359
| Gateway | 2 | 361
| SMTP | 2 | 363
| NTP | 2 | 365
| DNS1 | 2 | 367
| DNS2 | 2 | 369
371
Circuit Configuration
| Global CT Size | 1 | 601
| Global Breaker Size | 1 | 602
| Global Reset/Command | 1 | 603
604
604
| CT Size | 96 | 604
| Breaker Size | 96 | 700
| Voltage Phase | 96 | 796
| Circuit Assignment | 96 | 892
| CT Type/Compensation | 96 | 988 | Applies Compensation Model for Specific CT
| Reset/Command | 96 | 1084
1180
Alarming
| Voltage Presence | 102 | 2001 | 96 Channels + 6 Summary
| Over Voltage Alarm Status | 3 | 2001
| Under Voltage Alarm Status | 3
Voltage Readings
| Frequency | 1 | 5001
| Voltage LN | 4 | 5002
| Voltage LL | 4 | 5006
| Voltage Angle | 3 | 5010
| Voltage Scale | 1 | 5013
5014
| Frequency | 2 | 6001
| Voltage LN | 8 | 6003
| Voltage LL | 8 | 6011
| Voltage Angle | 6 | 6019
6025
Single Phase Reading by Type
| KWh | 192 | 7001
| KVARh | 192 | 7193
| KVAh | 192 | 7385
| KW | 96 | 7577
| KVAR | 96 | 7673
| KVA | 96 | 7769
| Current | 96 | 7865
| Power Factor | 96 | 7961
| Current Angle | 96 | 8057
| Percent THD | 96 | 8153
| KW Demand | 96 | 8249
| Current Demand | 96 | 8345
| Max KW Demand | 96 | 8441
| Max Current Demand | 96 | 8537
| Max KW | 96 | 8633
| Max Current | 96 | 8729
| KWH Snapshot | 192 | 8825
| Temperature | 96 | 9017
| Energy Scale | 96 | 9113
| Power Scale | 96 | 9209
| Current Scale | 96 | 9305
9401
| KWh | 192 | 10001
| KVARh | 192 | 10193
| KVAh | 192 | 10385
| KW | 192 | 10577
| KVAR | 192 | 10769
| KVA | 192 | 10961
| Current | 192 | 11153
| Power Factor | 192 | 11345
| Current Angle | 192 | 11537
| Percent THD | 192 | 11729
| KW Demand | 192 | 11921
| Current Demand | 192 | 12113
| Max KW Demand | 192 | 12305
| Max Current Demand | 192 | 12497
| Max KW | 192 | 12689
| Max Current | 192 | 12881
| KWH Snapshot | 192 | 13073
| Temperature | 192 | 13265
13457
Reading by Circuit (#1)
81
| # of Channels | 1 | 15001
| Assigned Channel | 3 | 15002
| CT Size | 3 | 15005
| Breaker Size | 3 | 15008
| Voltage Phase | 3 | 15011
| CT Compensation | 3 | 15014
| Reset/Command | 1 | 15017
| Voltage Presence | 3 | 15018
| KWh | 2 | 15101
| KVARh | 2 | 15103
| KVAh | 2 | 15105
| KW | 1 | 15107
| KVAR | 1 | 15108
| KVA | 1 | 15109
| Current | 1 | 15110
| Power Factor | 1 | 15111
| Current Angle | 1 | 15112
| Percent THD | 1 | 15113
| KW Demand | 1 | 15114
| Current Demand | 1 | 15115
| Max KW Demand | 1 | 15116
| Max Current Demand | 1 | 15117
| Max KW | 1 | 15118
| Max Current | 1 | 15119
| KWH Snapshot | 2 | 15120
| Temperature | 1 | 15122
| Energy Scale | 1 | 15123
| Power Scale | 1 | 15124
| Current Scale | 1 | 15125
| KWh | 2 | 15201
| KVARh | 2 | 15203
| KVAh | 2 | 15205
| KW | 2 | 15207
| KVAR | 2 | 15209
| KVA | 2 | 15211
| Current | 2 | 15213
| Power Factor | 2 | 15215
| Current Angle | 2 | 15217
| Percent THD | 2 | 15219
| KW Demand | 2 | 15221
| Current Demand | 2 | 15223
| Max KW Demand | 2 | 15225
| Max Current Demand | 2 | 15227
| Max KW | 2 | 15229
| Max Current | 2 | 15231
| KWH Snapshot | 2 | 15233
| Temperature | 2 | 15235
15237
Logical Circuits #2-96 |  | 7695 | 20501
Total Register Count |  | 14593

## Sheet1
|  |  | Modbus Register |  |  |  | Bacnet Object
|  |  | Integer |  | Float
| Description | Channel | Start (MSW) | End (LSW) | MSW | LSW | Object Type | Instance # | R/W | NV | Range | Default | Notes
Meter Information
| Serial Number |  | 1 | 2
| Bootloader Version |  | 3
| Firmware Version |  | 4
| Product ID |  | 5
| Power Up Counter |  | 6
| Device Health |  | 7
| Smart Port ID #1 |  | 8 | [9 empty] | 0 - Not Connected, 1 - CT Card,…
| Smart Port ID #2 |  | 9
| Smart Port ID #3 |  | 10
| Smart Port ID #4 |  | 11
| Smart Port #1 Serial Number |  | 12 | 13
| Smart Port #2 Serial Number |  | 14 | 15
| Smart Port #3 Serial Number |  | 16 | 17
| Smart Port #4 Serial Number |  | 18 | 19
| Smart Port #1 Firmware Version |  | 20
| Smart Port #2 Firmware Version |  | 21
| Smart Port #3 Firmware Version |  | 22
| Smart Port #4 Firmware Version |  | 23
| MAC Address (Bit 33-48) |  | 24
| MAC Address (Bit 17-32) |  | 25
| MAC Address (Bit 1-16) |  | 26
| Brand Name (16 Registers) |  | 27 | 42
| Model Name (32 Register) |  | 43 | 74
Meter Configuration
| Demand # of Sub-Intervals |  | 100
| Demand Sub-Interval Length |  | 101
| Demand Time Stamp (Year) |  | 102
| Demand Time Stamp (Month) |  | 103
| Demand Time Stamp (Day) |  | 104
| Demand Time Stamp (Weekday) |  | 105
| Demand Time Stamp (Hour) |  | 106
| Demand Time Stamp (Minute) |  | 107
| Demand Time Stamp (Second) |  | 108
| Configuration - Panel #1 |  | 109
| Configuration - Panel #2 |  | 110
| Location (64 Registers) |  | 212 | 275
| Location (64 Registers) |  | 276 | 339
| Real Time Clock (Year) |  | 340
| Real Time Clock (Month) |  | 341
| Real Time Clock (Day) |  | 342
| Real Time Clock (Weekday) |  | 343
| Real Time Clock (Hour) |  | 344
| Real Time Clock (Min) |  | 345
| Real Time Clock (Second) |  | 346
| Modbus Address |  | 347
| Modbus TCP Port |  | 348
| IP Address |  | 349 | 350
| Gateway |  | 351 | 352
| NTP |  | 353 | 354
| DNS 1 |  | 356 | 357
| DNS 2 |  | 358 | 359
| SMTP |  | 360 | 361
| Baudrate |  | 362 | 363
| Parity |  | 364
| Stop Bits |  | 365
| Dip Switch Enabled |  | 366
| Dips Switch Value |  | 367
Circuit Configuration
| CT Size |  | 400 | 495
| CT Size - Channel 1 | 1 | 400 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 2 | 2 | 401 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 3 | 3 | 402 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 4 | 4 | 403 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 5 | 5 | 404 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 6 | 6 | 405 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 7 | 7 | 406 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 8 | 8 | 407 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 9 | 9 | 408 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 10 | 10 | 409 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 11 | 11 | 410 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 12 | 12 | 411 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 13 | 13 | 412 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 14 | 14 | 413 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 15 | 15 | 414 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 16 | 16 | 415 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 17 | 17 | 416 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 18 | 18 | 417 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 19 | 19 | 418 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 20 | 20 | 419 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 21 | 21 | 420 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 22 | 22 | 421 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 23 | 23 | 422 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 24 | 24 | 423 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 25 | 25 | 424 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 26 | 26 | 425 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 27 | 27 | 426 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 28 | 28 | 427 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 29 | 29 | 428 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 30 | 30 | 429 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 31 | 31 | 430 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 32 | 32 | 431 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 33 | 33 | 432 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 34 | 34 | 433 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 35 | 35 | 434 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 36 | 36 | 435 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 37 | 37 | 436 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 38 | 38 | 437 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 39 | 39 | 438 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 40 | 40 | 439 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 41 | 41 | 440 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 42 | 42 | 441 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 43 | 43 | 442 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 44 | 44 | 443 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 45 | 45 | 444 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 46 | 46 | 445 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 47 | 47 | 446 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 48 | 48 | 447 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 49 | 49 | 448 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 50 | 50 | 449 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 51 | 51 | 450 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 52 | 52 | 451 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 53 | 53 | 452 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 54 | 54 | 453 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 55 | 55 | 454 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 56 | 56 | 455 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 57 | 57 | 456 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 58 | 58 | 457 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 59 | 59 | 458 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 60 | 60 | 459 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 61 | 61 | 460 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 62 | 62 | 461 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 63 | 63 | 462 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 64 | 64 | 463 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 65 | 65 | 464 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 66 | 66 | 465 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 67 | 67 | 466 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 68 | 68 | 467 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 69 | 69 | 468 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 70 | 70 | 469 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 71 | 71 | 470 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 72 | 72 | 471 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 73 | 73 | 472 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 74 | 74 | 473 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 75 | 75 | 474 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 76 | 76 | 475 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 77 | 77 | 476 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 78 | 78 | 477 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 79 | 79 | 478 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 80 | 80 | 479 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 81 | 81 | 480 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 82 | 82 | 481 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 83 | 83 | 482 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 84 | 84 | 483 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 85 | 85 | 484 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 86 | 86 | 485 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 87 | 87 | 486 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 88 | 88 | 487 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 89 | 89 | 488 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 90 | 90 | 489 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 91 | 91 | 490 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 92 | 92 | 491 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 93 | 93 | 492 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 94 | 94 | 493 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 95 | 95 | 494 | [5 empty] | R/W | NV | 0 - 32000
| CT Size - Channel 96 | 96 | 495 | [5 empty] | R/W | NV | 0 - 32000
| Global CT Size |  | 496
| Breaker Size |  | 500 | 595
| Breaker Size - Channel 1 | 1 | 500 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 2 | 2 | 501 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 3 | 3 | 502 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 4 | 4 | 503 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 5 | 5 | 504 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 6 | 6 | 505 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 7 | 7 | 506 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 8 | 8 | 507 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 9 | 9 | 508 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 10 | 10 | 509 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 11 | 11 | 510 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 12 | 12 | 511 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 13 | 13 | 512 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 14 | 14 | 513 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 15 | 15 | 514 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 16 | 16 | 515 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 17 | 17 | 516 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 18 | 18 | 517 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 19 | 19 | 518 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 20 | 20 | 519 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 21 | 21 | 520 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 22 | 22 | 521 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 23 | 23 | 522 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 24 | 24 | 523 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 25 | 25 | 524 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 26 | 26 | 525 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 27 | 27 | 526 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 28 | 28 | 527 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 29 | 29 | 528 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 30 | 30 | 529 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 31 | 31 | 530 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 32 | 32 | 531 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 33 | 33 | 532 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 34 | 34 | 533 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 35 | 35 | 534 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 36 | 36 | 535 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 37 | 37 | 536 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 38 | 38 | 537 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 39 | 39 | 538 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 40 | 40 | 539 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 41 | 41 | 540 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 42 | 42 | 541 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 43 | 43 | 542 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 44 | 44 | 543 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 45 | 45 | 544 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 46 | 46 | 545 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 47 | 47 | 546 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 48 | 48 | 547 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 49 | 49 | 548 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 50 | 50 | 549 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 51 | 51 | 550 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 52 | 52 | 551 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 53 | 53 | 552 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 54 | 54 | 553 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 55 | 55 | 554 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 56 | 56 | 555 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 57 | 57 | 556 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 58 | 58 | 557 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 59 | 59 | 558 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 60 | 60 | 559 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 61 | 61 | 560 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 62 | 62 | 561 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 63 | 63 | 562 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 64 | 64 | 563 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 65 | 65 | 564 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 66 | 66 | 565 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 67 | 67 | 566 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 68 | 68 | 567 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 69 | 69 | 568 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 70 | 70 | 569 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 71 | 71 | 570 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 72 | 72 | 571 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 73 | 73 | 572 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 74 | 74 | 573 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 75 | 75 | 574 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 76 | 76 | 575 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 77 | 77 | 576 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 78 | 78 | 577 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 79 | 79 | 578 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 80 | 80 | 579 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 81 | 81 | 580 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 82 | 82 | 581 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 83 | 83 | 582 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 84 | 84 | 583 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 85 | 85 | 584 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 86 | 86 | 585 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 87 | 87 | 586 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 88 | 88 | 587 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 89 | 89 | 588 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 90 | 90 | 589 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 91 | 91 | 590 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 92 | 92 | 591 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 93 | 93 | 592 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 94 | 94 | 593 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 95 | 95 | 594 | [5 empty] | R/W | NV | 0 - 32000
| Breaker Size - Channel 96 | 96 | 595 | [5 empty] | R/W | NV | 0 - 32000
| Global Breaker Size |  | 596
| Voltage Phase |  | 600 | 695
| Voltage Phase - Channel 1 | 1 | 600 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 2 | 2 | 601 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 3 | 3 | 602 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 4 | 4 | 603 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 5 | 5 | 604 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 6 | 6 | 605 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 7 | 7 | 606 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 8 | 8 | 607 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 9 | 9 | 608 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 10 | 10 | 609 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 11 | 11 | 610 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 12 | 12 | 611 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 13 | 13 | 612 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 14 | 14 | 613 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 15 | 15 | 614 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 16 | 16 | 615 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 17 | 17 | 616 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 18 | 18 | 617 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 19 | 19 | 618 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 20 | 20 | 619 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 21 | 21 | 620 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 22 | 22 | 621 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 23 | 23 | 622 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 24 | 24 | 623 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 25 | 25 | 624 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 26 | 26 | 625 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 27 | 27 | 626 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 28 | 28 | 627 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 29 | 29 | 628 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 30 | 30 | 629 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 31 | 31 | 630 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 32 | 32 | 631 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 33 | 33 | 632 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 34 | 34 | 633 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 35 | 35 | 634 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 36 | 36 | 635 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 37 | 37 | 636 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 38 | 38 | 637 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 39 | 39 | 638 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 40 | 40 | 639 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 41 | 41 | 640 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 42 | 42 | 641 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 43 | 43 | 642 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 44 | 44 | 643 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 45 | 45 | 644 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 46 | 46 | 645 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 47 | 47 | 646 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 48 | 48 | 647 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 49 | 49 | 648 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 50 | 50 | 649 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 51 | 51 | 650 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 52 | 52 | 651 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 53 | 53 | 652 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 54 | 54 | 653 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 55 | 55 | 654 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 56 | 56 | 655 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 57 | 57 | 656 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 58 | 58 | 657 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 59 | 59 | 658 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 60 | 60 | 659 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 61 | 61 | 660 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 62 | 62 | 661 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 63 | 63 | 662 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 64 | 64 | 663 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 65 | 65 | 664 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 66 | 66 | 665 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 67 | 67 | 666 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 68 | 68 | 667 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 69 | 69 | 668 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 70 | 70 | 669 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 71 | 71 | 670 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 72 | 72 | 671 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 73 | 73 | 672 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 74 | 74 | 673 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 75 | 75 | 674 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 76 | 76 | 675 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 77 | 77 | 676 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 78 | 78 | 677 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 79 | 79 | 678 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 80 | 80 | 679 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 81 | 81 | 680 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 82 | 82 | 681 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 83 | 83 | 682 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 84 | 84 | 683 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 85 | 85 | 684 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 86 | 86 | 685 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 87 | 87 | 686 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 88 | 88 | 687 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 89 | 89 | 688 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 90 | 90 | 689 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 91 | 91 | 690 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 92 | 92 | 691 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 93 | 93 | 692 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 94 | 94 | 693 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 95 | 95 | 694 | [5 empty] | R/W | NV | 0 - 32000
| Voltage Phase - Channel 96 | 96 | 695 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assignment |  | 700 | 795
| Circuit Assingment - Channel 1 | 1 | 700 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 2 | 2 | 701 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 3 | 3 | 702 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 4 | 4 | 703 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 5 | 5 | 704 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 6 | 6 | 705 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 7 | 7 | 706 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 8 | 8 | 707 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 9 | 9 | 708 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 10 | 10 | 709 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 11 | 11 | 710 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 12 | 12 | 711 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 13 | 13 | 712 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 14 | 14 | 713 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 15 | 15 | 714 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 16 | 16 | 715 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 17 | 17 | 716 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 18 | 18 | 717 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 19 | 19 | 718 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 20 | 20 | 719 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 21 | 21 | 720 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 22 | 22 | 721 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 23 | 23 | 722 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 24 | 24 | 723 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 25 | 25 | 724 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 26 | 26 | 725 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 27 | 27 | 726 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 28 | 28 | 727 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 29 | 29 | 728 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 30 | 30 | 729 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 31 | 31 | 730 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 32 | 32 | 731 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 33 | 33 | 732 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 34 | 34 | 733 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 35 | 35 | 734 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 36 | 36 | 735 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 37 | 37 | 736 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 38 | 38 | 737 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 39 | 39 | 738 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 40 | 40 | 739 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 41 | 41 | 740 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 42 | 42 | 741 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 43 | 43 | 742 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 44 | 44 | 743 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 45 | 45 | 744 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 46 | 46 | 745 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 47 | 47 | 746 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 48 | 48 | 747 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 49 | 49 | 748 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 50 | 50 | 749 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 51 | 51 | 750 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 52 | 52 | 751 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 53 | 53 | 752 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 54 | 54 | 753 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 55 | 55 | 754 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 56 | 56 | 755 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 57 | 57 | 756 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 58 | 58 | 757 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 59 | 59 | 758 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 60 | 60 | 759 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 61 | 61 | 760 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 62 | 62 | 761 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 63 | 63 | 762 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 64 | 64 | 763 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 65 | 65 | 764 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 66 | 66 | 765 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 67 | 67 | 766 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 68 | 68 | 767 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 69 | 69 | 768 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 70 | 70 | 769 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 71 | 71 | 770 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 72 | 72 | 771 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 73 | 73 | 772 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 74 | 74 | 773 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 75 | 75 | 774 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 76 | 76 | 775 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 77 | 77 | 776 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 78 | 78 | 777 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 79 | 79 | 778 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 80 | 80 | 779 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 81 | 81 | 780 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 82 | 82 | 781 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 83 | 83 | 782 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 84 | 84 | 783 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 85 | 85 | 784 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 86 | 86 | 785 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 87 | 87 | 786 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 88 | 88 | 787 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 89 | 89 | 788 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 90 | 90 | 789 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 91 | 91 | 790 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 92 | 92 | 791 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 93 | 93 | 792 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 94 | 94 | 793 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 95 | 95 | 794 | [5 empty] | R/W | NV | 0 - 32000
| Circuit Assingment - Channel 96 | 96 | 795 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command |  | 800 | 895
| Reset/Command - Channel 1 | 1 | 800 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 2 | 2 | 801 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 3 | 3 | 802 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 4 | 4 | 803 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 5 | 5 | 804 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 6 | 6 | 805 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 7 | 7 | 806 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 8 | 8 | 807 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 9 | 9 | 808 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 10 | 10 | 809 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 11 | 11 | 810 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 12 | 12 | 811 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 13 | 13 | 812 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 14 | 14 | 813 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 15 | 15 | 814 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 16 | 16 | 815 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 17 | 17 | 816 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 18 | 18 | 817 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 19 | 19 | 818 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 20 | 20 | 819 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 21 | 21 | 820 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 22 | 22 | 821 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 23 | 23 | 822 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 24 | 24 | 823 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 25 | 25 | 824 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 26 | 26 | 825 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 27 | 27 | 826 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 28 | 28 | 827 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 29 | 29 | 828 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 30 | 30 | 829 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 31 | 31 | 830 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 32 | 32 | 831 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 33 | 33 | 832 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 34 | 34 | 833 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 35 | 35 | 834 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 36 | 36 | 835 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 37 | 37 | 836 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 38 | 38 | 837 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 39 | 39 | 838 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 40 | 40 | 839 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 41 | 41 | 840 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 42 | 42 | 841 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 43 | 43 | 842 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 44 | 44 | 843 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 45 | 45 | 844 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 46 | 46 | 845 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 47 | 47 | 846 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 48 | 48 | 847 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 49 | 49 | 848 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 50 | 50 | 849 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 51 | 51 | 850 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 52 | 52 | 851 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 53 | 53 | 852 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 54 | 54 | 853 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 55 | 55 | 854 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 56 | 56 | 855 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 57 | 57 | 856 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 58 | 58 | 857 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 59 | 59 | 858 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 60 | 60 | 859 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 61 | 61 | 860 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 62 | 62 | 861 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 63 | 63 | 862 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 64 | 64 | 863 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 65 | 65 | 864 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 66 | 66 | 865 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 67 | 67 | 866 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 68 | 68 | 867 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 69 | 69 | 868 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 70 | 70 | 869 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 71 | 71 | 870 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 72 | 72 | 871 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 73 | 73 | 872 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 74 | 74 | 873 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 75 | 75 | 874 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 76 | 76 | 875 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 77 | 77 | 876 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 78 | 78 | 877 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 79 | 79 | 878 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 80 | 80 | 879 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 81 | 81 | 880 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 82 | 82 | 881 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 83 | 83 | 882 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 84 | 84 | 883 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 85 | 85 | 884 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 86 | 86 | 885 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 87 | 87 | 886 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 88 | 88 | 887 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 89 | 89 | 888 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 90 | 90 | 889 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 91 | 91 | 890 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 92 | 92 | 891 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 93 | 93 | 892 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 94 | 94 | 893 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 95 | 95 | 894 | [5 empty] | R/W | NV | 0 - 32000
| Reset/Command - Channel 96 | 96 | 895 | [5 empty] | R/W | NV | 0 - 32000
| Global Reset/Command |  | 896
| CT Type/Compensation |  | 900 | 995
| CT Type/Compensation - Channel 1 | 1 | 900 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 2 | 2 | 901 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 3 | 3 | 902 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 4 | 4 | 903 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 5 | 5 | 904 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 6 | 6 | 905 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 7 | 7 | 906 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 8 | 8 | 907 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 9 | 9 | 908 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 10 | 10 | 909 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 11 | 11 | 910 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 12 | 12 | 911 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 13 | 13 | 912 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 14 | 14 | 913 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 15 | 15 | 914 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 16 | 16 | 915 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 17 | 17 | 916 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 18 | 18 | 917 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 19 | 19 | 918 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 20 | 20 | 919 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 21 | 21 | 920 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 22 | 22 | 921 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 23 | 23 | 922 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 24 | 24 | 923 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 25 | 25 | 924 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 26 | 26 | 925 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 27 | 27 | 926 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 28 | 28 | 927 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 29 | 29 | 928 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 30 | 30 | 929 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 31 | 31 | 930 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 32 | 32 | 931 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 33 | 33 | 932 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 34 | 34 | 933 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 35 | 35 | 934 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 36 | 36 | 935 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 37 | 37 | 936 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 38 | 38 | 937 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 39 | 39 | 938 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 40 | 40 | 939 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 41 | 41 | 940 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 42 | 42 | 941 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 43 | 43 | 942 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 44 | 44 | 943 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 45 | 45 | 944 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 46 | 46 | 945 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 47 | 47 | 946 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 48 | 48 | 947 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 49 | 49 | 948 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 50 | 50 | 949 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 51 | 51 | 950 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 52 | 52 | 951 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 53 | 53 | 952 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 54 | 54 | 953 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 55 | 55 | 954 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 56 | 56 | 955 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 57 | 57 | 956 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 58 | 58 | 957 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 59 | 59 | 958 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 60 | 60 | 959 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 61 | 61 | 960 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 62 | 62 | 961 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 63 | 63 | 962 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 64 | 64 | 963 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 65 | 65 | 964 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 66 | 66 | 965 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 67 | 67 | 966 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 68 | 68 | 967 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 69 | 69 | 968 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 70 | 70 | 969 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 71 | 71 | 970 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 72 | 72 | 971 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 73 | 73 | 972 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 74 | 74 | 973 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 75 | 75 | 974 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 76 | 76 | 975 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 77 | 77 | 976 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 78 | 78 | 977 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 79 | 79 | 978 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 80 | 80 | 979 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 81 | 81 | 980 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 82 | 82 | 981 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 83 | 83 | 982 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 84 | 84 | 983 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 85 | 85 | 984 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 86 | 86 | 985 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 87 | 87 | 986 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 88 | 88 | 987 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 89 | 89 | 988 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 90 | 90 | 989 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 91 | 91 | 990 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 92 | 92 | 991 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 93 | 93 | 992 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 94 | 94 | 993 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 95 | 95 | 994 | [5 empty] | R/W | NV | 0 - 32000
| CT Type/Compensation - Channel 96 | 96 | 995 | [5 empty] | R/W | NV | 0 - 32000
| Global CT Type/Compensation |  | 996
Alarming |  |  | 1000 | 2999
Configuration
Alarm Status
Voltage Presense
Zero Current
Aux
| Aux Panel #1 |  | 3000
| Energy Scale |  | 3000
| Power Scale |  | 3001
| Current Scale |  | 3002
| kWh |  | 3003 | 3004 | 3100 | 3101
| kVARh |  | 3005 | 3006 | 3102 | 3103
| kVAh |  | 3007 | 3008 | 3104 | 3105
| kW |  | 3008 |  | 3106 | 3107
| kVAR |  | 3009 |  | 3108 | 3109
| kVA |  | 3010 |  | 3110 | 3111
| Current |  | 3011 |  | 3112 | 3113
| Power Factor |  | 3012 |  | 3114 | 3115
| Current Angle |  | 3013 |  | 3116 | 3117
| Percent THD |  | 3014 |  | 3118 | 3119
| Max Current |  | 3015 |  | 3120 | 3121
| Max kW |  | 3016 |  | 3122 | 3123
| Current Demand |  | 3017 |  | 3124 | 3125
| kW Demand |  | 3018 |  | 3126 | 3127
| Max Current Demand |  | 3019 |  | 3128 | 3129
| Max kW Demand |  | 3020 |  | 3130 | 3131
| KWH Snapshot |  | 3021 | 3022 | 3132 | 3133
Aux #2
Aux #3
Aux #4
Voltage Readings
| Voltage Scale |  | 4000
| Frequency |  | 4001 |  | 4100 | 4101
| Voltage LN Average |  | 4002 |  | 4102 | 4103
| Voltage LL Average |  | 4003 |  | 4104 | 4105
| Voltage LN |  | 4004 | 4006 | 4106 | 4109
| Voltage L1 |  | 4004 |  | 4106 | 4107
| Voltage L2 |  | 4005 |  | 4107 | 4108
| Voltage L3 |  | 4006 |  | 4108 | 4109
| Voltage LL |  | 4007 | 4009 | 4110 | 4113
| Voltage L1 - L2 |  | 4007 |  | 4110 | 4111
| Voltage L2 - L3 |  | 4008 |  | 4111 | 4112
| Voltage L3 - L1 |  | 4009 |  | 4112 | 4113
| Voltage Angle |  | 4010 | 4012 | 4114 | 4117
| Voltage Angle L1 |  | 4010 |  | 4114 | 4115 | [6 empty] | Always Read 0
| Voltage Angle L2 |  | 4011 |  | 4115 | 4116
| Voltage Angle L3 |  | 4012 |  | 4116 | 4117
| Percent THD |  | 4013 | 4015 | 4118 | 4121
| Percent THD - L1 |  | 4013 |  | 4118 | 4119 | [6 empty] | Always Reads 0
| Percent THD - L2 |  | 4014 |  | 4119 | 4120
| Percent THD - L3 |  | 4015 |  | 4120 | 4121
Dynamic Smart Port
| Smart Port #1 |  | 4200 | 4399
| Smart Port #2 |  | 4400 | 4599
| Smart Port #3 |  | 4600 | 4799
| Smart Port #4 |  | 4800 | 4999
Single Phase Reading by Type
| Energy Scale |  | 5000 | 5095 |  |  |  |  | R
| Energy Scale - Channel 1 | 1 | 5000 | [5 empty] | R
| Energy Scale - Channel 2 | 2 | 5001 | [5 empty] | R
| Energy Scale - Channel 3 | 3 | 5002 | [5 empty] | R
| Energy Scale - Channel 4 | 4 | 5003 | [5 empty] | R
| Energy Scale - Channel 5 | 5 | 5004 | [5 empty] | R
| Energy Scale - Channel 6 | 6 | 5005 | [5 empty] | R
| Energy Scale - Channel 7 | 7 | 5006 | [5 empty] | R
| Energy Scale - Channel 8 | 8 | 5007 | [5 empty] | R
| Energy Scale - Channel 9 | 9 | 5008 | [5 empty] | R
| Energy Scale - Channel 10 | 10 | 5009 | [5 empty] | R
| Energy Scale - Channel 11 | 11 | 5010 | [5 empty] | R
| Energy Scale - Channel 12 | 12 | 5011 | [5 empty] | R
| Energy Scale - Channel 13 | 13 | 5012 | [5 empty] | R
| Energy Scale - Channel 14 | 14 | 5013 | [5 empty] | R
| Energy Scale - Channel 15 | 15 | 5014 | [5 empty] | R
| Energy Scale - Channel 16 | 16 | 5015 | [5 empty] | R
| Energy Scale - Channel 17 | 17 | 5016 | [5 empty] | R
| Energy Scale - Channel 18 | 18 | 5017 | [5 empty] | R
| Energy Scale - Channel 19 | 19 | 5018 | [5 empty] | R
| Energy Scale - Channel 20 | 20 | 5019 | [5 empty] | R
| Energy Scale - Channel 21 | 21 | 5020 | [5 empty] | R
| Energy Scale - Channel 22 | 22 | 5021 | [5 empty] | R
| Energy Scale - Channel 23 | 23 | 5022 | [5 empty] | R
| Energy Scale - Channel 24 | 24 | 5023 | [5 empty] | R
| Energy Scale - Channel 25 | 25 | 5024 | [5 empty] | R
| Energy Scale - Channel 26 | 26 | 5025 | [5 empty] | R
| Energy Scale - Channel 27 | 27 | 5026 | [5 empty] | R
| Energy Scale - Channel 28 | 28 | 5027 | [5 empty] | R
| Energy Scale - Channel 29 | 29 | 5028 | [5 empty] | R
| Energy Scale - Channel 30 | 30 | 5029 | [5 empty] | R
| Energy Scale - Channel 31 | 31 | 5030 | [5 empty] | R
| Energy Scale - Channel 32 | 32 | 5031 | [5 empty] | R
| Energy Scale - Channel 33 | 33 | 5032 | [5 empty] | R
| Energy Scale - Channel 34 | 34 | 5033 | [5 empty] | R
| Energy Scale - Channel 35 | 35 | 5034 | [5 empty] | R
| Energy Scale - Channel 36 | 36 | 5035 | [5 empty] | R
| Energy Scale - Channel 37 | 37 | 5036 | [5 empty] | R
| Energy Scale - Channel 38 | 38 | 5037 | [5 empty] | R
| Energy Scale - Channel 39 | 39 | 5038 | [5 empty] | R
| Energy Scale - Channel 40 | 40 | 5039 | [5 empty] | R
| Energy Scale - Channel 41 | 41 | 5040 | [5 empty] | R
| Energy Scale - Channel 42 | 42 | 5041 | [5 empty] | R
| Energy Scale - Channel 43 | 43 | 5042 | [5 empty] | R
| Energy Scale - Channel 44 | 44 | 5043 | [5 empty] | R
| Energy Scale - Channel 45 | 45 | 5044 | [5 empty] | R
| Energy Scale - Channel 46 | 46 | 5045 | [5 empty] | R
| Energy Scale - Channel 47 | 47 | 5046 | [5 empty] | R
| Energy Scale - Channel 48 | 48 | 5047 | [5 empty] | R
| Energy Scale - Channel 49 | 49 | 5048 | [5 empty] | R
| Energy Scale - Channel 50 | 50 | 5049 | [5 empty] | R
| Energy Scale - Channel 51 | 51 | 5050 | [5 empty] | R
| Energy Scale - Channel 52 | 52 | 5051 | [5 empty] | R
| Energy Scale - Channel 53 | 53 | 5052 | [5 empty] | R
| Energy Scale - Channel 54 | 54 | 5053 | [5 empty] | R
| Energy Scale - Channel 55 | 55 | 5054 | [5 empty] | R
| Energy Scale - Channel 56 | 56 | 5055 | [5 empty] | R
| Energy Scale - Channel 57 | 57 | 5056 | [5 empty] | R
| Energy Scale - Channel 58 | 58 | 5057 | [5 empty] | R
| Energy Scale - Channel 59 | 59 | 5058 | [5 empty] | R
| Energy Scale - Channel 60 | 60 | 5059 | [5 empty] | R
| Energy Scale - Channel 61 | 61 | 5060 | [5 empty] | R
| Energy Scale - Channel 62 | 62 | 5061 | [5 empty] | R
| Energy Scale - Channel 63 | 63 | 5062 | [5 empty] | R
| Energy Scale - Channel 64 | 64 | 5063 | [5 empty] | R
| Energy Scale - Channel 65 | 65 | 5064 | [5 empty] | R
| Energy Scale - Channel 66 | 66 | 5065 | [5 empty] | R
| Energy Scale - Channel 67 | 67 | 5066 | [5 empty] | R
| Energy Scale - Channel 68 | 68 | 5067 | [5 empty] | R
| Energy Scale - Channel 69 | 69 | 5068 | [5 empty] | R
| Energy Scale - Channel 70 | 70 | 5069 | [5 empty] | R
| Energy Scale - Channel 71 | 71 | 5070 | [5 empty] | R
| Energy Scale - Channel 72 | 72 | 5071 | [5 empty] | R
| Energy Scale - Channel 73 | 73 | 5072 | [5 empty] | R
| Energy Scale - Channel 74 | 74 | 5073 | [5 empty] | R
| Energy Scale - Channel 75 | 75 | 5074 | [5 empty] | R
| Energy Scale - Channel 76 | 76 | 5075 | [5 empty] | R
| Energy Scale - Channel 77 | 77 | 5076 | [5 empty] | R
| Energy Scale - Channel 78 | 78 | 5077 | [5 empty] | R
| Energy Scale - Channel 79 | 79 | 5078 | [5 empty] | R
| Energy Scale - Channel 80 | 80 | 5079 | [5 empty] | R
| Energy Scale - Channel 81 | 81 | 5080 | [5 empty] | R
| Energy Scale - Channel 82 | 82 | 5081 | [5 empty] | R
| Energy Scale - Channel 83 | 83 | 5082 | [5 empty] | R
| Energy Scale - Channel 84 | 84 | 5083 | [5 empty] | R
| Energy Scale - Channel 85 | 85 | 5084 | [5 empty] | R
| Energy Scale - Channel 86 | 86 | 5085 | [5 empty] | R
| Energy Scale - Channel 87 | 87 | 5086 | [5 empty] | R
| Energy Scale - Channel 88 | 88 | 5087 | [5 empty] | R
| Energy Scale - Channel 89 | 89 | 5088 | [5 empty] | R
| Energy Scale - Channel 90 | 90 | 5089 | [5 empty] | R
| Energy Scale - Channel 91 | 91 | 5090 | [5 empty] | R
| Energy Scale - Channel 92 | 92 | 5091 | [5 empty] | R
| Energy Scale - Channel 93 | 93 | 5092 | [5 empty] | R
| Energy Scale - Channel 94 | 94 | 5093 | [5 empty] | R
| Energy Scale - Channel 95 | 95 | 5094 | [5 empty] | R
| Energy Scale - Channel 96 | 96 | 5095 | [5 empty] | R
| Power Scale |  | 5096 | 5191 |  |  |  |  | R
| Power Scale - Channel 1 | 1 | 5096 | [5 empty] | R
| Power Scale - Channel 2 | 2 | 5097 | [5 empty] | R
| Power Scale - Channel 3 | 3 | 5098 | [5 empty] | R
| Power Scale - Channel 4 | 4 | 5099 | [5 empty] | R
| Power Scale - Channel 5 | 5 | 5100 | [5 empty] | R
| Power Scale - Channel 6 | 6 | 5101 | [5 empty] | R
| Power Scale - Channel 7 | 7 | 5102 | [5 empty] | R
| Power Scale - Channel 8 | 8 | 5103 | [5 empty] | R
| Power Scale - Channel 9 | 9 | 5104 | [5 empty] | R
| Power Scale - Channel 10 | 10 | 5105 | [5 empty] | R
| Power Scale - Channel 11 | 11 | 5106 | [5 empty] | R
| Power Scale - Channel 12 | 12 | 5107 | [5 empty] | R
| Power Scale - Channel 13 | 13 | 5108 | [5 empty] | R
| Power Scale - Channel 14 | 14 | 5109 | [5 empty] | R
| Power Scale - Channel 15 | 15 | 5110 | [5 empty] | R
| Power Scale - Channel 16 | 16 | 5111 | [5 empty] | R
| Power Scale - Channel 17 | 17 | 5112 | [5 empty] | R
| Power Scale - Channel 18 | 18 | 5113 | [5 empty] | R
| Power Scale - Channel 19 | 19 | 5114 | [5 empty] | R
| Power Scale - Channel 20 | 20 | 5115 | [5 empty] | R
| Power Scale - Channel 21 | 21 | 5116 | [5 empty] | R
| Power Scale - Channel 22 | 22 | 5117 | [5 empty] | R
| Power Scale - Channel 23 | 23 | 5118 | [5 empty] | R
| Power Scale - Channel 24 | 24 | 5119 | [5 empty] | R
| Power Scale - Channel 25 | 25 | 5120 | [5 empty] | R
| Power Scale - Channel 26 | 26 | 5121 | [5 empty] | R
| Power Scale - Channel 27 | 27 | 5122 | [5 empty] | R
| Power Scale - Channel 28 | 28 | 5123 | [5 empty] | R
| Power Scale - Channel 29 | 29 | 5124 | [5 empty] | R
| Power Scale - Channel 30 | 30 | 5125 | [5 empty] | R
| Power Scale - Channel 31 | 31 | 5126 | [5 empty] | R
| Power Scale - Channel 32 | 32 | 5127 | [5 empty] | R
| Power Scale - Channel 33 | 33 | 5128 | [5 empty] | R
| Power Scale - Channel 34 | 34 | 5129 | [5 empty] | R
| Power Scale - Channel 35 | 35 | 5130 | [5 empty] | R
| Power Scale - Channel 36 | 36 | 5131 | [5 empty] | R
| Power Scale - Channel 37 | 37 | 5132 | [5 empty] | R
| Power Scale - Channel 38 | 38 | 5133 | [5 empty] | R
| Power Scale - Channel 39 | 39 | 5134 | [5 empty] | R
| Power Scale - Channel 40 | 40 | 5135 | [5 empty] | R
| Power Scale - Channel 41 | 41 | 5136 | [5 empty] | R
| Power Scale - Channel 42 | 42 | 5137 | [5 empty] | R
| Power Scale - Channel 43 | 43 | 5138 | [5 empty] | R
| Power Scale - Channel 44 | 44 | 5139 | [5 empty] | R
| Power Scale - Channel 45 | 45 | 5140 | [5 empty] | R
| Power Scale - Channel 46 | 46 | 5141 | [5 empty] | R
| Power Scale - Channel 47 | 47 | 5142 | [5 empty] | R
| Power Scale - Channel 48 | 48 | 5143 | [5 empty] | R
| Power Scale - Channel 49 | 49 | 5144 | [5 empty] | R
| Power Scale - Channel 50 | 50 | 5145 | [5 empty] | R
| Power Scale - Channel 51 | 51 | 5146 | [5 empty] | R
| Power Scale - Channel 52 | 52 | 5147 | [5 empty] | R
| Power Scale - Channel 53 | 53 | 5148 | [5 empty] | R
| Power Scale - Channel 54 | 54 | 5149 | [5 empty] | R
| Power Scale - Channel 55 | 55 | 5150 | [5 empty] | R
| Power Scale - Channel 56 | 56 | 5151 | [5 empty] | R
| Power Scale - Channel 57 | 57 | 5152 | [5 empty] | R
| Power Scale - Channel 58 | 58 | 5153 | [5 empty] | R
| Power Scale - Channel 59 | 59 | 5154 | [5 empty] | R
| Power Scale - Channel 60 | 60 | 5155 | [5 empty] | R
| Power Scale - Channel 61 | 61 | 5156 | [5 empty] | R
| Power Scale - Channel 62 | 62 | 5157 | [5 empty] | R
| Power Scale - Channel 63 | 63 | 5158 | [5 empty] | R
| Power Scale - Channel 64 | 64 | 5159 | [5 empty] | R
| Power Scale - Channel 65 | 65 | 5160 | [5 empty] | R
| Power Scale - Channel 66 | 66 | 5161 | [5 empty] | R
| Power Scale - Channel 67 | 67 | 5162 | [5 empty] | R
| Power Scale - Channel 68 | 68 | 5163 | [5 empty] | R
| Power Scale - Channel 69 | 69 | 5164 | [5 empty] | R
| Power Scale - Channel 70 | 70 | 5165 | [5 empty] | R
| Power Scale - Channel 71 | 71 | 5166 | [5 empty] | R
| Power Scale - Channel 72 | 72 | 5167 | [5 empty] | R
| Power Scale - Channel 73 | 73 | 5168 | [5 empty] | R
| Power Scale - Channel 74 | 74 | 5169 | [5 empty] | R
| Power Scale - Channel 75 | 75 | 5170 | [5 empty] | R
| Power Scale - Channel 76 | 76 | 5171 | [5 empty] | R
| Power Scale - Channel 77 | 77 | 5172 | [5 empty] | R
| Power Scale - Channel 78 | 78 | 5173 | [5 empty] | R
| Power Scale - Channel 79 | 79 | 5174 | [5 empty] | R
| Power Scale - Channel 80 | 80 | 5175 | [5 empty] | R
| Power Scale - Channel 81 | 81 | 5176 | [5 empty] | R
| Power Scale - Channel 82 | 82 | 5177 | [5 empty] | R
| Power Scale - Channel 83 | 83 | 5178 | [5 empty] | R
| Power Scale - Channel 84 | 84 | 5179 | [5 empty] | R
| Power Scale - Channel 85 | 85 | 5180 | [5 empty] | R
| Power Scale - Channel 86 | 86 | 5181 | [5 empty] | R
| Power Scale - Channel 87 | 87 | 5182 | [5 empty] | R
| Power Scale - Channel 88 | 88 | 5183 | [5 empty] | R
| Power Scale - Channel 89 | 89 | 5184 | [5 empty] | R
| Power Scale - Channel 90 | 90 | 5185 | [5 empty] | R
| Power Scale - Channel 91 | 91 | 5186 | [5 empty] | R
| Power Scale - Channel 92 | 92 | 5187 | [5 empty] | R
| Power Scale - Channel 93 | 93 | 5188 | [5 empty] | R
| Power Scale - Channel 94 | 94 | 5189 | [5 empty] | R
| Power Scale - Channel 95 | 95 | 5190 | [5 empty] | R
| Power Scale - Channel 96 | 96 | 5191 | [5 empty] | R
| Current Scale |  | 5192 | 5287 |  |  |  |  | R
| Current Scale - Channel 1 | 1 | 5192 | [5 empty] | R
| Current Scale - Channel 2 | 2 | 5193 | [5 empty] | R
| Current Scale - Channel 3 | 3 | 5194 | [5 empty] | R
| Current Scale - Channel 4 | 4 | 5195 | [5 empty] | R
| Current Scale - Channel 5 | 5 | 5196 | [5 empty] | R
| Current Scale - Channel 6 | 6 | 5197 | [5 empty] | R
| Current Scale - Channel 7 | 7 | 5198 | [5 empty] | R
| Current Scale - Channel 8 | 8 | 5199 | [5 empty] | R
| Current Scale - Channel 9 | 9 | 5200 | [5 empty] | R
| Current Scale - Channel 10 | 10 | 5201 | [5 empty] | R
| Current Scale - Channel 11 | 11 | 5202 | [5 empty] | R
| Current Scale - Channel 12 | 12 | 5203 | [5 empty] | R
| Current Scale - Channel 13 | 13 | 5204 | [5 empty] | R
| Current Scale - Channel 14 | 14 | 5205 | [5 empty] | R
| Current Scale - Channel 15 | 15 | 5206 | [5 empty] | R
| Current Scale - Channel 16 | 16 | 5207 | [5 empty] | R
| Current Scale - Channel 17 | 17 | 5208 | [5 empty] | R
| Current Scale - Channel 18 | 18 | 5209 | [5 empty] | R
| Current Scale - Channel 19 | 19 | 5210 | [5 empty] | R
| Current Scale - Channel 20 | 20 | 5211 | [5 empty] | R
| Current Scale - Channel 21 | 21 | 5212 | [5 empty] | R
| Current Scale - Channel 22 | 22 | 5213 | [5 empty] | R
| Current Scale - Channel 23 | 23 | 5214 | [5 empty] | R
| Current Scale - Channel 24 | 24 | 5215 | [5 empty] | R
| Current Scale - Channel 25 | 25 | 5216 | [5 empty] | R
| Current Scale - Channel 26 | 26 | 5217 | [5 empty] | R
| Current Scale - Channel 27 | 27 | 5218 | [5 empty] | R
| Current Scale - Channel 28 | 28 | 5219 | [5 empty] | R
| Current Scale - Channel 29 | 29 | 5220 | [5 empty] | R
| Current Scale - Channel 30 | 30 | 5221 | [5 empty] | R
| Current Scale - Channel 31 | 31 | 5222 | [5 empty] | R
| Current Scale - Channel 32 | 32 | 5223 | [5 empty] | R
| Current Scale - Channel 33 | 33 | 5224 | [5 empty] | R
| Current Scale - Channel 34 | 34 | 5225 | [5 empty] | R
| Current Scale - Channel 35 | 35 | 5226 | [5 empty] | R
| Current Scale - Channel 36 | 36 | 5227 | [5 empty] | R
| Current Scale - Channel 37 | 37 | 5228 | [5 empty] | R
| Current Scale - Channel 38 | 38 | 5229 | [5 empty] | R
| Current Scale - Channel 39 | 39 | 5230 | [5 empty] | R
| Current Scale - Channel 40 | 40 | 5231 | [5 empty] | R
| Current Scale - Channel 41 | 41 | 5232 | [5 empty] | R
| Current Scale - Channel 42 | 42 | 5233 | [5 empty] | R
| Current Scale - Channel 43 | 43 | 5234 | [5 empty] | R
| Current Scale - Channel 44 | 44 | 5235 | [5 empty] | R
| Current Scale - Channel 45 | 45 | 5236 | [5 empty] | R
| Current Scale - Channel 46 | 46 | 5237 | [5 empty] | R
| Current Scale - Channel 47 | 47 | 5238 | [5 empty] | R
| Current Scale - Channel 48 | 48 | 5239 | [5 empty] | R
| Current Scale - Channel 49 | 49 | 5240 | [5 empty] | R
| Current Scale - Channel 50 | 50 | 5241 | [5 empty] | R
| Current Scale - Channel 51 | 51 | 5242 | [5 empty] | R
| Current Scale - Channel 52 | 52 | 5243 | [5 empty] | R
| Current Scale - Channel 53 | 53 | 5244 | [5 empty] | R
| Current Scale - Channel 54 | 54 | 5245 | [5 empty] | R
| Current Scale - Channel 55 | 55 | 5246 | [5 empty] | R
| Current Scale - Channel 56 | 56 | 5247 | [5 empty] | R
| Current Scale - Channel 57 | 57 | 5248 | [5 empty] | R
| Current Scale - Channel 58 | 58 | 5249 | [5 empty] | R
| Current Scale - Channel 59 | 59 | 5250 | [5 empty] | R
| Current Scale - Channel 60 | 60 | 5251 | [5 empty] | R
| Current Scale - Channel 61 | 61 | 5252 | [5 empty] | R
| Current Scale - Channel 62 | 62 | 5253 | [5 empty] | R
| Current Scale - Channel 63 | 63 | 5254 | [5 empty] | R
| Current Scale - Channel 64 | 64 | 5255 | [5 empty] | R
| Current Scale - Channel 65 | 65 | 5256 | [5 empty] | R
| Current Scale - Channel 66 | 66 | 5257 | [5 empty] | R
| Current Scale - Channel 67 | 67 | 5258 | [5 empty] | R
| Current Scale - Channel 68 | 68 | 5259 | [5 empty] | R
| Current Scale - Channel 69 | 69 | 5260 | [5 empty] | R
| Current Scale - Channel 70 | 70 | 5261 | [5 empty] | R
| Current Scale - Channel 71 | 71 | 5262 | [5 empty] | R
| Current Scale - Channel 72 | 72 | 5263 | [5 empty] | R
| Current Scale - Channel 73 | 73 | 5264 | [5 empty] | R
| Current Scale - Channel 74 | 74 | 5265 | [5 empty] | R
| Current Scale - Channel 75 | 75 | 5266 | [5 empty] | R
| Current Scale - Channel 76 | 76 | 5267 | [5 empty] | R
| Current Scale - Channel 77 | 77 | 5268 | [5 empty] | R
| Current Scale - Channel 78 | 78 | 5269 | [5 empty] | R
| Current Scale - Channel 79 | 79 | 5270 | [5 empty] | R
| Current Scale - Channel 80 | 80 | 5271 | [5 empty] | R
| Current Scale - Channel 81 | 81 | 5272 | [5 empty] | R
| Current Scale - Channel 82 | 82 | 5273 | [5 empty] | R
| Current Scale - Channel 83 | 83 | 5274 | [5 empty] | R
| Current Scale - Channel 84 | 84 | 5275 | [5 empty] | R
| Current Scale - Channel 85 | 85 | 5276 | [5 empty] | R
| Current Scale - Channel 86 | 86 | 5277 | [5 empty] | R
| Current Scale - Channel 87 | 87 | 5278 | [5 empty] | R
| Current Scale - Channel 88 | 88 | 5279 | [5 empty] | R
| Current Scale - Channel 89 | 89 | 5280 | [5 empty] | R
| Current Scale - Channel 90 | 90 | 5281 | [5 empty] | R
| Current Scale - Channel 91 | 91 | 5282 | [5 empty] | R
| Current Scale - Channel 92 | 92 | 5283 | [5 empty] | R
| Current Scale - Channel 93 | 93 | 5284 | [5 empty] | R
| Current Scale - Channel 94 | 94 | 5285 | [5 empty] | R
| Current Scale - Channel 95 | 95 | 5286 | [5 empty] | R
| Current Scale - Channel 96 | 96 | 5287 | [5 empty] | R
| kWh |  | 5288 | 5479 | 10000 | 10191 |  |  | R | NV |  |  | 32 bit unsigned integer
| kWh - Channel 1 | 1 | 5288 | 5289 | 10000 | 10001 |  |  | R | NV
| kWh - Channel 2 | 2 | 5290 | 5291 | 10002 | 10003 |  |  | R | NV
| kWh - Channel 3 | 3 | 5292 | 5293 | 10004 | 10005 |  |  | R | NV
| kWh - Channel 4 | 4 | 5294 | 5295 | 10006 | 10007 |  |  | R | NV
| kWh - Channel 5 | 5 | 5296 | 5297 | 10008 | 10009 |  |  | R | NV
| kWh - Channel 6 | 6 | 5298 | 5299 | 10010 | 10011 |  |  | R | NV
| kWh - Channel 7 | 7 | 5300 | 5301 | 10012 | 10013 |  |  | R | NV
| kWh - Channel 8 | 8 | 5302 | 5303 | 10014 | 10015 |  |  | R | NV
| kWh - Channel 9 | 9 | 5304 | 5305 | 10016 | 10017 |  |  | R | NV
| kWh - Channel 10 | 10 | 5306 | 5307 | 10018 | 10019 |  |  | R | NV
| kWh - Channel 11 | 11 | 5308 | 5309 | 10020 | 10021 |  |  | R | NV
| kWh - Channel 12 | 12 | 5310 | 5311 | 10022 | 10023 |  |  | R | NV
| kWh - Channel 13 | 13 | 5312 | 5313 | 10024 | 10025 |  |  | R | NV
| kWh - Channel 14 | 14 | 5314 | 5315 | 10026 | 10027 |  |  | R | NV
| kWh - Channel 15 | 15 | 5316 | 5317 | 10028 | 10029 |  |  | R | NV
| kWh - Channel 16 | 16 | 5318 | 5319 | 10030 | 10031 |  |  | R | NV
| kWh - Channel 17 | 17 | 5320 | 5321 | 10032 | 10033 |  |  | R | NV
| kWh - Channel 18 | 18 | 5322 | 5323 | 10034 | 10035 |  |  | R | NV
| kWh - Channel 19 | 19 | 5324 | 5325 | 10036 | 10037 |  |  | R | NV
| kWh - Channel 20 | 20 | 5326 | 5327 | 10038 | 10039 |  |  | R | NV
| kWh - Channel 21 | 21 | 5328 | 5329 | 10040 | 10041 |  |  | R | NV
| kWh - Channel 22 | 22 | 5330 | 5331 | 10042 | 10043 |  |  | R | NV
| kWh - Channel 23 | 23 | 5332 | 5333 | 10044 | 10045 |  |  | R | NV
| kWh - Channel 24 | 24 | 5334 | 5335 | 10046 | 10047 |  |  | R | NV
| kWh - Channel 25 | 25 | 5336 | 5337 | 10048 | 10049 |  |  | R | NV
| kWh - Channel 26 | 26 | 5338 | 5339 | 10050 | 10051 |  |  | R | NV
| kWh - Channel 27 | 27 | 5340 | 5341 | 10052 | 10053 |  |  | R | NV
| kWh - Channel 28 | 28 | 5342 | 5343 | 10054 | 10055 |  |  | R | NV
| kWh - Channel 29 | 29 | 5344 | 5345 | 10056 | 10057 |  |  | R | NV
| kWh - Channel 30 | 30 | 5346 | 5347 | 10058 | 10059 |  |  | R | NV
| kWh - Channel 31 | 31 | 5348 | 5349 | 10060 | 10061 |  |  | R | NV
| kWh - Channel 32 | 32 | 5350 | 5351 | 10062 | 10063 |  |  | R | NV
| kWh - Channel 33 | 33 | 5352 | 5353 | 10064 | 10065 |  |  | R | NV
| kWh - Channel 34 | 34 | 5354 | 5355 | 10066 | 10067 |  |  | R | NV
| kWh - Channel 35 | 35 | 5356 | 5357 | 10068 | 10069 |  |  | R | NV
| kWh - Channel 36 | 36 | 5358 | 5359 | 10070 | 10071 |  |  | R | NV
| kWh - Channel 37 | 37 | 5360 | 5361 | 10072 | 10073 |  |  | R | NV
| kWh - Channel 38 | 38 | 5362 | 5363 | 10074 | 10075 |  |  | R | NV
| kWh - Channel 39 | 39 | 5364 | 5365 | 10076 | 10077 |  |  | R | NV
| kWh - Channel 40 | 40 | 5366 | 5367 | 10078 | 10079 |  |  | R | NV
| kWh - Channel 41 | 41 | 5368 | 5369 | 10080 | 10081 |  |  | R | NV
| kWh - Channel 42 | 42 | 5370 | 5371 | 10082 | 10083 |  |  | R | NV
| kWh - Channel 43 | 43 | 5372 | 5373 | 10084 | 10085 |  |  | R | NV
| kWh - Channel 44 | 44 | 5374 | 5375 | 10086 | 10087 |  |  | R | NV
| kWh - Channel 45 | 45 | 5376 | 5377 | 10088 | 10089 |  |  | R | NV
| kWh - Channel 46 | 46 | 5378 | 5379 | 10090 | 10091 |  |  | R | NV
| kWh - Channel 47 | 47 | 5380 | 5381 | 10092 | 10093 |  |  | R | NV
| kWh - Channel 48 | 48 | 5382 | 5383 | 10094 | 10095 |  |  | R | NV
| kWh - Channel 49 | 49 | 5384 | 5385 | 10096 | 10097 |  |  | R | NV
| kWh - Channel 50 | 50 | 5386 | 5387 | 10098 | 10099 |  |  | R | NV
| kWh - Channel 51 | 51 | 5388 | 5389 | 10100 | 10101 |  |  | R | NV
| kWh - Channel 52 | 52 | 5390 | 5391 | 10102 | 10103 |  |  | R | NV
| kWh - Channel 53 | 53 | 5392 | 5393 | 10104 | 10105 |  |  | R | NV
| kWh - Channel 54 | 54 | 5394 | 5395 | 10106 | 10107 |  |  | R | NV
| kWh - Channel 55 | 55 | 5396 | 5397 | 10108 | 10109 |  |  | R | NV
| kWh - Channel 56 | 56 | 5398 | 5399 | 10110 | 10111 |  |  | R | NV
| kWh - Channel 57 | 57 | 5400 | 5401 | 10112 | 10113 |  |  | R | NV
| kWh - Channel 58 | 58 | 5402 | 5403 | 10114 | 10115 |  |  | R | NV
| kWh - Channel 59 | 59 | 5404 | 5405 | 10116 | 10117 |  |  | R | NV
| kWh - Channel 60 | 60 | 5406 | 5407 | 10118 | 10119 |  |  | R | NV
| kWh - Channel 61 | 61 | 5408 | 5409 | 10120 | 10121 |  |  | R | NV
| kWh - Channel 62 | 62 | 5410 | 5411 | 10122 | 10123 |  |  | R | NV
| kWh - Channel 63 | 63 | 5412 | 5413 | 10124 | 10125 |  |  | R | NV
| kWh - Channel 64 | 64 | 5414 | 5415 | 10126 | 10127 |  |  | R | NV
| kWh - Channel 65 | 65 | 5416 | 5417 | 10128 | 10129 |  |  | R | NV
| kWh - Channel 66 | 66 | 5418 | 5419 | 10130 | 10131 |  |  | R | NV
| kWh - Channel 67 | 67 | 5420 | 5421 | 10132 | 10133 |  |  | R | NV
| kWh - Channel 68 | 68 | 5422 | 5423 | 10134 | 10135 |  |  | R | NV
| kWh - Channel 69 | 69 | 5424 | 5425 | 10136 | 10137 |  |  | R | NV
| kWh - Channel 70 | 70 | 5426 | 5427 | 10138 | 10139 |  |  | R | NV
| kWh - Channel 71 | 71 | 5428 | 5429 | 10140 | 10141 |  |  | R | NV
| kWh - Channel 72 | 72 | 5430 | 5431 | 10142 | 10143 |  |  | R | NV
| kWh - Channel 73 | 73 | 5432 | 5433 | 10144 | 10145 |  |  | R | NV
| kWh - Channel 74 | 74 | 5434 | 5435 | 10146 | 10147 |  |  | R | NV
| kWh - Channel 75 | 75 | 5436 | 5437 | 10148 | 10149 |  |  | R | NV
| kWh - Channel 76 | 76 | 5438 | 5439 | 10150 | 10151 |  |  | R | NV
| kWh - Channel 77 | 77 | 5440 | 5441 | 10152 | 10153 |  |  | R | NV
| kWh - Channel 78 | 78 | 5442 | 5443 | 10154 | 10155 |  |  | R | NV
| kWh - Channel 79 | 79 | 5444 | 5445 | 10156 | 10157 |  |  | R | NV
| kWh - Channel 80 | 80 | 5446 | 5447 | 10158 | 10159 |  |  | R | NV
| kWh - Channel 81 | 81 | 5448 | 5449 | 10160 | 10161 |  |  | R | NV
| kWh - Channel 82 | 82 | 5450 | 5451 | 10162 | 10163 |  |  | R | NV
| kWh - Channel 83 | 83 | 5452 | 5453 | 10164 | 10165 |  |  | R | NV
| kWh - Channel 84 | 84 | 5454 | 5455 | 10166 | 10167 |  |  | R | NV
| kWh - Channel 85 | 85 | 5456 | 5457 | 10168 | 10169 |  |  | R | NV
| kWh - Channel 86 | 86 | 5458 | 5459 | 10170 | 10171 |  |  | R | NV
| kWh - Channel 87 | 87 | 5460 | 5461 | 10172 | 10173 |  |  | R | NV
| kWh - Channel 88 | 88 | 5462 | 5463 | 10174 | 10175 |  |  | R | NV
| kWh - Channel 89 | 89 | 5464 | 5465 | 10176 | 10177 |  |  | R | NV
| kWh - Channel 90 | 90 | 5466 | 5467 | 10178 | 10179 |  |  | R | NV
| kWh - Channel 91 | 91 | 5468 | 5469 | 10180 | 10181 |  |  | R | NV
| kWh - Channel 92 | 92 | 5470 | 5471 | 10182 | 10183 |  |  | R | NV
| kWh - Channel 93 | 93 | 5472 | 5473 | 10184 | 10185 |  |  | R | NV
| kWh - Channel 94 | 94 | 5474 | 5475 | 10186 | 10187 |  |  | R | NV
| kWh - Channel 95 | 95 | 5476 | 5477 | 10188 | 10189 |  |  | R | NV
| kWh - Channel 96 | 96 | 5478 | 5479 | 10190 | 10191 |  |  | R | NV
| kVARh |  | 5480 | 5671 | 10192 | 10383 |  |  | R | NV |  |  | 32 bit unsigned integer
| kVARh - Channel 1 | 1 | 5480 | 5481 | 10192 | 10193 |  |  | R | NV
| kVARh - Channel 2 | 2 | 5482 | 5483 | 10194 | 10195 |  |  | R | NV
| kVARh - Channel 3 | 3 | 5484 | 5485 | 10196 | 10197 |  |  | R | NV
| kVARh - Channel 4 | 4 | 5486 | 5487 | 10198 | 10199 |  |  | R | NV
| kVARh - Channel 5 | 5 | 5488 | 5489 | 10200 | 10201 |  |  | R | NV
| kVARh - Channel 6 | 6 | 5490 | 5491 | 10202 | 10203 |  |  | R | NV
| kVARh - Channel 7 | 7 | 5492 | 5493 | 10204 | 10205 |  |  | R | NV
| kVARh - Channel 8 | 8 | 5494 | 5495 | 10206 | 10207 |  |  | R | NV
| kVARh - Channel 9 | 9 | 5496 | 5497 | 10208 | 10209 |  |  | R | NV
| kVARh - Channel 10 | 10 | 5498 | 5499 | 10210 | 10211 |  |  | R | NV
| kVARh - Channel 11 | 11 | 5500 | 5501 | 10212 | 10213 |  |  | R | NV
| kVARh - Channel 12 | 12 | 5502 | 5503 | 10214 | 10215 |  |  | R | NV
| kVARh - Channel 13 | 13 | 5504 | 5505 | 10216 | 10217 |  |  | R | NV
| kVARh - Channel 14 | 14 | 5506 | 5507 | 10218 | 10219 |  |  | R | NV
| kVARh - Channel 15 | 15 | 5508 | 5509 | 10220 | 10221 |  |  | R | NV
| kVARh - Channel 16 | 16 | 5510 | 5511 | 10222 | 10223 |  |  | R | NV
| kVARh - Channel 17 | 17 | 5512 | 5513 | 10224 | 10225 |  |  | R | NV
| kVARh - Channel 18 | 18 | 5514 | 5515 | 10226 | 10227 |  |  | R | NV
| kVARh - Channel 19 | 19 | 5516 | 5517 | 10228 | 10229 |  |  | R | NV
| kVARh - Channel 20 | 20 | 5518 | 5519 | 10230 | 10231 |  |  | R | NV
| kVARh - Channel 21 | 21 | 5520 | 5521 | 10232 | 10233 |  |  | R | NV
| kVARh - Channel 22 | 22 | 5522 | 5523 | 10234 | 10235 |  |  | R | NV
| kVARh - Channel 23 | 23 | 5524 | 5525 | 10236 | 10237 |  |  | R | NV
| kVARh - Channel 24 | 24 | 5526 | 5527 | 10238 | 10239 |  |  | R | NV
| kVARh - Channel 25 | 25 | 5528 | 5529 | 10240 | 10241 |  |  | R | NV
| kVARh - Channel 26 | 26 | 5530 | 5531 | 10242 | 10243 |  |  | R | NV
| kVARh - Channel 27 | 27 | 5532 | 5533 | 10244 | 10245 |  |  | R | NV
| kVARh - Channel 28 | 28 | 5534 | 5535 | 10246 | 10247 |  |  | R | NV
| kVARh - Channel 29 | 29 | 5536 | 5537 | 10248 | 10249 |  |  | R | NV
| kVARh - Channel 30 | 30 | 5538 | 5539 | 10250 | 10251 |  |  | R | NV
| kVARh - Channel 31 | 31 | 5540 | 5541 | 10252 | 10253 |  |  | R | NV
| kVARh - Channel 32 | 32 | 5542 | 5543 | 10254 | 10255 |  |  | R | NV
| kVARh - Channel 33 | 33 | 5544 | 5545 | 10256 | 10257 |  |  | R | NV
| kVARh - Channel 34 | 34 | 5546 | 5547 | 10258 | 10259 |  |  | R | NV
| kVARh - Channel 35 | 35 | 5548 | 5549 | 10260 | 10261 |  |  | R | NV
| kVARh - Channel 36 | 36 | 5550 | 5551 | 10262 | 10263 |  |  | R | NV
| kVARh - Channel 37 | 37 | 5552 | 5553 | 10264 | 10265 |  |  | R | NV
| kVARh - Channel 38 | 38 | 5554 | 5555 | 10266 | 10267 |  |  | R | NV
| kVARh - Channel 39 | 39 | 5556 | 5557 | 10268 | 10269 |  |  | R | NV
| kVARh - Channel 40 | 40 | 5558 | 5559 | 10270 | 10271 |  |  | R | NV
| kVARh - Channel 41 | 41 | 5560 | 5561 | 10272 | 10273 |  |  | R | NV
| kVARh - Channel 42 | 42 | 5562 | 5563 | 10274 | 10275 |  |  | R | NV
| kVARh - Channel 43 | 43 | 5564 | 5565 | 10276 | 10277 |  |  | R | NV
| kVARh - Channel 44 | 44 | 5566 | 5567 | 10278 | 10279 |  |  | R | NV
| kVARh - Channel 45 | 45 | 5568 | 5569 | 10280 | 10281 |  |  | R | NV
| kVARh - Channel 46 | 46 | 5570 | 5571 | 10282 | 10283 |  |  | R | NV
| kVARh - Channel 47 | 47 | 5572 | 5573 | 10284 | 10285 |  |  | R | NV
| kVARh - Channel 48 | 48 | 5574 | 5575 | 10286 | 10287 |  |  | R | NV
| kVARh - Channel 49 | 49 | 5576 | 5577 | 10288 | 10289 |  |  | R | NV
| kVARh - Channel 50 | 50 | 5578 | 5579 | 10290 | 10291 |  |  | R | NV
| kVARh - Channel 51 | 51 | 5580 | 5581 | 10292 | 10293 |  |  | R | NV
| kVARh - Channel 52 | 52 | 5582 | 5583 | 10294 | 10295 |  |  | R | NV
| kVARh - Channel 53 | 53 | 5584 | 5585 | 10296 | 10297 |  |  | R | NV
| kVARh - Channel 54 | 54 | 5586 | 5587 | 10298 | 10299 |  |  | R | NV
| kVARh - Channel 55 | 55 | 5588 | 5589 | 10300 | 10301 |  |  | R | NV
| kVARh - Channel 56 | 56 | 5590 | 5591 | 10302 | 10303 |  |  | R | NV
| kVARh - Channel 57 | 57 | 5592 | 5593 | 10304 | 10305 |  |  | R | NV
| kVARh - Channel 58 | 58 | 5594 | 5595 | 10306 | 10307 |  |  | R | NV
| kVARh - Channel 59 | 59 | 5596 | 5597 | 10308 | 10309 |  |  | R | NV
| kVARh - Channel 60 | 60 | 5598 | 5599 | 10310 | 10311 |  |  | R | NV
| kVARh - Channel 61 | 61 | 5600 | 5601 | 10312 | 10313 |  |  | R | NV
| kVARh - Channel 62 | 62 | 5602 | 5603 | 10314 | 10315 |  |  | R | NV
| kVARh - Channel 63 | 63 | 5604 | 5605 | 10316 | 10317 |  |  | R | NV
| kVARh - Channel 64 | 64 | 5606 | 5607 | 10318 | 10319 |  |  | R | NV
| kVARh - Channel 65 | 65 | 5608 | 5609 | 10320 | 10321 |  |  | R | NV
| kVARh - Channel 66 | 66 | 5610 | 5611 | 10322 | 10323 |  |  | R | NV
| kVARh - Channel 67 | 67 | 5612 | 5613 | 10324 | 10325 |  |  | R | NV
| kVARh - Channel 68 | 68 | 5614 | 5615 | 10326 | 10327 |  |  | R | NV
| kVARh - Channel 69 | 69 | 5616 | 5617 | 10328 | 10329 |  |  | R | NV
| kVARh - Channel 70 | 70 | 5618 | 5619 | 10330 | 10331 |  |  | R | NV
| kVARh - Channel 71 | 71 | 5620 | 5621 | 10332 | 10333 |  |  | R | NV
| kVARh - Channel 72 | 72 | 5622 | 5623 | 10334 | 10335 |  |  | R | NV
| kVARh - Channel 73 | 73 | 5624 | 5625 | 10336 | 10337 |  |  | R | NV
| kVARh - Channel 74 | 74 | 5626 | 5627 | 10338 | 10339 |  |  | R | NV
| kVARh - Channel 75 | 75 | 5628 | 5629 | 10340 | 10341 |  |  | R | NV
| kVARh - Channel 76 | 76 | 5630 | 5631 | 10342 | 10343 |  |  | R | NV
| kVARh - Channel 77 | 77 | 5632 | 5633 | 10344 | 10345 |  |  | R | NV
| kVARh - Channel 78 | 78 | 5634 | 5635 | 10346 | 10347 |  |  | R | NV
| kVARh - Channel 79 | 79 | 5636 | 5637 | 10348 | 10349 |  |  | R | NV
| kVARh - Channel 80 | 80 | 5638 | 5639 | 10350 | 10351 |  |  | R | NV
| kVARh - Channel 81 | 81 | 5640 | 5641 | 10352 | 10353 |  |  | R | NV
| kVARh - Channel 82 | 82 | 5642 | 5643 | 10354 | 10355 |  |  | R | NV
| kVARh - Channel 83 | 83 | 5644 | 5645 | 10356 | 10357 |  |  | R | NV
| kVARh - Channel 84 | 84 | 5646 | 5647 | 10358 | 10359 |  |  | R | NV
| kVARh - Channel 85 | 85 | 5648 | 5649 | 10360 | 10361 |  |  | R | NV
| kVARh - Channel 86 | 86 | 5650 | 5651 | 10362 | 10363 |  |  | R | NV
| kVARh - Channel 87 | 87 | 5652 | 5653 | 10364 | 10365 |  |  | R | NV
| kVARh - Channel 88 | 88 | 5654 | 5655 | 10366 | 10367 |  |  | R | NV
| kVARh - Channel 89 | 89 | 5656 | 5657 | 10368 | 10369 |  |  | R | NV
| kVARh - Channel 90 | 90 | 5658 | 5659 | 10370 | 10371 |  |  | R | NV
| kVARh - Channel 91 | 91 | 5660 | 5661 | 10372 | 10373 |  |  | R | NV
| kVARh - Channel 92 | 92 | 5662 | 5663 | 10374 | 10375 |  |  | R | NV
| kVARh - Channel 93 | 93 | 5664 | 5665 | 10376 | 10377 |  |  | R | NV
| kVARh - Channel 94 | 94 | 5666 | 5667 | 10378 | 10379 |  |  | R | NV
| kVARh - Channel 95 | 95 | 5668 | 5669 | 10380 | 10381 |  |  | R | NV
| kVARh - Channel 96 | 96 | 5670 | 5671 | 10382 | 10383 |  |  | R | NV
| kVAh |  | 5672 | 5863 | 10384 | 10575 |  |  | R | NV |  |  | 32 bit unsigned integer
| kVAh - Channel 1 | 1 | 5672 | 5673 | 10384 | 10385 |  |  | R | NV
| kVAh - Channel 2 | 2 | 5674 | 5675 | 10386 | 10387 |  |  | R | NV
| kVAh - Channel 3 | 3 | 5676 | 5677 | 10388 | 10389 |  |  | R | NV
| kVAh - Channel 4 | 4 | 5678 | 5679 | 10390 | 10391 |  |  | R | NV
| kVAh - Channel 5 | 5 | 5680 | 5681 | 10392 | 10393 |  |  | R | NV
| kVAh - Channel 6 | 6 | 5682 | 5683 | 10394 | 10395 |  |  | R | NV
| kVAh - Channel 7 | 7 | 5684 | 5685 | 10396 | 10397 |  |  | R | NV
| kVAh - Channel 8 | 8 | 5686 | 5687 | 10398 | 10399 |  |  | R | NV
| kVAh - Channel 9 | 9 | 5688 | 5689 | 10400 | 10401 |  |  | R | NV
| kVAh - Channel 10 | 10 | 5690 | 5691 | 10402 | 10403 |  |  | R | NV
| kVAh - Channel 11 | 11 | 5692 | 5693 | 10404 | 10405 |  |  | R | NV
| kVAh - Channel 12 | 12 | 5694 | 5695 | 10406 | 10407 |  |  | R | NV
| kVAh - Channel 13 | 13 | 5696 | 5697 | 10408 | 10409 |  |  | R | NV
| kVAh - Channel 14 | 14 | 5698 | 5699 | 10410 | 10411 |  |  | R | NV
| kVAh - Channel 15 | 15 | 5700 | 5701 | 10412 | 10413 |  |  | R | NV
| kVAh - Channel 16 | 16 | 5702 | 5703 | 10414 | 10415 |  |  | R | NV
| kVAh - Channel 17 | 17 | 5704 | 5705 | 10416 | 10417 |  |  | R | NV
| kVAh - Channel 18 | 18 | 5706 | 5707 | 10418 | 10419 |  |  | R | NV
| kVAh - Channel 19 | 19 | 5708 | 5709 | 10420 | 10421 |  |  | R | NV
| kVAh - Channel 20 | 20 | 5710 | 5711 | 10422 | 10423 |  |  | R | NV
| kVAh - Channel 21 | 21 | 5712 | 5713 | 10424 | 10425 |  |  | R | NV
| kVAh - Channel 22 | 22 | 5714 | 5715 | 10426 | 10427 |  |  | R | NV
| kVAh - Channel 23 | 23 | 5716 | 5717 | 10428 | 10429 |  |  | R | NV
| kVAh - Channel 24 | 24 | 5718 | 5719 | 10430 | 10431 |  |  | R | NV
| kVAh - Channel 25 | 25 | 5720 | 5721 | 10432 | 10433 |  |  | R | NV
| kVAh - Channel 26 | 26 | 5722 | 5723 | 10434 | 10435 |  |  | R | NV
| kVAh - Channel 27 | 27 | 5724 | 5725 | 10436 | 10437 |  |  | R | NV
| kVAh - Channel 28 | 28 | 5726 | 5727 | 10438 | 10439 |  |  | R | NV
| kVAh - Channel 29 | 29 | 5728 | 5729 | 10440 | 10441 |  |  | R | NV
| kVAh - Channel 30 | 30 | 5730 | 5731 | 10442 | 10443 |  |  | R | NV
| kVAh - Channel 31 | 31 | 5732 | 5733 | 10444 | 10445 |  |  | R | NV
| kVAh - Channel 32 | 32 | 5734 | 5735 | 10446 | 10447 |  |  | R | NV
| kVAh - Channel 33 | 33 | 5736 | 5737 | 10448 | 10449 |  |  | R | NV
| kVAh - Channel 34 | 34 | 5738 | 5739 | 10450 | 10451 |  |  | R | NV
| kVAh - Channel 35 | 35 | 5740 | 5741 | 10452 | 10453 |  |  | R | NV
| kVAh - Channel 36 | 36 | 5742 | 5743 | 10454 | 10455 |  |  | R | NV
| kVAh - Channel 37 | 37 | 5744 | 5745 | 10456 | 10457 |  |  | R | NV
| kVAh - Channel 38 | 38 | 5746 | 5747 | 10458 | 10459 |  |  | R | NV
| kVAh - Channel 39 | 39 | 5748 | 5749 | 10460 | 10461 |  |  | R | NV
| kVAh - Channel 40 | 40 | 5750 | 5751 | 10462 | 10463 |  |  | R | NV
| kVAh - Channel 41 | 41 | 5752 | 5753 | 10464 | 10465 |  |  | R | NV
| kVAh - Channel 42 | 42 | 5754 | 5755 | 10466 | 10467 |  |  | R | NV
| kVAh - Channel 43 | 43 | 5756 | 5757 | 10468 | 10469 |  |  | R | NV
| kVAh - Channel 44 | 44 | 5758 | 5759 | 10470 | 10471 |  |  | R | NV
| kVAh - Channel 45 | 45 | 5760 | 5761 | 10472 | 10473 |  |  | R | NV
| kVAh - Channel 46 | 46 | 5762 | 5763 | 10474 | 10475 |  |  | R | NV
| kVAh - Channel 47 | 47 | 5764 | 5765 | 10476 | 10477 |  |  | R | NV
| kVAh - Channel 48 | 48 | 5766 | 5767 | 10478 | 10479 |  |  | R | NV
| kVAh - Channel 49 | 49 | 5768 | 5769 | 10480 | 10481 |  |  | R | NV
| kVAh - Channel 50 | 50 | 5770 | 5771 | 10482 | 10483 |  |  | R | NV
| kVAh - Channel 51 | 51 | 5772 | 5773 | 10484 | 10485 |  |  | R | NV
| kVAh - Channel 52 | 52 | 5774 | 5775 | 10486 | 10487 |  |  | R | NV
| kVAh - Channel 53 | 53 | 5776 | 5777 | 10488 | 10489 |  |  | R | NV
| kVAh - Channel 54 | 54 | 5778 | 5779 | 10490 | 10491 |  |  | R | NV
| kVAh - Channel 55 | 55 | 5780 | 5781 | 10492 | 10493 |  |  | R | NV
| kVAh - Channel 56 | 56 | 5782 | 5783 | 10494 | 10495 |  |  | R | NV
| kVAh - Channel 57 | 57 | 5784 | 5785 | 10496 | 10497 |  |  | R | NV
| kVAh - Channel 58 | 58 | 5786 | 5787 | 10498 | 10499 |  |  | R | NV
| kVAh - Channel 59 | 59 | 5788 | 5789 | 10500 | 10501 |  |  | R | NV
| kVAh - Channel 60 | 60 | 5790 | 5791 | 10502 | 10503 |  |  | R | NV
| kVAh - Channel 61 | 61 | 5792 | 5793 | 10504 | 10505 |  |  | R | NV
| kVAh - Channel 62 | 62 | 5794 | 5795 | 10506 | 10507 |  |  | R | NV
| kVAh - Channel 63 | 63 | 5796 | 5797 | 10508 | 10509 |  |  | R | NV
| kVAh - Channel 64 | 64 | 5798 | 5799 | 10510 | 10511 |  |  | R | NV
| kVAh - Channel 65 | 65 | 5800 | 5801 | 10512 | 10513 |  |  | R | NV
| kVAh - Channel 66 | 66 | 5802 | 5803 | 10514 | 10515 |  |  | R | NV
| kVAh - Channel 67 | 67 | 5804 | 5805 | 10516 | 10517 |  |  | R | NV
| kVAh - Channel 68 | 68 | 5806 | 5807 | 10518 | 10519 |  |  | R | NV
| kVAh - Channel 69 | 69 | 5808 | 5809 | 10520 | 10521 |  |  | R | NV
| kVAh - Channel 70 | 70 | 5810 | 5811 | 10522 | 10523 |  |  | R | NV
| kVAh - Channel 71 | 71 | 5812 | 5813 | 10524 | 10525 |  |  | R | NV
| kVAh - Channel 72 | 72 | 5814 | 5815 | 10526 | 10527 |  |  | R | NV
| kVAh - Channel 73 | 73 | 5816 | 5817 | 10528 | 10529 |  |  | R | NV
| kVAh - Channel 74 | 74 | 5818 | 5819 | 10530 | 10531 |  |  | R | NV
| kVAh - Channel 75 | 75 | 5820 | 5821 | 10532 | 10533 |  |  | R | NV
| kVAh - Channel 76 | 76 | 5822 | 5823 | 10534 | 10535 |  |  | R | NV
| kVAh - Channel 77 | 77 | 5824 | 5825 | 10536 | 10537 |  |  | R | NV
| kVAh - Channel 78 | 78 | 5826 | 5827 | 10538 | 10539 |  |  | R | NV
| kVAh - Channel 79 | 79 | 5828 | 5829 | 10540 | 10541 |  |  | R | NV
| kVAh - Channel 80 | 80 | 5830 | 5831 | 10542 | 10543 |  |  | R | NV
| kVAh - Channel 81 | 81 | 5832 | 5833 | 10544 | 10545 |  |  | R | NV
| kVAh - Channel 82 | 82 | 5834 | 5835 | 10546 | 10547 |  |  | R | NV
| kVAh - Channel 83 | 83 | 5836 | 5837 | 10548 | 10549 |  |  | R | NV
| kVAh - Channel 84 | 84 | 5838 | 5839 | 10550 | 10551 |  |  | R | NV
| kVAh - Channel 85 | 85 | 5840 | 5841 | 10552 | 10553 |  |  | R | NV
| kVAh - Channel 86 | 86 | 5842 | 5843 | 10554 | 10555 |  |  | R | NV
| kVAh - Channel 87 | 87 | 5844 | 5845 | 10556 | 10557 |  |  | R | NV
| kVAh - Channel 88 | 88 | 5846 | 5847 | 10558 | 10559 |  |  | R | NV
| kVAh - Channel 89 | 89 | 5848 | 5849 | 10560 | 10561 |  |  | R | NV
| kVAh - Channel 90 | 90 | 5850 | 5851 | 10562 | 10563 |  |  | R | NV
| kVAh - Channel 91 | 91 | 5852 | 5853 | 10564 | 10565 |  |  | R | NV
| kVAh - Channel 92 | 92 | 5854 | 5855 | 10566 | 10567 |  |  | R | NV
| kVAh - Channel 93 | 93 | 5856 | 5857 | 10568 | 10569 |  |  | R | NV
| kVAh - Channel 94 | 94 | 5858 | 5859 | 10570 | 10571 |  |  | R | NV
| kVAh - Channel 95 | 95 | 5860 | 5861 | 10572 | 10573 |  |  | R | NV
| kVAh - Channel 96 | 96 | 5862 | 5863 | 10574 | 10575 |  |  | R | NV
| kW |  | 5864 | 5959 | 10576 | 10767 |  |  | R
| kW - Channel 1 | 1 | 5864 |  | 10576 | 10577 |  |  | R
| kW - Channel 2 | 2 | 5865 |  | 10578 | 10579 |  |  | R
| kW - Channel 3 | 3 | 5866 |  | 10580 | 10581 |  |  | R
| kW - Channel 4 | 4 | 5867 |  | 10582 | 10583 |  |  | R
| kW - Channel 5 | 5 | 5868 |  | 10584 | 10585 |  |  | R
| kW - Channel 6 | 6 | 5869 |  | 10586 | 10587 |  |  | R
| kW - Channel 7 | 7 | 5870 |  | 10588 | 10589 |  |  | R
| kW - Channel 8 | 8 | 5871 |  | 10590 | 10591 |  |  | R
| kW - Channel 9 | 9 | 5872 |  | 10592 | 10593 |  |  | R
| kW - Channel 10 | 10 | 5873 |  | 10594 | 10595 |  |  | R
| kW - Channel 11 | 11 | 5874 |  | 10596 | 10597 |  |  | R
| kW - Channel 12 | 12 | 5875 |  | 10598 | 10599 |  |  | R
| kW - Channel 13 | 13 | 5876 |  | 10600 | 10601 |  |  | R
| kW - Channel 14 | 14 | 5877 |  | 10602 | 10603 |  |  | R
| kW - Channel 15 | 15 | 5878 |  | 10604 | 10605 |  |  | R
| kW - Channel 16 | 16 | 5879 |  | 10606 | 10607 |  |  | R
| kW - Channel 17 | 17 | 5880 |  | 10608 | 10609 |  |  | R
| kW - Channel 18 | 18 | 5881 |  | 10610 | 10611 |  |  | R
| kW - Channel 19 | 19 | 5882 |  | 10612 | 10613 |  |  | R
| kW - Channel 20 | 20 | 5883 |  | 10614 | 10615 |  |  | R
| kW - Channel 21 | 21 | 5884 |  | 10616 | 10617 |  |  | R
| kW - Channel 22 | 22 | 5885 |  | 10618 | 10619 |  |  | R
| kW - Channel 23 | 23 | 5886 |  | 10620 | 10621 |  |  | R
| kW - Channel 24 | 24 | 5887 |  | 10622 | 10623 |  |  | R
| kW - Channel 25 | 25 | 5888 |  | 10624 | 10625 |  |  | R
| kW - Channel 26 | 26 | 5889 |  | 10626 | 10627 |  |  | R
| kW - Channel 27 | 27 | 5890 |  | 10628 | 10629 |  |  | R
| kW - Channel 28 | 28 | 5891 |  | 10630 | 10631 |  |  | R
| kW - Channel 29 | 29 | 5892 |  | 10632 | 10633 |  |  | R
| kW - Channel 30 | 30 | 5893 |  | 10634 | 10635 |  |  | R
| kW - Channel 31 | 31 | 5894 |  | 10636 | 10637 |  |  | R
| kW - Channel 32 | 32 | 5895 |  | 10638 | 10639 |  |  | R
| kW - Channel 33 | 33 | 5896 |  | 10640 | 10641 |  |  | R
| kW - Channel 34 | 34 | 5897 |  | 10642 | 10643 |  |  | R
| kW - Channel 35 | 35 | 5898 |  | 10644 | 10645 |  |  | R
| kW - Channel 36 | 36 | 5899 |  | 10646 | 10647 |  |  | R
| kW - Channel 37 | 37 | 5900 |  | 10648 | 10649 |  |  | R
| kW - Channel 38 | 38 | 5901 |  | 10650 | 10651 |  |  | R
| kW - Channel 39 | 39 | 5902 |  | 10652 | 10653 |  |  | R
| kW - Channel 40 | 40 | 5903 |  | 10654 | 10655 |  |  | R
| kW - Channel 41 | 41 | 5904 |  | 10656 | 10657 |  |  | R
| kW - Channel 42 | 42 | 5905 |  | 10658 | 10659 |  |  | R
| kW - Channel 43 | 43 | 5906 |  | 10660 | 10661 |  |  | R
| kW - Channel 44 | 44 | 5907 |  | 10662 | 10663 |  |  | R
| kW - Channel 45 | 45 | 5908 |  | 10664 | 10665 |  |  | R
| kW - Channel 46 | 46 | 5909 |  | 10666 | 10667 |  |  | R
| kW - Channel 47 | 47 | 5910 |  | 10668 | 10669 |  |  | R
| kW - Channel 48 | 48 | 5911 |  | 10670 | 10671 |  |  | R
| kW - Channel 49 | 49 | 5912 |  | 10672 | 10673 |  |  | R
| kW - Channel 50 | 50 | 5913 |  | 10674 | 10675 |  |  | R
| kW - Channel 51 | 51 | 5914 |  | 10676 | 10677 |  |  | R
| kW - Channel 52 | 52 | 5915 |  | 10678 | 10679 |  |  | R
| kW - Channel 53 | 53 | 5916 |  | 10680 | 10681 |  |  | R
| kW - Channel 54 | 54 | 5917 |  | 10682 | 10683 |  |  | R
| kW - Channel 55 | 55 | 5918 |  | 10684 | 10685 |  |  | R
| kW - Channel 56 | 56 | 5919 |  | 10686 | 10687 |  |  | R
| kW - Channel 57 | 57 | 5920 |  | 10688 | 10689 |  |  | R
| kW - Channel 58 | 58 | 5921 |  | 10690 | 10691 |  |  | R
| kW - Channel 59 | 59 | 5922 |  | 10692 | 10693 |  |  | R
| kW - Channel 60 | 60 | 5923 |  | 10694 | 10695 |  |  | R
| kW - Channel 61 | 61 | 5924 |  | 10696 | 10697 |  |  | R
| kW - Channel 62 | 62 | 5925 |  | 10698 | 10699 |  |  | R
| kW - Channel 63 | 63 | 5926 |  | 10700 | 10701 |  |  | R
| kW - Channel 64 | 64 | 5927 |  | 10702 | 10703 |  |  | R
| kW - Channel 65 | 65 | 5928 |  | 10704 | 10705 |  |  | R
| kW - Channel 66 | 66 | 5929 |  | 10706 | 10707 |  |  | R
| kW - Channel 67 | 67 | 5930 |  | 10708 | 10709 |  |  | R
| kW - Channel 68 | 68 | 5931 |  | 10710 | 10711 |  |  | R
| kW - Channel 69 | 69 | 5932 |  | 10712 | 10713 |  |  | R
| kW - Channel 70 | 70 | 5933 |  | 10714 | 10715 |  |  | R
| kW - Channel 71 | 71 | 5934 |  | 10716 | 10717 |  |  | R
| kW - Channel 72 | 72 | 5935 |  | 10718 | 10719 |  |  | R
| kW - Channel 73 | 73 | 5936 |  | 10720 | 10721 |  |  | R
| kW - Channel 74 | 74 | 5937 |  | 10722 | 10723 |  |  | R
| kW - Channel 75 | 75 | 5938 |  | 10724 | 10725 |  |  | R
| kW - Channel 76 | 76 | 5939 |  | 10726 | 10727 |  |  | R
| kW - Channel 77 | 77 | 5940 |  | 10728 | 10729 |  |  | R
| kW - Channel 78 | 78 | 5941 |  | 10730 | 10731 |  |  | R
| kW - Channel 79 | 79 | 5942 |  | 10732 | 10733 |  |  | R
| kW - Channel 80 | 80 | 5943 |  | 10734 | 10735 |  |  | R
| kW - Channel 81 | 81 | 5944 |  | 10736 | 10737 |  |  | R
| kW - Channel 82 | 82 | 5945 |  | 10738 | 10739 |  |  | R
| kW - Channel 83 | 83 | 5946 |  | 10740 | 10741 |  |  | R
| kW - Channel 84 | 84 | 5947 |  | 10742 | 10743 |  |  | R
| kW - Channel 85 | 85 | 5948 |  | 10744 | 10745 |  |  | R
| kW - Channel 86 | 86 | 5949 |  | 10746 | 10747 |  |  | R
| kW - Channel 87 | 87 | 5950 |  | 10748 | 10749 |  |  | R
| kW - Channel 88 | 88 | 5951 |  | 10750 | 10751 |  |  | R
| kW - Channel 89 | 89 | 5952 |  | 10752 | 10753 |  |  | R
| kW - Channel 90 | 90 | 5953 |  | 10754 | 10755 |  |  | R
| kW - Channel 91 | 91 | 5954 |  | 10756 | 10757 |  |  | R
| kW - Channel 92 | 92 | 5955 |  | 10758 | 10759 |  |  | R
| kW - Channel 93 | 93 | 5956 |  | 10760 | 10761 |  |  | R
| kW - Channel 94 | 94 | 5957 |  | 10762 | 10763 |  |  | R
| kW - Channel 95 | 95 | 5958 |  | 10764 | 10765 |  |  | R
| kW - Channel 96 | 96 | 5959 |  | 10766 | 10767 |  |  | R
| kVAR |  | 5960 | 6055 | 10768 | 10959 |  |  | R
| kVAR - Channel 1 | 1 | 5960 |  | 10768 | 10769 |  |  | R
| kVAR - Channel 2 | 2 | 5961 |  | 10770 | 10771 |  |  | R
| kVAR - Channel 3 | 3 | 5962 |  | 10772 | 10773 |  |  | R
| kVAR - Channel 4 | 4 | 5963 |  | 10774 | 10775 |  |  | R
| kVAR - Channel 5 | 5 | 5964 |  | 10776 | 10777 |  |  | R
| kVAR - Channel 6 | 6 | 5965 |  | 10778 | 10779 |  |  | R
| kVAR - Channel 7 | 7 | 5966 |  | 10780 | 10781 |  |  | R
| kVAR - Channel 8 | 8 | 5967 |  | 10782 | 10783 |  |  | R
| kVAR - Channel 9 | 9 | 5968 |  | 10784 | 10785 |  |  | R
| kVAR - Channel 10 | 10 | 5969 |  | 10786 | 10787 |  |  | R
| kVAR - Channel 11 | 11 | 5970 |  | 10788 | 10789 |  |  | R
| kVAR - Channel 12 | 12 | 5971 |  | 10790 | 10791 |  |  | R
| kVAR - Channel 13 | 13 | 5972 |  | 10792 | 10793 |  |  | R
| kVAR - Channel 14 | 14 | 5973 |  | 10794 | 10795 |  |  | R
| kVAR - Channel 15 | 15 | 5974 |  | 10796 | 10797 |  |  | R
| kVAR - Channel 16 | 16 | 5975 |  | 10798 | 10799 |  |  | R
| kVAR - Channel 17 | 17 | 5976 |  | 10800 | 10801 |  |  | R
| kVAR - Channel 18 | 18 | 5977 |  | 10802 | 10803 |  |  | R
| kVAR - Channel 19 | 19 | 5978 |  | 10804 | 10805 |  |  | R
| kVAR - Channel 20 | 20 | 5979 |  | 10806 | 10807 |  |  | R
| kVAR - Channel 21 | 21 | 5980 |  | 10808 | 10809 |  |  | R
| kVAR - Channel 22 | 22 | 5981 |  | 10810 | 10811 |  |  | R
| kVAR - Channel 23 | 23 | 5982 |  | 10812 | 10813 |  |  | R
| kVAR - Channel 24 | 24 | 5983 |  | 10814 | 10815 |  |  | R
| kVAR - Channel 25 | 25 | 5984 |  | 10816 | 10817 |  |  | R
| kVAR - Channel 26 | 26 | 5985 |  | 10818 | 10819 |  |  | R
| kVAR - Channel 27 | 27 | 5986 |  | 10820 | 10821 |  |  | R
| kVAR - Channel 28 | 28 | 5987 |  | 10822 | 10823 |  |  | R
| kVAR - Channel 29 | 29 | 5988 |  | 10824 | 10825 |  |  | R
| kVAR - Channel 30 | 30 | 5989 |  | 10826 | 10827 |  |  | R
| kVAR - Channel 31 | 31 | 5990 |  | 10828 | 10829 |  |  | R
| kVAR - Channel 32 | 32 | 5991 |  | 10830 | 10831 |  |  | R
| kVAR - Channel 33 | 33 | 5992 |  | 10832 | 10833 |  |  | R
| kVAR - Channel 34 | 34 | 5993 |  | 10834 | 10835 |  |  | R
| kVAR - Channel 35 | 35 | 5994 |  | 10836 | 10837 |  |  | R
| kVAR - Channel 36 | 36 | 5995 |  | 10838 | 10839 |  |  | R
| kVAR - Channel 37 | 37 | 5996 |  | 10840 | 10841 |  |  | R
| kVAR - Channel 38 | 38 | 5997 |  | 10842 | 10843 |  |  | R
| kVAR - Channel 39 | 39 | 5998 |  | 10844 | 10845 |  |  | R
| kVAR - Channel 40 | 40 | 5999 |  | 10846 | 10847 |  |  | R
| kVAR - Channel 41 | 41 | 6000 |  | 10848 | 10849 |  |  | R
| kVAR - Channel 42 | 42 | 6001 |  | 10850 | 10851 |  |  | R
| kVAR - Channel 43 | 43 | 6002 |  | 10852 | 10853 |  |  | R
| kVAR - Channel 44 | 44 | 6003 |  | 10854 | 10855 |  |  | R
| kVAR - Channel 45 | 45 | 6004 |  | 10856 | 10857 |  |  | R
| kVAR - Channel 46 | 46 | 6005 |  | 10858 | 10859 |  |  | R
| kVAR - Channel 47 | 47 | 6006 |  | 10860 | 10861 |  |  | R
| kVAR - Channel 48 | 48 | 6007 |  | 10862 | 10863 |  |  | R
| kVAR - Channel 49 | 49 | 6008 |  | 10864 | 10865 |  |  | R
| kVAR - Channel 50 | 50 | 6009 |  | 10866 | 10867 |  |  | R
| kVAR - Channel 51 | 51 | 6010 |  | 10868 | 10869 |  |  | R
| kVAR - Channel 52 | 52 | 6011 |  | 10870 | 10871 |  |  | R
| kVAR - Channel 53 | 53 | 6012 |  | 10872 | 10873 |  |  | R
| kVAR - Channel 54 | 54 | 6013 |  | 10874 | 10875 |  |  | R
| kVAR - Channel 55 | 55 | 6014 |  | 10876 | 10877 |  |  | R
| kVAR - Channel 56 | 56 | 6015 |  | 10878 | 10879 |  |  | R
| kVAR - Channel 57 | 57 | 6016 |  | 10880 | 10881 |  |  | R
| kVAR - Channel 58 | 58 | 6017 |  | 10882 | 10883 |  |  | R
| kVAR - Channel 59 | 59 | 6018 |  | 10884 | 10885 |  |  | R
| kVAR - Channel 60 | 60 | 6019 |  | 10886 | 10887 |  |  | R
| kVAR - Channel 61 | 61 | 6020 |  | 10888 | 10889 |  |  | R
| kVAR - Channel 62 | 62 | 6021 |  | 10890 | 10891 |  |  | R
| kVAR - Channel 63 | 63 | 6022 |  | 10892 | 10893 |  |  | R
| kVAR - Channel 64 | 64 | 6023 |  | 10894 | 10895 |  |  | R
| kVAR - Channel 65 | 65 | 6024 |  | 10896 | 10897 |  |  | R
| kVAR - Channel 66 | 66 | 6025 |  | 10898 | 10899 |  |  | R
| kVAR - Channel 67 | 67 | 6026 |  | 10900 | 10901 |  |  | R
| kVAR - Channel 68 | 68 | 6027 |  | 10902 | 10903 |  |  | R
| kVAR - Channel 69 | 69 | 6028 |  | 10904 | 10905 |  |  | R
| kVAR - Channel 70 | 70 | 6029 |  | 10906 | 10907 |  |  | R
| kVAR - Channel 71 | 71 | 6030 |  | 10908 | 10909 |  |  | R
| kVAR - Channel 72 | 72 | 6031 |  | 10910 | 10911 |  |  | R
| kVAR - Channel 73 | 73 | 6032 |  | 10912 | 10913 |  |  | R
| kVAR - Channel 74 | 74 | 6033 |  | 10914 | 10915 |  |  | R
| kVAR - Channel 75 | 75 | 6034 |  | 10916 | 10917 |  |  | R
| kVAR - Channel 76 | 76 | 6035 |  | 10918 | 10919 |  |  | R
| kVAR - Channel 77 | 77 | 6036 |  | 10920 | 10921 |  |  | R
| kVAR - Channel 78 | 78 | 6037 |  | 10922 | 10923 |  |  | R
| kVAR - Channel 79 | 79 | 6038 |  | 10924 | 10925 |  |  | R
| kVAR - Channel 80 | 80 | 6039 |  | 10926 | 10927 |  |  | R
| kVAR - Channel 81 | 81 | 6040 |  | 10928 | 10929 |  |  | R
| kVAR - Channel 82 | 82 | 6041 |  | 10930 | 10931 |  |  | R
| kVAR - Channel 83 | 83 | 6042 |  | 10932 | 10933 |  |  | R
| kVAR - Channel 84 | 84 | 6043 |  | 10934 | 10935 |  |  | R
| kVAR - Channel 85 | 85 | 6044 |  | 10936 | 10937 |  |  | R
| kVAR - Channel 86 | 86 | 6045 |  | 10938 | 10939 |  |  | R
| kVAR - Channel 87 | 87 | 6046 |  | 10940 | 10941 |  |  | R
| kVAR - Channel 88 | 88 | 6047 |  | 10942 | 10943 |  |  | R
| kVAR - Channel 89 | 89 | 6048 |  | 10944 | 10945 |  |  | R
| kVAR - Channel 90 | 90 | 6049 |  | 10946 | 10947 |  |  | R
| kVAR - Channel 91 | 91 | 6050 |  | 10948 | 10949 |  |  | R
| kVAR - Channel 92 | 92 | 6051 |  | 10950 | 10951 |  |  | R
| kVAR - Channel 93 | 93 | 6052 |  | 10952 | 10953 |  |  | R
| kVAR - Channel 94 | 94 | 6053 |  | 10954 | 10955 |  |  | R
| kVAR - Channel 95 | 95 | 6054 |  | 10956 | 10957 |  |  | R
| kVAR - Channel 96 | 96 | 6055 |  | 10958 | 10959 |  |  | R
| kVA |  | 6056 | 6151 | 10960 | 11151 |  |  | R
| kVA - Channel 1 | 1 | 6056 |  | 10960 | 10961 |  |  | R
| kVA - Channel 2 | 2 | 6057 |  | 10962 | 10963 |  |  | R
| kVA - Channel 3 | 3 | 6058 |  | 10964 | 10965 |  |  | R
| kVA - Channel 4 | 4 | 6059 |  | 10966 | 10967 |  |  | R
| kVA - Channel 5 | 5 | 6060 |  | 10968 | 10969 |  |  | R
| kVA - Channel 6 | 6 | 6061 |  | 10970 | 10971 |  |  | R
| kVA - Channel 7 | 7 | 6062 |  | 10972 | 10973 |  |  | R
| kVA - Channel 8 | 8 | 6063 |  | 10974 | 10975 |  |  | R
| kVA - Channel 9 | 9 | 6064 |  | 10976 | 10977 |  |  | R
| kVA - Channel 10 | 10 | 6065 |  | 10978 | 10979 |  |  | R
| kVA - Channel 11 | 11 | 6066 |  | 10980 | 10981 |  |  | R
| kVA - Channel 12 | 12 | 6067 |  | 10982 | 10983 |  |  | R
| kVA - Channel 13 | 13 | 6068 |  | 10984 | 10985 |  |  | R
| kVA - Channel 14 | 14 | 6069 |  | 10986 | 10987 |  |  | R
| kVA - Channel 15 | 15 | 6070 |  | 10988 | 10989 |  |  | R
| kVA - Channel 16 | 16 | 6071 |  | 10990 | 10991 |  |  | R
| kVA - Channel 17 | 17 | 6072 |  | 10992 | 10993 |  |  | R
| kVA - Channel 18 | 18 | 6073 |  | 10994 | 10995 |  |  | R
| kVA - Channel 19 | 19 | 6074 |  | 10996 | 10997 |  |  | R
| kVA - Channel 20 | 20 | 6075 |  | 10998 | 10999 |  |  | R
| kVA - Channel 21 | 21 | 6076 |  | 11000 | 11001 |  |  | R
| kVA - Channel 22 | 22 | 6077 |  | 11002 | 11003 |  |  | R
| kVA - Channel 23 | 23 | 6078 |  | 11004 | 11005 |  |  | R
| kVA - Channel 24 | 24 | 6079 |  | 11006 | 11007 |  |  | R
| kVA - Channel 25 | 25 | 6080 |  | 11008 | 11009 |  |  | R
| kVA - Channel 26 | 26 | 6081 |  | 11010 | 11011 |  |  | R
| kVA - Channel 27 | 27 | 6082 |  | 11012 | 11013 |  |  | R
| kVA - Channel 28 | 28 | 6083 |  | 11014 | 11015 |  |  | R
| kVA - Channel 29 | 29 | 6084 |  | 11016 | 11017 |  |  | R
| kVA - Channel 30 | 30 | 6085 |  | 11018 | 11019 |  |  | R
| kVA - Channel 31 | 31 | 6086 |  | 11020 | 11021 |  |  | R
| kVA - Channel 32 | 32 | 6087 |  | 11022 | 11023 |  |  | R
| kVA - Channel 33 | 33 | 6088 |  | 11024 | 11025 |  |  | R
| kVA - Channel 34 | 34 | 6089 |  | 11026 | 11027 |  |  | R
| kVA - Channel 35 | 35 | 6090 |  | 11028 | 11029 |  |  | R
| kVA - Channel 36 | 36 | 6091 |  | 11030 | 11031 |  |  | R
| kVA - Channel 37 | 37 | 6092 |  | 11032 | 11033 |  |  | R
| kVA - Channel 38 | 38 | 6093 |  | 11034 | 11035 |  |  | R
| kVA - Channel 39 | 39 | 6094 |  | 11036 | 11037 |  |  | R
| kVA - Channel 40 | 40 | 6095 |  | 11038 | 11039 |  |  | R
| kVA - Channel 41 | 41 | 6096 |  | 11040 | 11041 |  |  | R
| kVA - Channel 42 | 42 | 6097 |  | 11042 | 11043 |  |  | R
| kVA - Channel 43 | 43 | 6098 |  | 11044 | 11045 |  |  | R
| kVA - Channel 44 | 44 | 6099 |  | 11046 | 11047 |  |  | R
| kVA - Channel 45 | 45 | 6100 |  | 11048 | 11049 |  |  | R
| kVA - Channel 46 | 46 | 6101 |  | 11050 | 11051 |  |  | R
| kVA - Channel 47 | 47 | 6102 |  | 11052 | 11053 |  |  | R
| kVA - Channel 48 | 48 | 6103 |  | 11054 | 11055 |  |  | R
| kVA - Channel 49 | 49 | 6104 |  | 11056 | 11057 |  |  | R
| kVA - Channel 50 | 50 | 6105 |  | 11058 | 11059 |  |  | R
| kVA - Channel 51 | 51 | 6106 |  | 11060 | 11061 |  |  | R
| kVA - Channel 52 | 52 | 6107 |  | 11062 | 11063 |  |  | R
| kVA - Channel 53 | 53 | 6108 |  | 11064 | 11065 |  |  | R
| kVA - Channel 54 | 54 | 6109 |  | 11066 | 11067 |  |  | R
| kVA - Channel 55 | 55 | 6110 |  | 11068 | 11069 |  |  | R
| kVA - Channel 56 | 56 | 6111 |  | 11070 | 11071 |  |  | R
| kVA - Channel 57 | 57 | 6112 |  | 11072 | 11073 |  |  | R
| kVA - Channel 58 | 58 | 6113 |  | 11074 | 11075 |  |  | R
| kVA - Channel 59 | 59 | 6114 |  | 11076 | 11077 |  |  | R
| kVA - Channel 60 | 60 | 6115 |  | 11078 | 11079 |  |  | R
| kVA - Channel 61 | 61 | 6116 |  | 11080 | 11081 |  |  | R
| kVA - Channel 62 | 62 | 6117 |  | 11082 | 11083 |  |  | R
| kVA - Channel 63 | 63 | 6118 |  | 11084 | 11085 |  |  | R
| kVA - Channel 64 | 64 | 6119 |  | 11086 | 11087 |  |  | R
| kVA - Channel 65 | 65 | 6120 |  | 11088 | 11089 |  |  | R
| kVA - Channel 66 | 66 | 6121 |  | 11090 | 11091 |  |  | R
| kVA - Channel 67 | 67 | 6122 |  | 11092 | 11093 |  |  | R
| kVA - Channel 68 | 68 | 6123 |  | 11094 | 11095 |  |  | R
| kVA - Channel 69 | 69 | 6124 |  | 11096 | 11097 |  |  | R
| kVA - Channel 70 | 70 | 6125 |  | 11098 | 11099 |  |  | R
| kVA - Channel 71 | 71 | 6126 |  | 11100 | 11101 |  |  | R
| kVA - Channel 72 | 72 | 6127 |  | 11102 | 11103 |  |  | R
| kVA - Channel 73 | 73 | 6128 |  | 11104 | 11105 |  |  | R
| kVA - Channel 74 | 74 | 6129 |  | 11106 | 11107 |  |  | R
| kVA - Channel 75 | 75 | 6130 |  | 11108 | 11109 |  |  | R
| kVA - Channel 76 | 76 | 6131 |  | 11110 | 11111 |  |  | R
| kVA - Channel 77 | 77 | 6132 |  | 11112 | 11113 |  |  | R
| kVA - Channel 78 | 78 | 6133 |  | 11114 | 11115 |  |  | R
| kVA - Channel 79 | 79 | 6134 |  | 11116 | 11117 |  |  | R
| kVA - Channel 80 | 80 | 6135 |  | 11118 | 11119 |  |  | R
| kVA - Channel 81 | 81 | 6136 |  | 11120 | 11121 |  |  | R
| kVA - Channel 82 | 82 | 6137 |  | 11122 | 11123 |  |  | R
| kVA - Channel 83 | 83 | 6138 |  | 11124 | 11125 |  |  | R
| kVA - Channel 84 | 84 | 6139 |  | 11126 | 11127 |  |  | R
| kVA - Channel 85 | 85 | 6140 |  | 11128 | 11129 |  |  | R
| kVA - Channel 86 | 86 | 6141 |  | 11130 | 11131 |  |  | R
| kVA - Channel 87 | 87 | 6142 |  | 11132 | 11133 |  |  | R
| kVA - Channel 88 | 88 | 6143 |  | 11134 | 11135 |  |  | R
| kVA - Channel 89 | 89 | 6144 |  | 11136 | 11137 |  |  | R
| kVA - Channel 90 | 90 | 6145 |  | 11138 | 11139 |  |  | R
| kVA - Channel 91 | 91 | 6146 |  | 11140 | 11141 |  |  | R
| kVA - Channel 92 | 92 | 6147 |  | 11142 | 11143 |  |  | R
| kVA - Channel 93 | 93 | 6148 |  | 11144 | 11145 |  |  | R
| kVA - Channel 94 | 94 | 6149 |  | 11146 | 11147 |  |  | R
| kVA - Channel 95 | 95 | 6150 |  | 11148 | 11149 |  |  | R
| kVA - Channel 96 | 96 | 6151 |  | 11150 | 11151 |  |  | R
| Current |  | 6152 | 6247 | 11152 | 11343 |  |  | R
| Current - Channel 1 | 1 | 6152 |  | 11152 | 11153 |  |  | R
| Current - Channel 2 | 2 | 6153 |  | 11154 | 11155 |  |  | R
| Current - Channel 3 | 3 | 6154 |  | 11156 | 11157 |  |  | R
| Current - Channel 4 | 4 | 6155 |  | 11158 | 11159 |  |  | R
| Current - Channel 5 | 5 | 6156 |  | 11160 | 11161 |  |  | R
| Current - Channel 6 | 6 | 6157 |  | 11162 | 11163 |  |  | R
| Current - Channel 7 | 7 | 6158 |  | 11164 | 11165 |  |  | R
| Current - Channel 8 | 8 | 6159 |  | 11166 | 11167 |  |  | R
| Current - Channel 9 | 9 | 6160 |  | 11168 | 11169 |  |  | R
| Current - Channel 10 | 10 | 6161 |  | 11170 | 11171 |  |  | R
| Current - Channel 11 | 11 | 6162 |  | 11172 | 11173 |  |  | R
| Current - Channel 12 | 12 | 6163 |  | 11174 | 11175 |  |  | R
| Current - Channel 13 | 13 | 6164 |  | 11176 | 11177 |  |  | R
| Current - Channel 14 | 14 | 6165 |  | 11178 | 11179 |  |  | R
| Current - Channel 15 | 15 | 6166 |  | 11180 | 11181 |  |  | R
| Current - Channel 16 | 16 | 6167 |  | 11182 | 11183 |  |  | R
| Current - Channel 17 | 17 | 6168 |  | 11184 | 11185 |  |  | R
| Current - Channel 18 | 18 | 6169 |  | 11186 | 11187 |  |  | R
| Current - Channel 19 | 19 | 6170 |  | 11188 | 11189 |  |  | R
| Current - Channel 20 | 20 | 6171 |  | 11190 | 11191 |  |  | R
| Current - Channel 21 | 21 | 6172 |  | 11192 | 11193 |  |  | R
| Current - Channel 22 | 22 | 6173 |  | 11194 | 11195 |  |  | R
| Current - Channel 23 | 23 | 6174 |  | 11196 | 11197 |  |  | R
| Current - Channel 24 | 24 | 6175 |  | 11198 | 11199 |  |  | R
| Current - Channel 25 | 25 | 6176 |  | 11200 | 11201 |  |  | R
| Current - Channel 26 | 26 | 6177 |  | 11202 | 11203 |  |  | R
| Current - Channel 27 | 27 | 6178 |  | 11204 | 11205 |  |  | R
| Current - Channel 28 | 28 | 6179 |  | 11206 | 11207 |  |  | R
| Current - Channel 29 | 29 | 6180 |  | 11208 | 11209 |  |  | R
| Current - Channel 30 | 30 | 6181 |  | 11210 | 11211 |  |  | R
| Current - Channel 31 | 31 | 6182 |  | 11212 | 11213 |  |  | R
| Current - Channel 32 | 32 | 6183 |  | 11214 | 11215 |  |  | R
| Current - Channel 33 | 33 | 6184 |  | 11216 | 11217 |  |  | R
| Current - Channel 34 | 34 | 6185 |  | 11218 | 11219 |  |  | R
| Current - Channel 35 | 35 | 6186 |  | 11220 | 11221 |  |  | R
| Current - Channel 36 | 36 | 6187 |  | 11222 | 11223 |  |  | R
| Current - Channel 37 | 37 | 6188 |  | 11224 | 11225 |  |  | R
| Current - Channel 38 | 38 | 6189 |  | 11226 | 11227 |  |  | R
| Current - Channel 39 | 39 | 6190 |  | 11228 | 11229 |  |  | R
| Current - Channel 40 | 40 | 6191 |  | 11230 | 11231 |  |  | R
| Current - Channel 41 | 41 | 6192 |  | 11232 | 11233 |  |  | R
| Current - Channel 42 | 42 | 6193 |  | 11234 | 11235 |  |  | R
| Current - Channel 43 | 43 | 6194 |  | 11236 | 11237 |  |  | R
| Current - Channel 44 | 44 | 6195 |  | 11238 | 11239 |  |  | R
| Current - Channel 45 | 45 | 6196 |  | 11240 | 11241 |  |  | R
| Current - Channel 46 | 46 | 6197 |  | 11242 | 11243 |  |  | R
| Current - Channel 47 | 47 | 6198 |  | 11244 | 11245 |  |  | R
| Current - Channel 48 | 48 | 6199 |  | 11246 | 11247 |  |  | R
| Current - Channel 49 | 49 | 6200 |  | 11248 | 11249 |  |  | R
| Current - Channel 50 | 50 | 6201 |  | 11250 | 11251 |  |  | R
| Current - Channel 51 | 51 | 6202 |  | 11252 | 11253 |  |  | R
| Current - Channel 52 | 52 | 6203 |  | 11254 | 11255 |  |  | R
| Current - Channel 53 | 53 | 6204 |  | 11256 | 11257 |  |  | R
| Current - Channel 54 | 54 | 6205 |  | 11258 | 11259 |  |  | R
| Current - Channel 55 | 55 | 6206 |  | 11260 | 11261 |  |  | R
| Current - Channel 56 | 56 | 6207 |  | 11262 | 11263 |  |  | R
| Current - Channel 57 | 57 | 6208 |  | 11264 | 11265 |  |  | R
| Current - Channel 58 | 58 | 6209 |  | 11266 | 11267 |  |  | R
| Current - Channel 59 | 59 | 6210 |  | 11268 | 11269 |  |  | R
| Current - Channel 60 | 60 | 6211 |  | 11270 | 11271 |  |  | R
| Current - Channel 61 | 61 | 6212 |  | 11272 | 11273 |  |  | R
| Current - Channel 62 | 62 | 6213 |  | 11274 | 11275 |  |  | R
| Current - Channel 63 | 63 | 6214 |  | 11276 | 11277 |  |  | R
| Current - Channel 64 | 64 | 6215 |  | 11278 | 11279 |  |  | R
| Current - Channel 65 | 65 | 6216 |  | 11280 | 11281 |  |  | R
| Current - Channel 66 | 66 | 6217 |  | 11282 | 11283 |  |  | R
| Current - Channel 67 | 67 | 6218 |  | 11284 | 11285 |  |  | R
| Current - Channel 68 | 68 | 6219 |  | 11286 | 11287 |  |  | R
| Current - Channel 69 | 69 | 6220 |  | 11288 | 11289 |  |  | R
| Current - Channel 70 | 70 | 6221 |  | 11290 | 11291 |  |  | R
| Current - Channel 71 | 71 | 6222 |  | 11292 | 11293 |  |  | R
| Current - Channel 72 | 72 | 6223 |  | 11294 | 11295 |  |  | R
| Current - Channel 73 | 73 | 6224 |  | 11296 | 11297 |  |  | R
| Current - Channel 74 | 74 | 6225 |  | 11298 | 11299 |  |  | R
| Current - Channel 75 | 75 | 6226 |  | 11300 | 11301 |  |  | R
| Current - Channel 76 | 76 | 6227 |  | 11302 | 11303 |  |  | R
| Current - Channel 77 | 77 | 6228 |  | 11304 | 11305 |  |  | R
| Current - Channel 78 | 78 | 6229 |  | 11306 | 11307 |  |  | R
| Current - Channel 79 | 79 | 6230 |  | 11308 | 11309 |  |  | R
| Current - Channel 80 | 80 | 6231 |  | 11310 | 11311 |  |  | R
| Current - Channel 81 | 81 | 6232 |  | 11312 | 11313 |  |  | R
| Current - Channel 82 | 82 | 6233 |  | 11314 | 11315 |  |  | R
| Current - Channel 83 | 83 | 6234 |  | 11316 | 11317 |  |  | R
| Current - Channel 84 | 84 | 6235 |  | 11318 | 11319 |  |  | R
| Current - Channel 85 | 85 | 6236 |  | 11320 | 11321 |  |  | R
| Current - Channel 86 | 86 | 6237 |  | 11322 | 11323 |  |  | R
| Current - Channel 87 | 87 | 6238 |  | 11324 | 11325 |  |  | R
| Current - Channel 88 | 88 | 6239 |  | 11326 | 11327 |  |  | R
| Current - Channel 89 | 89 | 6240 |  | 11328 | 11329 |  |  | R
| Current - Channel 90 | 90 | 6241 |  | 11330 | 11331 |  |  | R
| Current - Channel 91 | 91 | 6242 |  | 11332 | 11333 |  |  | R
| Current - Channel 92 | 92 | 6243 |  | 11334 | 11335 |  |  | R
| Current - Channel 93 | 93 | 6244 |  | 11336 | 11337 |  |  | R
| Current - Channel 94 | 94 | 6245 |  | 11338 | 11339 |  |  | R
| Current - Channel 95 | 95 | 6246 |  | 11340 | 11341 |  |  | R
| Current - Channel 96 | 96 | 6247 |  | 11342 | 11343 |  |  | R
| Power Factor |  | 6248 | 6343 | 11344 | 11535 |  |  | R
| Power Factor - Channel 1 | 1 | 6248 |  | 11344 | 11345 |  |  | R
| Power Factor - Channel 2 | 2 | 6249 |  | 11346 | 11347 |  |  | R
| Power Factor - Channel 3 | 3 | 6250 |  | 11348 | 11349 |  |  | R
| Power Factor - Channel 4 | 4 | 6251 |  | 11350 | 11351 |  |  | R
| Power Factor - Channel 5 | 5 | 6252 |  | 11352 | 11353 |  |  | R
| Power Factor - Channel 6 | 6 | 6253 |  | 11354 | 11355 |  |  | R
| Power Factor - Channel 7 | 7 | 6254 |  | 11356 | 11357 |  |  | R
| Power Factor - Channel 8 | 8 | 6255 |  | 11358 | 11359 |  |  | R
| Power Factor - Channel 9 | 9 | 6256 |  | 11360 | 11361 |  |  | R
| Power Factor - Channel 10 | 10 | 6257 |  | 11362 | 11363 |  |  | R
| Power Factor - Channel 11 | 11 | 6258 |  | 11364 | 11365 |  |  | R
| Power Factor - Channel 12 | 12 | 6259 |  | 11366 | 11367 |  |  | R
| Power Factor - Channel 13 | 13 | 6260 |  | 11368 | 11369 |  |  | R
| Power Factor - Channel 14 | 14 | 6261 |  | 11370 | 11371 |  |  | R
| Power Factor - Channel 15 | 15 | 6262 |  | 11372 | 11373 |  |  | R
| Power Factor - Channel 16 | 16 | 6263 |  | 11374 | 11375 |  |  | R
| Power Factor - Channel 17 | 17 | 6264 |  | 11376 | 11377 |  |  | R
| Power Factor - Channel 18 | 18 | 6265 |  | 11378 | 11379 |  |  | R
| Power Factor - Channel 19 | 19 | 6266 |  | 11380 | 11381 |  |  | R
| Power Factor - Channel 20 | 20 | 6267 |  | 11382 | 11383 |  |  | R
| Power Factor - Channel 21 | 21 | 6268 |  | 11384 | 11385 |  |  | R
| Power Factor - Channel 22 | 22 | 6269 |  | 11386 | 11387 |  |  | R
| Power Factor - Channel 23 | 23 | 6270 |  | 11388 | 11389 |  |  | R
| Power Factor - Channel 24 | 24 | 6271 |  | 11390 | 11391 |  |  | R
| Power Factor - Channel 25 | 25 | 6272 |  | 11392 | 11393 |  |  | R
| Power Factor - Channel 26 | 26 | 6273 |  | 11394 | 11395 |  |  | R
| Power Factor - Channel 27 | 27 | 6274 |  | 11396 | 11397 |  |  | R
| Power Factor - Channel 28 | 28 | 6275 |  | 11398 | 11399 |  |  | R
| Power Factor - Channel 29 | 29 | 6276 |  | 11400 | 11401 |  |  | R
| Power Factor - Channel 30 | 30 | 6277 |  | 11402 | 11403 |  |  | R
| Power Factor - Channel 31 | 31 | 6278 |  | 11404 | 11405 |  |  | R
| Power Factor - Channel 32 | 32 | 6279 |  | 11406 | 11407 |  |  | R
| Power Factor - Channel 33 | 33 | 6280 |  | 11408 | 11409 |  |  | R
| Power Factor - Channel 34 | 34 | 6281 |  | 11410 | 11411 |  |  | R
| Power Factor - Channel 35 | 35 | 6282 |  | 11412 | 11413 |  |  | R
| Power Factor - Channel 36 | 36 | 6283 |  | 11414 | 11415 |  |  | R
| Power Factor - Channel 37 | 37 | 6284 |  | 11416 | 11417 |  |  | R
| Power Factor - Channel 38 | 38 | 6285 |  | 11418 | 11419 |  |  | R
| Power Factor - Channel 39 | 39 | 6286 |  | 11420 | 11421 |  |  | R
| Power Factor - Channel 40 | 40 | 6287 |  | 11422 | 11423 |  |  | R
| Power Factor - Channel 41 | 41 | 6288 |  | 11424 | 11425 |  |  | R
| Power Factor - Channel 42 | 42 | 6289 |  | 11426 | 11427 |  |  | R
| Power Factor - Channel 43 | 43 | 6290 |  | 11428 | 11429 |  |  | R
| Power Factor - Channel 44 | 44 | 6291 |  | 11430 | 11431 |  |  | R
| Power Factor - Channel 45 | 45 | 6292 |  | 11432 | 11433 |  |  | R
| Power Factor - Channel 46 | 46 | 6293 |  | 11434 | 11435 |  |  | R
| Power Factor - Channel 47 | 47 | 6294 |  | 11436 | 11437 |  |  | R
| Power Factor - Channel 48 | 48 | 6295 |  | 11438 | 11439 |  |  | R
| Power Factor - Channel 49 | 49 | 6296 |  | 11440 | 11441 |  |  | R
| Power Factor - Channel 50 | 50 | 6297 |  | 11442 | 11443 |  |  | R
| Power Factor - Channel 51 | 51 | 6298 |  | 11444 | 11445 |  |  | R
| Power Factor - Channel 52 | 52 | 6299 |  | 11446 | 11447 |  |  | R
| Power Factor - Channel 53 | 53 | 6300 |  | 11448 | 11449 |  |  | R
| Power Factor - Channel 54 | 54 | 6301 |  | 11450 | 11451 |  |  | R
| Power Factor - Channel 55 | 55 | 6302 |  | 11452 | 11453 |  |  | R
| Power Factor - Channel 56 | 56 | 6303 |  | 11454 | 11455 |  |  | R
| Power Factor - Channel 57 | 57 | 6304 |  | 11456 | 11457 |  |  | R
| Power Factor - Channel 58 | 58 | 6305 |  | 11458 | 11459 |  |  | R
| Power Factor - Channel 59 | 59 | 6306 |  | 11460 | 11461 |  |  | R
| Power Factor - Channel 60 | 60 | 6307 |  | 11462 | 11463 |  |  | R
| Power Factor - Channel 61 | 61 | 6308 |  | 11464 | 11465 |  |  | R
| Power Factor - Channel 62 | 62 | 6309 |  | 11466 | 11467 |  |  | R
| Power Factor - Channel 63 | 63 | 6310 |  | 11468 | 11469 |  |  | R
| Power Factor - Channel 64 | 64 | 6311 |  | 11470 | 11471 |  |  | R
| Power Factor - Channel 65 | 65 | 6312 |  | 11472 | 11473 |  |  | R
| Power Factor - Channel 66 | 66 | 6313 |  | 11474 | 11475 |  |  | R
| Power Factor - Channel 67 | 67 | 6314 |  | 11476 | 11477 |  |  | R
| Power Factor - Channel 68 | 68 | 6315 |  | 11478 | 11479 |  |  | R
| Power Factor - Channel 69 | 69 | 6316 |  | 11480 | 11481 |  |  | R
| Power Factor - Channel 70 | 70 | 6317 |  | 11482 | 11483 |  |  | R
| Power Factor - Channel 71 | 71 | 6318 |  | 11484 | 11485 |  |  | R
| Power Factor - Channel 72 | 72 | 6319 |  | 11486 | 11487 |  |  | R
| Power Factor - Channel 73 | 73 | 6320 |  | 11488 | 11489 |  |  | R
| Power Factor - Channel 74 | 74 | 6321 |  | 11490 | 11491 |  |  | R
| Power Factor - Channel 75 | 75 | 6322 |  | 11492 | 11493 |  |  | R
| Power Factor - Channel 76 | 76 | 6323 |  | 11494 | 11495 |  |  | R
| Power Factor - Channel 77 | 77 | 6324 |  | 11496 | 11497 |  |  | R
| Power Factor - Channel 78 | 78 | 6325 |  | 11498 | 11499 |  |  | R
| Power Factor - Channel 79 | 79 | 6326 |  | 11500 | 11501 |  |  | R
| Power Factor - Channel 80 | 80 | 6327 |  | 11502 | 11503 |  |  | R
| Power Factor - Channel 81 | 81 | 6328 |  | 11504 | 11505 |  |  | R
| Power Factor - Channel 82 | 82 | 6329 |  | 11506 | 11507 |  |  | R
| Power Factor - Channel 83 | 83 | 6330 |  | 11508 | 11509 |  |  | R
| Power Factor - Channel 84 | 84 | 6331 |  | 11510 | 11511 |  |  | R
| Power Factor - Channel 85 | 85 | 6332 |  | 11512 | 11513 |  |  | R
| Power Factor - Channel 86 | 86 | 6333 |  | 11514 | 11515 |  |  | R
| Power Factor - Channel 87 | 87 | 6334 |  | 11516 | 11517 |  |  | R
| Power Factor - Channel 88 | 88 | 6335 |  | 11518 | 11519 |  |  | R
| Power Factor - Channel 89 | 89 | 6336 |  | 11520 | 11521 |  |  | R
| Power Factor - Channel 90 | 90 | 6337 |  | 11522 | 11523 |  |  | R
| Power Factor - Channel 91 | 91 | 6338 |  | 11524 | 11525 |  |  | R
| Power Factor - Channel 92 | 92 | 6339 |  | 11526 | 11527 |  |  | R
| Power Factor - Channel 93 | 93 | 6340 |  | 11528 | 11529 |  |  | R
| Power Factor - Channel 94 | 94 | 6341 |  | 11530 | 11531 |  |  | R
| Power Factor - Channel 95 | 95 | 6342 |  | 11532 | 11533 |  |  | R
| Power Factor - Channel 96 | 96 | 6343 |  | 11534 | 11535 |  |  | R
| Current Angle |  | 6344 | 6439 | 11536 | 11727 |  |  | R
| Current Angle- Channel 1 | 1 | 6344 |  | 11536 | 11537 |  |  | R
| Current Angle- Channel 2 | 2 | 6345 |  | 11538 | 11539 |  |  | R
| Current Angle- Channel 3 | 3 | 6346 |  | 11540 | 11541 |  |  | R
| Current Angle- Channel 4 | 4 | 6347 |  | 11542 | 11543 |  |  | R
| Current Angle- Channel 5 | 5 | 6348 |  | 11544 | 11545 |  |  | R
| Current Angle- Channel 6 | 6 | 6349 |  | 11546 | 11547 |  |  | R
| Current Angle- Channel 7 | 7 | 6350 |  | 11548 | 11549 |  |  | R
| Current Angle- Channel 8 | 8 | 6351 |  | 11550 | 11551 |  |  | R
| Current Angle- Channel 9 | 9 | 6352 |  | 11552 | 11553 |  |  | R
| Current Angle- Channel 10 | 10 | 6353 |  | 11554 | 11555 |  |  | R
| Current Angle- Channel 11 | 11 | 6354 |  | 11556 | 11557 |  |  | R
| Current Angle- Channel 12 | 12 | 6355 |  | 11558 | 11559 |  |  | R
| Current Angle- Channel 13 | 13 | 6356 |  | 11560 | 11561 |  |  | R
| Current Angle- Channel 14 | 14 | 6357 |  | 11562 | 11563 |  |  | R
| Current Angle- Channel 15 | 15 | 6358 |  | 11564 | 11565 |  |  | R
| Current Angle- Channel 16 | 16 | 6359 |  | 11566 | 11567 |  |  | R
| Current Angle- Channel 17 | 17 | 6360 |  | 11568 | 11569 |  |  | R
| Current Angle- Channel 18 | 18 | 6361 |  | 11570 | 11571 |  |  | R
| Current Angle- Channel 19 | 19 | 6362 |  | 11572 | 11573 |  |  | R
| Current Angle- Channel 20 | 20 | 6363 |  | 11574 | 11575 |  |  | R
| Current Angle- Channel 21 | 21 | 6364 |  | 11576 | 11577 |  |  | R
| Current Angle- Channel 22 | 22 | 6365 |  | 11578 | 11579 |  |  | R
| Current Angle- Channel 23 | 23 | 6366 |  | 11580 | 11581 |  |  | R
| Current Angle- Channel 24 | 24 | 6367 |  | 11582 | 11583 |  |  | R
| Current Angle- Channel 25 | 25 | 6368 |  | 11584 | 11585 |  |  | R
| Current Angle- Channel 26 | 26 | 6369 |  | 11586 | 11587 |  |  | R
| Current Angle- Channel 27 | 27 | 6370 |  | 11588 | 11589 |  |  | R
| Current Angle- Channel 28 | 28 | 6371 |  | 11590 | 11591 |  |  | R
| Current Angle- Channel 29 | 29 | 6372 |  | 11592 | 11593 |  |  | R
| Current Angle- Channel 30 | 30 | 6373 |  | 11594 | 11595 |  |  | R
| Current Angle- Channel 31 | 31 | 6374 |  | 11596 | 11597 |  |  | R
| Current Angle- Channel 32 | 32 | 6375 |  | 11598 | 11599 |  |  | R
| Current Angle- Channel 33 | 33 | 6376 |  | 11600 | 11601 |  |  | R
| Current Angle- Channel 34 | 34 | 6377 |  | 11602 | 11603 |  |  | R
| Current Angle- Channel 35 | 35 | 6378 |  | 11604 | 11605 |  |  | R
| Current Angle- Channel 36 | 36 | 6379 |  | 11606 | 11607 |  |  | R
| Current Angle- Channel 37 | 37 | 6380 |  | 11608 | 11609 |  |  | R
| Current Angle- Channel 38 | 38 | 6381 |  | 11610 | 11611 |  |  | R
| Current Angle- Channel 39 | 39 | 6382 |  | 11612 | 11613 |  |  | R
| Current Angle- Channel 40 | 40 | 6383 |  | 11614 | 11615 |  |  | R
| Current Angle- Channel 41 | 41 | 6384 |  | 11616 | 11617 |  |  | R
| Current Angle- Channel 42 | 42 | 6385 |  | 11618 | 11619 |  |  | R
| Current Angle- Channel 43 | 43 | 6386 |  | 11620 | 11621 |  |  | R
| Current Angle- Channel 44 | 44 | 6387 |  | 11622 | 11623 |  |  | R
| Current Angle- Channel 45 | 45 | 6388 |  | 11624 | 11625 |  |  | R
| Current Angle- Channel 46 | 46 | 6389 |  | 11626 | 11627 |  |  | R
| Current Angle- Channel 47 | 47 | 6390 |  | 11628 | 11629 |  |  | R
| Current Angle- Channel 48 | 48 | 6391 |  | 11630 | 11631 |  |  | R
| Current Angle- Channel 49 | 49 | 6392 |  | 11632 | 11633 |  |  | R
| Current Angle- Channel 50 | 50 | 6393 |  | 11634 | 11635 |  |  | R
| Current Angle- Channel 51 | 51 | 6394 |  | 11636 | 11637 |  |  | R
| Current Angle- Channel 52 | 52 | 6395 |  | 11638 | 11639 |  |  | R
| Current Angle- Channel 53 | 53 | 6396 |  | 11640 | 11641 |  |  | R
| Current Angle- Channel 54 | 54 | 6397 |  | 11642 | 11643 |  |  | R
| Current Angle- Channel 55 | 55 | 6398 |  | 11644 | 11645 |  |  | R
| Current Angle- Channel 56 | 56 | 6399 |  | 11646 | 11647 |  |  | R
| Current Angle- Channel 57 | 57 | 6400 |  | 11648 | 11649 |  |  | R
| Current Angle- Channel 58 | 58 | 6401 |  | 11650 | 11651 |  |  | R
| Current Angle- Channel 59 | 59 | 6402 |  | 11652 | 11653 |  |  | R
| Current Angle- Channel 60 | 60 | 6403 |  | 11654 | 11655 |  |  | R
| Current Angle- Channel 61 | 61 | 6404 |  | 11656 | 11657 |  |  | R
| Current Angle- Channel 62 | 62 | 6405 |  | 11658 | 11659 |  |  | R
| Current Angle- Channel 63 | 63 | 6406 |  | 11660 | 11661 |  |  | R
| Current Angle- Channel 64 | 64 | 6407 |  | 11662 | 11663 |  |  | R
| Current Angle- Channel 65 | 65 | 6408 |  | 11664 | 11665 |  |  | R
| Current Angle- Channel 66 | 66 | 6409 |  | 11666 | 11667 |  |  | R
| Current Angle- Channel 67 | 67 | 6410 |  | 11668 | 11669 |  |  | R
| Current Angle- Channel 68 | 68 | 6411 |  | 11670 | 11671 |  |  | R
| Current Angle- Channel 69 | 69 | 6412 |  | 11672 | 11673 |  |  | R
| Current Angle- Channel 70 | 70 | 6413 |  | 11674 | 11675 |  |  | R
| Current Angle- Channel 71 | 71 | 6414 |  | 11676 | 11677 |  |  | R
| Current Angle- Channel 72 | 72 | 6415 |  | 11678 | 11679 |  |  | R
| Current Angle- Channel 73 | 73 | 6416 |  | 11680 | 11681 |  |  | R
| Current Angle- Channel 74 | 74 | 6417 |  | 11682 | 11683 |  |  | R
| Current Angle- Channel 75 | 75 | 6418 |  | 11684 | 11685 |  |  | R
| Current Angle- Channel 76 | 76 | 6419 |  | 11686 | 11687 |  |  | R
| Current Angle- Channel 77 | 77 | 6420 |  | 11688 | 11689 |  |  | R
| Current Angle- Channel 78 | 78 | 6421 |  | 11690 | 11691 |  |  | R
| Current Angle- Channel 79 | 79 | 6422 |  | 11692 | 11693 |  |  | R
| Current Angle- Channel 80 | 80 | 6423 |  | 11694 | 11695 |  |  | R
| Current Angle- Channel 81 | 81 | 6424 |  | 11696 | 11697 |  |  | R
| Current Angle- Channel 82 | 82 | 6425 |  | 11698 | 11699 |  |  | R
| Current Angle- Channel 83 | 83 | 6426 |  | 11700 | 11701 |  |  | R
| Current Angle- Channel 84 | 84 | 6427 |  | 11702 | 11703 |  |  | R
| Current Angle- Channel 85 | 85 | 6428 |  | 11704 | 11705 |  |  | R
| Current Angle- Channel 86 | 86 | 6429 |  | 11706 | 11707 |  |  | R
| Current Angle- Channel 87 | 87 | 6430 |  | 11708 | 11709 |  |  | R
| Current Angle- Channel 88 | 88 | 6431 |  | 11710 | 11711 |  |  | R
| Current Angle- Channel 89 | 89 | 6432 |  | 11712 | 11713 |  |  | R
| Current Angle- Channel 90 | 90 | 6433 |  | 11714 | 11715 |  |  | R
| Current Angle- Channel 91 | 91 | 6434 |  | 11716 | 11717 |  |  | R
| Current Angle- Channel 92 | 92 | 6435 |  | 11718 | 11719 |  |  | R
| Current Angle- Channel 93 | 93 | 6436 |  | 11720 | 11721 |  |  | R
| Current Angle- Channel 94 | 94 | 6437 |  | 11722 | 11723 |  |  | R
| Current Angle- Channel 95 | 95 | 6438 |  | 11724 | 11725 |  |  | R
| Current Angle- Channel 96 | 96 | 6439 |  | 11726 | 11727 |  |  | R
| Percent THD |  | 6440 | 6535 | 11728 | 11919 |  |  | R
| Percent THD - Channel 1 | 1 | 6440 |  | 11728 | 11729 |  |  | R
| Percent THD - Channel 2 | 2 | 6441 |  | 11730 | 11731 |  |  | R
| Percent THD - Channel 3 | 3 | 6442 |  | 11732 | 11733 |  |  | R
| Percent THD - Channel 4 | 4 | 6443 |  | 11734 | 11735 |  |  | R
| Percent THD - Channel 5 | 5 | 6444 |  | 11736 | 11737 |  |  | R
| Percent THD - Channel 6 | 6 | 6445 |  | 11738 | 11739 |  |  | R
| Percent THD - Channel 7 | 7 | 6446 |  | 11740 | 11741 |  |  | R
| Percent THD - Channel 8 | 8 | 6447 |  | 11742 | 11743 |  |  | R
| Percent THD - Channel 9 | 9 | 6448 |  | 11744 | 11745 |  |  | R
| Percent THD - Channel 10 | 10 | 6449 |  | 11746 | 11747 |  |  | R
| Percent THD - Channel 11 | 11 | 6450 |  | 11748 | 11749 |  |  | R
| Percent THD - Channel 12 | 12 | 6451 |  | 11750 | 11751 |  |  | R
| Percent THD - Channel 13 | 13 | 6452 |  | 11752 | 11753 |  |  | R
| Percent THD - Channel 14 | 14 | 6453 |  | 11754 | 11755 |  |  | R
| Percent THD - Channel 15 | 15 | 6454 |  | 11756 | 11757 |  |  | R
| Percent THD - Channel 16 | 16 | 6455 |  | 11758 | 11759 |  |  | R
| Percent THD - Channel 17 | 17 | 6456 |  | 11760 | 11761 |  |  | R
| Percent THD - Channel 18 | 18 | 6457 |  | 11762 | 11763 |  |  | R
| Percent THD - Channel 19 | 19 | 6458 |  | 11764 | 11765 |  |  | R
| Percent THD - Channel 20 | 20 | 6459 |  | 11766 | 11767 |  |  | R
| Percent THD - Channel 21 | 21 | 6460 |  | 11768 | 11769 |  |  | R
| Percent THD - Channel 22 | 22 | 6461 |  | 11770 | 11771 |  |  | R
| Percent THD - Channel 23 | 23 | 6462 |  | 11772 | 11773 |  |  | R
| Percent THD - Channel 24 | 24 | 6463 |  | 11774 | 11775 |  |  | R
| Percent THD - Channel 25 | 25 | 6464 |  | 11776 | 11777 |  |  | R
| Percent THD - Channel 26 | 26 | 6465 |  | 11778 | 11779 |  |  | R
| Percent THD - Channel 27 | 27 | 6466 |  | 11780 | 11781 |  |  | R
| Percent THD - Channel 28 | 28 | 6467 |  | 11782 | 11783 |  |  | R
| Percent THD - Channel 29 | 29 | 6468 |  | 11784 | 11785 |  |  | R
| Percent THD - Channel 30 | 30 | 6469 |  | 11786 | 11787 |  |  | R
| Percent THD - Channel 31 | 31 | 6470 |  | 11788 | 11789 |  |  | R
| Percent THD - Channel 32 | 32 | 6471 |  | 11790 | 11791 |  |  | R
| Percent THD - Channel 33 | 33 | 6472 |  | 11792 | 11793 |  |  | R
| Percent THD - Channel 34 | 34 | 6473 |  | 11794 | 11795 |  |  | R
| Percent THD - Channel 35 | 35 | 6474 |  | 11796 | 11797 |  |  | R
| Percent THD - Channel 36 | 36 | 6475 |  | 11798 | 11799 |  |  | R
| Percent THD - Channel 37 | 37 | 6476 |  | 11800 | 11801 |  |  | R
| Percent THD - Channel 38 | 38 | 6477 |  | 11802 | 11803 |  |  | R
| Percent THD - Channel 39 | 39 | 6478 |  | 11804 | 11805 |  |  | R
| Percent THD - Channel 40 | 40 | 6479 |  | 11806 | 11807 |  |  | R
| Percent THD - Channel 41 | 41 | 6480 |  | 11808 | 11809 |  |  | R
| Percent THD - Channel 42 | 42 | 6481 |  | 11810 | 11811 |  |  | R
| Percent THD - Channel 43 | 43 | 6482 |  | 11812 | 11813 |  |  | R
| Percent THD - Channel 44 | 44 | 6483 |  | 11814 | 11815 |  |  | R
| Percent THD - Channel 45 | 45 | 6484 |  | 11816 | 11817 |  |  | R
| Percent THD - Channel 46 | 46 | 6485 |  | 11818 | 11819 |  |  | R
| Percent THD - Channel 47 | 47 | 6486 |  | 11820 | 11821 |  |  | R
| Percent THD - Channel 48 | 48 | 6487 |  | 11822 | 11823 |  |  | R
| Percent THD - Channel 49 | 49 | 6488 |  | 11824 | 11825 |  |  | R
| Percent THD - Channel 50 | 50 | 6489 |  | 11826 | 11827 |  |  | R
| Percent THD - Channel 51 | 51 | 6490 |  | 11828 | 11829 |  |  | R
| Percent THD - Channel 52 | 52 | 6491 |  | 11830 | 11831 |  |  | R
| Percent THD - Channel 53 | 53 | 6492 |  | 11832 | 11833 |  |  | R
| Percent THD - Channel 54 | 54 | 6493 |  | 11834 | 11835 |  |  | R
| Percent THD - Channel 55 | 55 | 6494 |  | 11836 | 11837 |  |  | R
| Percent THD - Channel 56 | 56 | 6495 |  | 11838 | 11839 |  |  | R
| Percent THD - Channel 57 | 57 | 6496 |  | 11840 | 11841 |  |  | R
| Percent THD - Channel 58 | 58 | 6497 |  | 11842 | 11843 |  |  | R
| Percent THD - Channel 59 | 59 | 6498 |  | 11844 | 11845 |  |  | R
| Percent THD - Channel 60 | 60 | 6499 |  | 11846 | 11847 |  |  | R
| Percent THD - Channel 61 | 61 | 6500 |  | 11848 | 11849 |  |  | R
| Percent THD - Channel 62 | 62 | 6501 |  | 11850 | 11851 |  |  | R
| Percent THD - Channel 63 | 63 | 6502 |  | 11852 | 11853 |  |  | R
| Percent THD - Channel 64 | 64 | 6503 |  | 11854 | 11855 |  |  | R
| Percent THD - Channel 65 | 65 | 6504 |  | 11856 | 11857 |  |  | R
| Percent THD - Channel 66 | 66 | 6505 |  | 11858 | 11859 |  |  | R
| Percent THD - Channel 67 | 67 | 6506 |  | 11860 | 11861 |  |  | R
| Percent THD - Channel 68 | 68 | 6507 |  | 11862 | 11863 |  |  | R
| Percent THD - Channel 69 | 69 | 6508 |  | 11864 | 11865 |  |  | R
| Percent THD - Channel 70 | 70 | 6509 |  | 11866 | 11867 |  |  | R
| Percent THD - Channel 71 | 71 | 6510 |  | 11868 | 11869 |  |  | R
| Percent THD - Channel 72 | 72 | 6511 |  | 11870 | 11871 |  |  | R
| Percent THD - Channel 73 | 73 | 6512 |  | 11872 | 11873 |  |  | R
| Percent THD - Channel 74 | 74 | 6513 |  | 11874 | 11875 |  |  | R
| Percent THD - Channel 75 | 75 | 6514 |  | 11876 | 11877 |  |  | R
| Percent THD - Channel 76 | 76 | 6515 |  | 11878 | 11879 |  |  | R
| Percent THD - Channel 77 | 77 | 6516 |  | 11880 | 11881 |  |  | R
| Percent THD - Channel 78 | 78 | 6517 |  | 11882 | 11883 |  |  | R
| Percent THD - Channel 79 | 79 | 6518 |  | 11884 | 11885 |  |  | R
| Percent THD - Channel 80 | 80 | 6519 |  | 11886 | 11887 |  |  | R
| Percent THD - Channel 81 | 81 | 6520 |  | 11888 | 11889 |  |  | R
| Percent THD - Channel 82 | 82 | 6521 |  | 11890 | 11891 |  |  | R
| Percent THD - Channel 83 | 83 | 6522 |  | 11892 | 11893 |  |  | R
| Percent THD - Channel 84 | 84 | 6523 |  | 11894 | 11895 |  |  | R
| Percent THD - Channel 85 | 85 | 6524 |  | 11896 | 11897 |  |  | R
| Percent THD - Channel 86 | 86 | 6525 |  | 11898 | 11899 |  |  | R
| Percent THD - Channel 87 | 87 | 6526 |  | 11900 | 11901 |  |  | R
| Percent THD - Channel 88 | 88 | 6527 |  | 11902 | 11903 |  |  | R
| Percent THD - Channel 89 | 89 | 6528 |  | 11904 | 11905 |  |  | R
| Percent THD - Channel 90 | 90 | 6529 |  | 11906 | 11907 |  |  | R
| Percent THD - Channel 91 | 91 | 6530 |  | 11908 | 11909 |  |  | R
| Percent THD - Channel 92 | 92 | 6531 |  | 11910 | 11911 |  |  | R
| Percent THD - Channel 93 | 93 | 6532 |  | 11912 | 11913 |  |  | R
| Percent THD - Channel 94 | 94 | 6533 |  | 11914 | 11915 |  |  | R
| Percent THD - Channel 95 | 95 | 6534 |  | 11916 | 11917 |  |  | R
| Percent THD - Channel 96 | 96 | 6535 |  | 11918 | 11919 |  |  | R
| Max Current |  | 6536 | 6631 | 11920 | 12111 |  |  | R | NV
| Max Current- Channel 1 | 1 | 6536 |  | 11920 | 11921 |  |  | R | NV
| Max Current- Channel 2 | 2 | 6537 |  | 11922 | 11923 |  |  | R | NV
| Max Current- Channel 3 | 3 | 6538 |  | 11924 | 11925 |  |  | R | NV
| Max Current- Channel 4 | 4 | 6539 |  | 11926 | 11927 |  |  | R | NV
| Max Current- Channel 5 | 5 | 6540 |  | 11928 | 11929 |  |  | R | NV
| Max Current- Channel 6 | 6 | 6541 |  | 11930 | 11931 |  |  | R | NV
| Max Current- Channel 7 | 7 | 6542 |  | 11932 | 11933 |  |  | R | NV
| Max Current- Channel 8 | 8 | 6543 |  | 11934 | 11935 |  |  | R | NV
| Max Current- Channel 9 | 9 | 6544 |  | 11936 | 11937 |  |  | R | NV
| Max Current- Channel 10 | 10 | 6545 |  | 11938 | 11939 |  |  | R | NV
| Max Current- Channel 11 | 11 | 6546 |  | 11940 | 11941 |  |  | R | NV
| Max Current- Channel 12 | 12 | 6547 |  | 11942 | 11943 |  |  | R | NV
| Max Current- Channel 13 | 13 | 6548 |  | 11944 | 11945 |  |  | R | NV
| Max Current- Channel 14 | 14 | 6549 |  | 11946 | 11947 |  |  | R | NV
| Max Current- Channel 15 | 15 | 6550 |  | 11948 | 11949 |  |  | R | NV
| Max Current- Channel 16 | 16 | 6551 |  | 11950 | 11951 |  |  | R | NV
| Max Current- Channel 17 | 17 | 6552 |  | 11952 | 11953 |  |  | R | NV
| Max Current- Channel 18 | 18 | 6553 |  | 11954 | 11955 |  |  | R | NV
| Max Current- Channel 19 | 19 | 6554 |  | 11956 | 11957 |  |  | R | NV
| Max Current- Channel 20 | 20 | 6555 |  | 11958 | 11959 |  |  | R | NV
| Max Current- Channel 21 | 21 | 6556 |  | 11960 | 11961 |  |  | R | NV
| Max Current- Channel 22 | 22 | 6557 |  | 11962 | 11963 |  |  | R | NV
| Max Current- Channel 23 | 23 | 6558 |  | 11964 | 11965 |  |  | R | NV
| Max Current- Channel 24 | 24 | 6559 |  | 11966 | 11967 |  |  | R | NV
| Max Current- Channel 25 | 25 | 6560 |  | 11968 | 11969 |  |  | R | NV
| Max Current- Channel 26 | 26 | 6561 |  | 11970 | 11971 |  |  | R | NV
| Max Current- Channel 27 | 27 | 6562 |  | 11972 | 11973 |  |  | R | NV
| Max Current- Channel 28 | 28 | 6563 |  | 11974 | 11975 |  |  | R | NV
| Max Current- Channel 29 | 29 | 6564 |  | 11976 | 11977 |  |  | R | NV
| Max Current- Channel 30 | 30 | 6565 |  | 11978 | 11979 |  |  | R | NV
| Max Current- Channel 31 | 31 | 6566 |  | 11980 | 11981 |  |  | R | NV
| Max Current- Channel 32 | 32 | 6567 |  | 11982 | 11983 |  |  | R | NV
| Max Current- Channel 33 | 33 | 6568 |  | 11984 | 11985 |  |  | R | NV
| Max Current- Channel 34 | 34 | 6569 |  | 11986 | 11987 |  |  | R | NV
| Max Current- Channel 35 | 35 | 6570 |  | 11988 | 11989 |  |  | R | NV
| Max Current- Channel 36 | 36 | 6571 |  | 11990 | 11991 |  |  | R | NV
| Max Current- Channel 37 | 37 | 6572 |  | 11992 | 11993 |  |  | R | NV
| Max Current- Channel 38 | 38 | 6573 |  | 11994 | 11995 |  |  | R | NV
| Max Current- Channel 39 | 39 | 6574 |  | 11996 | 11997 |  |  | R | NV
| Max Current- Channel 40 | 40 | 6575 |  | 11998 | 11999 |  |  | R | NV
| Max Current- Channel 41 | 41 | 6576 |  | 12000 | 12001 |  |  | R | NV
| Max Current- Channel 42 | 42 | 6577 |  | 12002 | 12003 |  |  | R | NV
| Max Current- Channel 43 | 43 | 6578 |  | 12004 | 12005 |  |  | R | NV
| Max Current- Channel 44 | 44 | 6579 |  | 12006 | 12007 |  |  | R | NV
| Max Current- Channel 45 | 45 | 6580 |  | 12008 | 12009 |  |  | R | NV
| Max Current- Channel 46 | 46 | 6581 |  | 12010 | 12011 |  |  | R | NV
| Max Current- Channel 47 | 47 | 6582 |  | 12012 | 12013 |  |  | R | NV
| Max Current- Channel 48 | 48 | 6583 |  | 12014 | 12015 |  |  | R | NV
| Max Current- Channel 49 | 49 | 6584 |  | 12016 | 12017 |  |  | R | NV
| Max Current- Channel 50 | 50 | 6585 |  | 12018 | 12019 |  |  | R | NV
| Max Current- Channel 51 | 51 | 6586 |  | 12020 | 12021 |  |  | R | NV
| Max Current- Channel 52 | 52 | 6587 |  | 12022 | 12023 |  |  | R | NV
| Max Current- Channel 53 | 53 | 6588 |  | 12024 | 12025 |  |  | R | NV
| Max Current- Channel 54 | 54 | 6589 |  | 12026 | 12027 |  |  | R | NV
| Max Current- Channel 55 | 55 | 6590 |  | 12028 | 12029 |  |  | R | NV
| Max Current- Channel 56 | 56 | 6591 |  | 12030 | 12031 |  |  | R | NV
| Max Current- Channel 57 | 57 | 6592 |  | 12032 | 12033 |  |  | R | NV
| Max Current- Channel 58 | 58 | 6593 |  | 12034 | 12035 |  |  | R | NV
| Max Current- Channel 59 | 59 | 6594 |  | 12036 | 12037 |  |  | R | NV
| Max Current- Channel 60 | 60 | 6595 |  | 12038 | 12039 |  |  | R | NV
| Max Current- Channel 61 | 61 | 6596 |  | 12040 | 12041 |  |  | R | NV
| Max Current- Channel 62 | 62 | 6597 |  | 12042 | 12043 |  |  | R | NV
| Max Current- Channel 63 | 63 | 6598 |  | 12044 | 12045 |  |  | R | NV
| Max Current- Channel 64 | 64 | 6599 |  | 12046 | 12047 |  |  | R | NV
| Max Current- Channel 65 | 65 | 6600 |  | 12048 | 12049 |  |  | R | NV
| Max Current- Channel 66 | 66 | 6601 |  | 12050 | 12051 |  |  | R | NV
| Max Current- Channel 67 | 67 | 6602 |  | 12052 | 12053 |  |  | R | NV
| Max Current- Channel 68 | 68 | 6603 |  | 12054 | 12055 |  |  | R | NV
| Max Current- Channel 69 | 69 | 6604 |  | 12056 | 12057 |  |  | R | NV
| Max Current- Channel 70 | 70 | 6605 |  | 12058 | 12059 |  |  | R | NV
| Max Current- Channel 71 | 71 | 6606 |  | 12060 | 12061 |  |  | R | NV
| Max Current- Channel 72 | 72 | 6607 |  | 12062 | 12063 |  |  | R | NV
| Max Current- Channel 73 | 73 | 6608 |  | 12064 | 12065 |  |  | R | NV
| Max Current- Channel 74 | 74 | 6609 |  | 12066 | 12067 |  |  | R | NV
| Max Current- Channel 75 | 75 | 6610 |  | 12068 | 12069 |  |  | R | NV
| Max Current- Channel 76 | 76 | 6611 |  | 12070 | 12071 |  |  | R | NV
| Max Current- Channel 77 | 77 | 6612 |  | 12072 | 12073 |  |  | R | NV
| Max Current- Channel 78 | 78 | 6613 |  | 12074 | 12075 |  |  | R | NV
| Max Current- Channel 79 | 79 | 6614 |  | 12076 | 12077 |  |  | R | NV
| Max Current- Channel 80 | 80 | 6615 |  | 12078 | 12079 |  |  | R | NV
| Max Current- Channel 81 | 81 | 6616 |  | 12080 | 12081 |  |  | R | NV
| Max Current- Channel 82 | 82 | 6617 |  | 12082 | 12083 |  |  | R | NV
| Max Current- Channel 83 | 83 | 6618 |  | 12084 | 12085 |  |  | R | NV
| Max Current- Channel 84 | 84 | 6619 |  | 12086 | 12087 |  |  | R | NV
| Max Current- Channel 85 | 85 | 6620 |  | 12088 | 12089 |  |  | R | NV
| Max Current- Channel 86 | 86 | 6621 |  | 12090 | 12091 |  |  | R | NV
| Max Current- Channel 87 | 87 | 6622 |  | 12092 | 12093 |  |  | R | NV
| Max Current- Channel 88 | 88 | 6623 |  | 12094 | 12095 |  |  | R | NV
| Max Current- Channel 89 | 89 | 6624 |  | 12096 | 12097 |  |  | R | NV
| Max Current- Channel 90 | 90 | 6625 |  | 12098 | 12099 |  |  | R | NV
| Max Current- Channel 91 | 91 | 6626 |  | 12100 | 12101 |  |  | R | NV
| Max Current- Channel 92 | 92 | 6627 |  | 12102 | 12103 |  |  | R | NV
| Max Current- Channel 93 | 93 | 6628 |  | 12104 | 12105 |  |  | R | NV
| Max Current- Channel 94 | 94 | 6629 |  | 12106 | 12107 |  |  | R | NV
| Max Current- Channel 95 | 95 | 6630 |  | 12108 | 12109 |  |  | R | NV
| Max Current- Channel 96 | 96 | 6631 |  | 12110 | 12111 |  |  | R | NV
| Max kW |  | 6632 | 6727 | 12112 | 12303 |  |  | R | NV
| Max kW- Channel 1 | 1 | 6632 |  | 12112 | 12113 |  |  | R | NV
| Max kW- Channel 2 | 2 | 6633 |  | 12114 | 12115 |  |  | R | NV
| Max kW- Channel 3 | 3 | 6634 |  | 12116 | 12117 |  |  | R | NV
| Max kW- Channel 4 | 4 | 6635 |  | 12118 | 12119 |  |  | R | NV
| Max kW- Channel 5 | 5 | 6636 |  | 12120 | 12121 |  |  | R | NV
| Max kW- Channel 6 | 6 | 6637 |  | 12122 | 12123 |  |  | R | NV
| Max kW- Channel 7 | 7 | 6638 |  | 12124 | 12125 |  |  | R | NV
| Max kW- Channel 8 | 8 | 6639 |  | 12126 | 12127 |  |  | R | NV
| Max kW- Channel 9 | 9 | 6640 |  | 12128 | 12129 |  |  | R | NV
| Max kW- Channel 10 | 10 | 6641 |  | 12130 | 12131 |  |  | R | NV
| Max kW- Channel 11 | 11 | 6642 |  | 12132 | 12133 |  |  | R | NV
| Max kW- Channel 12 | 12 | 6643 |  | 12134 | 12135 |  |  | R | NV
| Max kW- Channel 13 | 13 | 6644 |  | 12136 | 12137 |  |  | R | NV
| Max kW- Channel 14 | 14 | 6645 |  | 12138 | 12139 |  |  | R | NV
| Max kW- Channel 15 | 15 | 6646 |  | 12140 | 12141 |  |  | R | NV
| Max kW- Channel 16 | 16 | 6647 |  | 12142 | 12143 |  |  | R | NV
| Max kW- Channel 17 | 17 | 6648 |  | 12144 | 12145 |  |  | R | NV
| Max kW- Channel 18 | 18 | 6649 |  | 12146 | 12147 |  |  | R | NV
| Max kW- Channel 19 | 19 | 6650 |  | 12148 | 12149 |  |  | R | NV
| Max kW- Channel 20 | 20 | 6651 |  | 12150 | 12151 |  |  | R | NV
| Max kW- Channel 21 | 21 | 6652 |  | 12152 | 12153 |  |  | R | NV
| Max kW- Channel 22 | 22 | 6653 |  | 12154 | 12155 |  |  | R | NV
| Max kW- Channel 23 | 23 | 6654 |  | 12156 | 12157 |  |  | R | NV
| Max kW- Channel 24 | 24 | 6655 |  | 12158 | 12159 |  |  | R | NV
| Max kW- Channel 25 | 25 | 6656 |  | 12160 | 12161 |  |  | R | NV
| Max kW- Channel 26 | 26 | 6657 |  | 12162 | 12163 |  |  | R | NV
| Max kW- Channel 27 | 27 | 6658 |  | 12164 | 12165 |  |  | R | NV
| Max kW- Channel 28 | 28 | 6659 |  | 12166 | 12167 |  |  | R | NV
| Max kW- Channel 29 | 29 | 6660 |  | 12168 | 12169 |  |  | R | NV
| Max kW- Channel 30 | 30 | 6661 |  | 12170 | 12171 |  |  | R | NV
| Max kW- Channel 31 | 31 | 6662 |  | 12172 | 12173 |  |  | R | NV
| Max kW- Channel 32 | 32 | 6663 |  | 12174 | 12175 |  |  | R | NV
| Max kW- Channel 33 | 33 | 6664 |  | 12176 | 12177 |  |  | R | NV
| Max kW- Channel 34 | 34 | 6665 |  | 12178 | 12179 |  |  | R | NV
| Max kW- Channel 35 | 35 | 6666 |  | 12180 | 12181 |  |  | R | NV
| Max kW- Channel 36 | 36 | 6667 |  | 12182 | 12183 |  |  | R | NV
| Max kW- Channel 37 | 37 | 6668 |  | 12184 | 12185 |  |  | R | NV
| Max kW- Channel 38 | 38 | 6669 |  | 12186 | 12187 |  |  | R | NV
| Max kW- Channel 39 | 39 | 6670 |  | 12188 | 12189 |  |  | R | NV
| Max kW- Channel 40 | 40 | 6671 |  | 12190 | 12191 |  |  | R | NV
| Max kW- Channel 41 | 41 | 6672 |  | 12192 | 12193 |  |  | R | NV
| Max kW- Channel 42 | 42 | 6673 |  | 12194 | 12195 |  |  | R | NV
| Max kW- Channel 43 | 43 | 6674 |  | 12196 | 12197 |  |  | R | NV
| Max kW- Channel 44 | 44 | 6675 |  | 12198 | 12199 |  |  | R | NV
| Max kW- Channel 45 | 45 | 6676 |  | 12200 | 12201 |  |  | R | NV
| Max kW- Channel 46 | 46 | 6677 |  | 12202 | 12203 |  |  | R | NV
| Max kW- Channel 47 | 47 | 6678 |  | 12204 | 12205 |  |  | R | NV
| Max kW- Channel 48 | 48 | 6679 |  | 12206 | 12207 |  |  | R | NV
| Max kW- Channel 49 | 49 | 6680 |  | 12208 | 12209 |  |  | R | NV
| Max kW- Channel 50 | 50 | 6681 |  | 12210 | 12211 |  |  | R | NV
| Max kW- Channel 51 | 51 | 6682 |  | 12212 | 12213 |  |  | R | NV
| Max kW- Channel 52 | 52 | 6683 |  | 12214 | 12215 |  |  | R | NV
| Max kW- Channel 53 | 53 | 6684 |  | 12216 | 12217 |  |  | R | NV
| Max kW- Channel 54 | 54 | 6685 |  | 12218 | 12219 |  |  | R | NV
| Max kW- Channel 55 | 55 | 6686 |  | 12220 | 12221 |  |  | R | NV
| Max kW- Channel 56 | 56 | 6687 |  | 12222 | 12223 |  |  | R | NV
| Max kW- Channel 57 | 57 | 6688 |  | 12224 | 12225 |  |  | R | NV
| Max kW- Channel 58 | 58 | 6689 |  | 12226 | 12227 |  |  | R | NV
| Max kW- Channel 59 | 59 | 6690 |  | 12228 | 12229 |  |  | R | NV
| Max kW- Channel 60 | 60 | 6691 |  | 12230 | 12231 |  |  | R | NV
| Max kW- Channel 61 | 61 | 6692 |  | 12232 | 12233 |  |  | R | NV
| Max kW- Channel 62 | 62 | 6693 |  | 12234 | 12235 |  |  | R | NV
| Max kW- Channel 63 | 63 | 6694 |  | 12236 | 12237 |  |  | R | NV
| Max kW- Channel 64 | 64 | 6695 |  | 12238 | 12239 |  |  | R | NV
| Max kW- Channel 65 | 65 | 6696 |  | 12240 | 12241 |  |  | R | NV
| Max kW- Channel 66 | 66 | 6697 |  | 12242 | 12243 |  |  | R | NV
| Max kW- Channel 67 | 67 | 6698 |  | 12244 | 12245 |  |  | R | NV
| Max kW- Channel 68 | 68 | 6699 |  | 12246 | 12247 |  |  | R | NV
| Max kW- Channel 69 | 69 | 6700 |  | 12248 | 12249 |  |  | R | NV
| Max kW- Channel 70 | 70 | 6701 |  | 12250 | 12251 |  |  | R | NV
| Max kW- Channel 71 | 71 | 6702 |  | 12252 | 12253 |  |  | R | NV
| Max kW- Channel 72 | 72 | 6703 |  | 12254 | 12255 |  |  | R | NV
| Max kW- Channel 73 | 73 | 6704 |  | 12256 | 12257 |  |  | R | NV
| Max kW- Channel 74 | 74 | 6705 |  | 12258 | 12259 |  |  | R | NV
| Max kW- Channel 75 | 75 | 6706 |  | 12260 | 12261 |  |  | R | NV
| Max kW- Channel 76 | 76 | 6707 |  | 12262 | 12263 |  |  | R | NV
| Max kW- Channel 77 | 77 | 6708 |  | 12264 | 12265 |  |  | R | NV
| Max kW- Channel 78 | 78 | 6709 |  | 12266 | 12267 |  |  | R | NV
| Max kW- Channel 79 | 79 | 6710 |  | 12268 | 12269 |  |  | R | NV
| Max kW- Channel 80 | 80 | 6711 |  | 12270 | 12271 |  |  | R | NV
| Max kW- Channel 81 | 81 | 6712 |  | 12272 | 12273 |  |  | R | NV
| Max kW- Channel 82 | 82 | 6713 |  | 12274 | 12275 |  |  | R | NV
| Max kW- Channel 83 | 83 | 6714 |  | 12276 | 12277 |  |  | R | NV
| Max kW- Channel 84 | 84 | 6715 |  | 12278 | 12279 |  |  | R | NV
| Max kW- Channel 85 | 85 | 6716 |  | 12280 | 12281 |  |  | R | NV
| Max kW- Channel 86 | 86 | 6717 |  | 12282 | 12283 |  |  | R | NV
| Max kW- Channel 87 | 87 | 6718 |  | 12284 | 12285 |  |  | R | NV
| Max kW- Channel 88 | 88 | 6719 |  | 12286 | 12287 |  |  | R | NV
| Max kW- Channel 89 | 89 | 6720 |  | 12288 | 12289 |  |  | R | NV
| Max kW- Channel 90 | 90 | 6721 |  | 12290 | 12291 |  |  | R | NV
| Max kW- Channel 91 | 91 | 6722 |  | 12292 | 12293 |  |  | R | NV
| Max kW- Channel 92 | 92 | 6723 |  | 12294 | 12295 |  |  | R | NV
| Max kW- Channel 93 | 93 | 6724 |  | 12296 | 12297 |  |  | R | NV
| Max kW- Channel 94 | 94 | 6725 |  | 12298 | 12299 |  |  | R | NV
| Max kW- Channel 95 | 95 | 6726 |  | 12300 | 12301 |  |  | R | NV
| Max kW- Channel 96 | 96 | 6727 |  | 12302 | 12303 |  |  | R | NV
| Current Demand |  | 6728 | 6823 | 12304 | 12495 |  |  | R
| Current Demand- Channel 1 | 1 | 6728 |  | 12304 | 12305 |  |  | R
| Current Demand- Channel 2 | 2 | 6729 |  | 12306 | 12307 |  |  | R
| Current Demand- Channel 3 | 3 | 6730 |  | 12308 | 12309 |  |  | R
| Current Demand- Channel 4 | 4 | 6731 |  | 12310 | 12311 |  |  | R
| Current Demand- Channel 5 | 5 | 6732 |  | 12312 | 12313 |  |  | R
| Current Demand- Channel 6 | 6 | 6733 |  | 12314 | 12315 |  |  | R
| Current Demand- Channel 7 | 7 | 6734 |  | 12316 | 12317 |  |  | R
| Current Demand- Channel 8 | 8 | 6735 |  | 12318 | 12319 |  |  | R
| Current Demand- Channel 9 | 9 | 6736 |  | 12320 | 12321 |  |  | R
| Current Demand- Channel 10 | 10 | 6737 |  | 12322 | 12323 |  |  | R
| Current Demand- Channel 11 | 11 | 6738 |  | 12324 | 12325 |  |  | R
| Current Demand- Channel 12 | 12 | 6739 |  | 12326 | 12327 |  |  | R
| Current Demand- Channel 13 | 13 | 6740 |  | 12328 | 12329 |  |  | R
| Current Demand- Channel 14 | 14 | 6741 |  | 12330 | 12331 |  |  | R
| Current Demand- Channel 15 | 15 | 6742 |  | 12332 | 12333 |  |  | R
| Current Demand- Channel 16 | 16 | 6743 |  | 12334 | 12335 |  |  | R
| Current Demand- Channel 17 | 17 | 6744 |  | 12336 | 12337 |  |  | R
| Current Demand- Channel 18 | 18 | 6745 |  | 12338 | 12339 |  |  | R
| Current Demand- Channel 19 | 19 | 6746 |  | 12340 | 12341 |  |  | R
| Current Demand- Channel 20 | 20 | 6747 |  | 12342 | 12343 |  |  | R
| Current Demand- Channel 21 | 21 | 6748 |  | 12344 | 12345 |  |  | R
| Current Demand- Channel 22 | 22 | 6749 |  | 12346 | 12347 |  |  | R
| Current Demand- Channel 23 | 23 | 6750 |  | 12348 | 12349 |  |  | R
| Current Demand- Channel 24 | 24 | 6751 |  | 12350 | 12351 |  |  | R
| Current Demand- Channel 25 | 25 | 6752 |  | 12352 | 12353 |  |  | R
| Current Demand- Channel 26 | 26 | 6753 |  | 12354 | 12355 |  |  | R
| Current Demand- Channel 27 | 27 | 6754 |  | 12356 | 12357 |  |  | R
| Current Demand- Channel 28 | 28 | 6755 |  | 12358 | 12359 |  |  | R
| Current Demand- Channel 29 | 29 | 6756 |  | 12360 | 12361 |  |  | R
| Current Demand- Channel 30 | 30 | 6757 |  | 12362 | 12363 |  |  | R
| Current Demand- Channel 31 | 31 | 6758 |  | 12364 | 12365 |  |  | R
| Current Demand- Channel 32 | 32 | 6759 |  | 12366 | 12367 |  |  | R
| Current Demand- Channel 33 | 33 | 6760 |  | 12368 | 12369 |  |  | R
| Current Demand- Channel 34 | 34 | 6761 |  | 12370 | 12371 |  |  | R
| Current Demand- Channel 35 | 35 | 6762 |  | 12372 | 12373 |  |  | R
| Current Demand- Channel 36 | 36 | 6763 |  | 12374 | 12375 |  |  | R
| Current Demand- Channel 37 | 37 | 6764 |  | 12376 | 12377 |  |  | R
| Current Demand- Channel 38 | 38 | 6765 |  | 12378 | 12379 |  |  | R
| Current Demand- Channel 39 | 39 | 6766 |  | 12380 | 12381 |  |  | R
| Current Demand- Channel 40 | 40 | 6767 |  | 12382 | 12383 |  |  | R
| Current Demand- Channel 41 | 41 | 6768 |  | 12384 | 12385 |  |  | R
| Current Demand- Channel 42 | 42 | 6769 |  | 12386 | 12387 |  |  | R
| Current Demand- Channel 43 | 43 | 6770 |  | 12388 | 12389 |  |  | R
| Current Demand- Channel 44 | 44 | 6771 |  | 12390 | 12391 |  |  | R
| Current Demand- Channel 45 | 45 | 6772 |  | 12392 | 12393 |  |  | R
| Current Demand- Channel 46 | 46 | 6773 |  | 12394 | 12395 |  |  | R
| Current Demand- Channel 47 | 47 | 6774 |  | 12396 | 12397 |  |  | R
| Current Demand- Channel 48 | 48 | 6775 |  | 12398 | 12399 |  |  | R
| Current Demand- Channel 49 | 49 | 6776 |  | 12400 | 12401 |  |  | R
| Current Demand- Channel 50 | 50 | 6777 |  | 12402 | 12403 |  |  | R
| Current Demand- Channel 51 | 51 | 6778 |  | 12404 | 12405 |  |  | R
| Current Demand- Channel 52 | 52 | 6779 |  | 12406 | 12407 |  |  | R
| Current Demand- Channel 53 | 53 | 6780 |  | 12408 | 12409 |  |  | R
| Current Demand- Channel 54 | 54 | 6781 |  | 12410 | 12411 |  |  | R
| Current Demand- Channel 55 | 55 | 6782 |  | 12412 | 12413 |  |  | R
| Current Demand- Channel 56 | 56 | 6783 |  | 12414 | 12415 |  |  | R
| Current Demand- Channel 57 | 57 | 6784 |  | 12416 | 12417 |  |  | R
| Current Demand- Channel 58 | 58 | 6785 |  | 12418 | 12419 |  |  | R
| Current Demand- Channel 59 | 59 | 6786 |  | 12420 | 12421 |  |  | R
| Current Demand- Channel 60 | 60 | 6787 |  | 12422 | 12423 |  |  | R
| Current Demand- Channel 61 | 61 | 6788 |  | 12424 | 12425 |  |  | R
| Current Demand- Channel 62 | 62 | 6789 |  | 12426 | 12427 |  |  | R
| Current Demand- Channel 63 | 63 | 6790 |  | 12428 | 12429 |  |  | R
| Current Demand- Channel 64 | 64 | 6791 |  | 12430 | 12431 |  |  | R
| Current Demand- Channel 65 | 65 | 6792 |  | 12432 | 12433 |  |  | R
| Current Demand- Channel 66 | 66 | 6793 |  | 12434 | 12435 |  |  | R
| Current Demand- Channel 67 | 67 | 6794 |  | 12436 | 12437 |  |  | R
| Current Demand- Channel 68 | 68 | 6795 |  | 12438 | 12439 |  |  | R
| Current Demand- Channel 69 | 69 | 6796 |  | 12440 | 12441 |  |  | R
| Current Demand- Channel 70 | 70 | 6797 |  | 12442 | 12443 |  |  | R
| Current Demand- Channel 71 | 71 | 6798 |  | 12444 | 12445 |  |  | R
| Current Demand- Channel 72 | 72 | 6799 |  | 12446 | 12447 |  |  | R
| Current Demand- Channel 73 | 73 | 6800 |  | 12448 | 12449 |  |  | R
| Current Demand- Channel 74 | 74 | 6801 |  | 12450 | 12451 |  |  | R
| Current Demand- Channel 75 | 75 | 6802 |  | 12452 | 12453 |  |  | R
| Current Demand- Channel 76 | 76 | 6803 |  | 12454 | 12455 |  |  | R
| Current Demand- Channel 77 | 77 | 6804 |  | 12456 | 12457 |  |  | R
| Current Demand- Channel 78 | 78 | 6805 |  | 12458 | 12459 |  |  | R
| Current Demand- Channel 79 | 79 | 6806 |  | 12460 | 12461 |  |  | R
| Current Demand- Channel 80 | 80 | 6807 |  | 12462 | 12463 |  |  | R
| Current Demand- Channel 81 | 81 | 6808 |  | 12464 | 12465 |  |  | R
| Current Demand- Channel 82 | 82 | 6809 |  | 12466 | 12467 |  |  | R
| Current Demand- Channel 83 | 83 | 6810 |  | 12468 | 12469 |  |  | R
| Current Demand- Channel 84 | 84 | 6811 |  | 12470 | 12471 |  |  | R
| Current Demand- Channel 85 | 85 | 6812 |  | 12472 | 12473 |  |  | R
| Current Demand- Channel 86 | 86 | 6813 |  | 12474 | 12475 |  |  | R
| Current Demand- Channel 87 | 87 | 6814 |  | 12476 | 12477 |  |  | R
| Current Demand- Channel 88 | 88 | 6815 |  | 12478 | 12479 |  |  | R
| Current Demand- Channel 89 | 89 | 6816 |  | 12480 | 12481 |  |  | R
| Current Demand- Channel 90 | 90 | 6817 |  | 12482 | 12483 |  |  | R
| Current Demand- Channel 91 | 91 | 6818 |  | 12484 | 12485 |  |  | R
| Current Demand- Channel 92 | 92 | 6819 |  | 12486 | 12487 |  |  | R
| Current Demand- Channel 93 | 93 | 6820 |  | 12488 | 12489 |  |  | R
| Current Demand- Channel 94 | 94 | 6821 |  | 12490 | 12491 |  |  | R
| Current Demand- Channel 95 | 95 | 6822 |  | 12492 | 12493 |  |  | R
| Current Demand- Channel 96 | 96 | 6823 |  | 12494 | 12495 |  |  | R
| kW Demand |  | 6824 | 6919 | 12496 | 12687 |  |  | R
| kW Demand- Channel 1 | 1 | 6824 |  | 12496 | 12497 |  |  | R
| kW Demand- Channel 2 | 2 | 6825 |  | 12498 | 12499 |  |  | R
| kW Demand- Channel 3 | 3 | 6826 |  | 12500 | 12501 |  |  | R
| kW Demand- Channel 4 | 4 | 6827 |  | 12502 | 12503 |  |  | R
| kW Demand- Channel 5 | 5 | 6828 |  | 12504 | 12505 |  |  | R
| kW Demand- Channel 6 | 6 | 6829 |  | 12506 | 12507 |  |  | R
| kW Demand- Channel 7 | 7 | 6830 |  | 12508 | 12509 |  |  | R
| kW Demand- Channel 8 | 8 | 6831 |  | 12510 | 12511 |  |  | R
| kW Demand- Channel 9 | 9 | 6832 |  | 12512 | 12513 |  |  | R
| kW Demand- Channel 10 | 10 | 6833 |  | 12514 | 12515 |  |  | R
| kW Demand- Channel 11 | 11 | 6834 |  | 12516 | 12517 |  |  | R
| kW Demand- Channel 12 | 12 | 6835 |  | 12518 | 12519 |  |  | R
| kW Demand- Channel 13 | 13 | 6836 |  | 12520 | 12521 |  |  | R
| kW Demand- Channel 14 | 14 | 6837 |  | 12522 | 12523 |  |  | R
| kW Demand- Channel 15 | 15 | 6838 |  | 12524 | 12525 |  |  | R
| kW Demand- Channel 16 | 16 | 6839 |  | 12526 | 12527 |  |  | R
| kW Demand- Channel 17 | 17 | 6840 |  | 12528 | 12529 |  |  | R
| kW Demand- Channel 18 | 18 | 6841 |  | 12530 | 12531 |  |  | R
| kW Demand- Channel 19 | 19 | 6842 |  | 12532 | 12533 |  |  | R
| kW Demand- Channel 20 | 20 | 6843 |  | 12534 | 12535 |  |  | R
| kW Demand- Channel 21 | 21 | 6844 |  | 12536 | 12537 |  |  | R
| kW Demand- Channel 22 | 22 | 6845 |  | 12538 | 12539 |  |  | R
| kW Demand- Channel 23 | 23 | 6846 |  | 12540 | 12541 |  |  | R
| kW Demand- Channel 24 | 24 | 6847 |  | 12542 | 12543 |  |  | R
| kW Demand- Channel 25 | 25 | 6848 |  | 12544 | 12545 |  |  | R
| kW Demand- Channel 26 | 26 | 6849 |  | 12546 | 12547 |  |  | R
| kW Demand- Channel 27 | 27 | 6850 |  | 12548 | 12549 |  |  | R
| kW Demand- Channel 28 | 28 | 6851 |  | 12550 | 12551 |  |  | R
| kW Demand- Channel 29 | 29 | 6852 |  | 12552 | 12553 |  |  | R
| kW Demand- Channel 30 | 30 | 6853 |  | 12554 | 12555 |  |  | R
| kW Demand- Channel 31 | 31 | 6854 |  | 12556 | 12557 |  |  | R
| kW Demand- Channel 32 | 32 | 6855 |  | 12558 | 12559 |  |  | R
| kW Demand- Channel 33 | 33 | 6856 |  | 12560 | 12561 |  |  | R
| kW Demand- Channel 34 | 34 | 6857 |  | 12562 | 12563 |  |  | R
| kW Demand- Channel 35 | 35 | 6858 |  | 12564 | 12565 |  |  | R
| kW Demand- Channel 36 | 36 | 6859 |  | 12566 | 12567 |  |  | R
| kW Demand- Channel 37 | 37 | 6860 |  | 12568 | 12569 |  |  | R
| kW Demand- Channel 38 | 38 | 6861 |  | 12570 | 12571 |  |  | R
| kW Demand- Channel 39 | 39 | 6862 |  | 12572 | 12573 |  |  | R
| kW Demand- Channel 40 | 40 | 6863 |  | 12574 | 12575 |  |  | R
| kW Demand- Channel 41 | 41 | 6864 |  | 12576 | 12577 |  |  | R
| kW Demand- Channel 42 | 42 | 6865 |  | 12578 | 12579 |  |  | R
| kW Demand- Channel 43 | 43 | 6866 |  | 12580 | 12581 |  |  | R
| kW Demand- Channel 44 | 44 | 6867 |  | 12582 | 12583 |  |  | R
| kW Demand- Channel 45 | 45 | 6868 |  | 12584 | 12585 |  |  | R
| kW Demand- Channel 46 | 46 | 6869 |  | 12586 | 12587 |  |  | R
| kW Demand- Channel 47 | 47 | 6870 |  | 12588 | 12589 |  |  | R
| kW Demand- Channel 48 | 48 | 6871 |  | 12590 | 12591 |  |  | R
| kW Demand- Channel 49 | 49 | 6872 |  | 12592 | 12593 |  |  | R
| kW Demand- Channel 50 | 50 | 6873 |  | 12594 | 12595 |  |  | R
| kW Demand- Channel 51 | 51 | 6874 |  | 12596 | 12597 |  |  | R
| kW Demand- Channel 52 | 52 | 6875 |  | 12598 | 12599 |  |  | R
| kW Demand- Channel 53 | 53 | 6876 |  | 12600 | 12601 |  |  | R
| kW Demand- Channel 54 | 54 | 6877 |  | 12602 | 12603 |  |  | R
| kW Demand- Channel 55 | 55 | 6878 |  | 12604 | 12605 |  |  | R
| kW Demand- Channel 56 | 56 | 6879 |  | 12606 | 12607 |  |  | R
| kW Demand- Channel 57 | 57 | 6880 |  | 12608 | 12609 |  |  | R
| kW Demand- Channel 58 | 58 | 6881 |  | 12610 | 12611 |  |  | R
| kW Demand- Channel 59 | 59 | 6882 |  | 12612 | 12613 |  |  | R
| kW Demand- Channel 60 | 60 | 6883 |  | 12614 | 12615 |  |  | R
| kW Demand- Channel 61 | 61 | 6884 |  | 12616 | 12617 |  |  | R
| kW Demand- Channel 62 | 62 | 6885 |  | 12618 | 12619 |  |  | R
| kW Demand- Channel 63 | 63 | 6886 |  | 12620 | 12621 |  |  | R
| kW Demand- Channel 64 | 64 | 6887 |  | 12622 | 12623 |  |  | R
| kW Demand- Channel 65 | 65 | 6888 |  | 12624 | 12625 |  |  | R
| kW Demand- Channel 66 | 66 | 6889 |  | 12626 | 12627 |  |  | R
| kW Demand- Channel 67 | 67 | 6890 |  | 12628 | 12629 |  |  | R
| kW Demand- Channel 68 | 68 | 6891 |  | 12630 | 12631 |  |  | R
| kW Demand- Channel 69 | 69 | 6892 |  | 12632 | 12633 |  |  | R
| kW Demand- Channel 70 | 70 | 6893 |  | 12634 | 12635 |  |  | R
| kW Demand- Channel 71 | 71 | 6894 |  | 12636 | 12637 |  |  | R
| kW Demand- Channel 72 | 72 | 6895 |  | 12638 | 12639 |  |  | R
| kW Demand- Channel 73 | 73 | 6896 |  | 12640 | 12641 |  |  | R
| kW Demand- Channel 74 | 74 | 6897 |  | 12642 | 12643 |  |  | R
| kW Demand- Channel 75 | 75 | 6898 |  | 12644 | 12645 |  |  | R
| kW Demand- Channel 76 | 76 | 6899 |  | 12646 | 12647 |  |  | R
| kW Demand- Channel 77 | 77 | 6900 |  | 12648 | 12649 |  |  | R
| kW Demand- Channel 78 | 78 | 6901 |  | 12650 | 12651 |  |  | R
| kW Demand- Channel 79 | 79 | 6902 |  | 12652 | 12653 |  |  | R
| kW Demand- Channel 80 | 80 | 6903 |  | 12654 | 12655 |  |  | R
| kW Demand- Channel 81 | 81 | 6904 |  | 12656 | 12657 |  |  | R
| kW Demand- Channel 82 | 82 | 6905 |  | 12658 | 12659 |  |  | R
| kW Demand- Channel 83 | 83 | 6906 |  | 12660 | 12661 |  |  | R
| kW Demand- Channel 84 | 84 | 6907 |  | 12662 | 12663 |  |  | R
| kW Demand- Channel 85 | 85 | 6908 |  | 12664 | 12665 |  |  | R
| kW Demand- Channel 86 | 86 | 6909 |  | 12666 | 12667 |  |  | R
| kW Demand- Channel 87 | 87 | 6910 |  | 12668 | 12669 |  |  | R
| kW Demand- Channel 88 | 88 | 6911 |  | 12670 | 12671 |  |  | R
| kW Demand- Channel 89 | 89 | 6912 |  | 12672 | 12673 |  |  | R
| kW Demand- Channel 90 | 90 | 6913 |  | 12674 | 12675 |  |  | R
| kW Demand- Channel 91 | 91 | 6914 |  | 12676 | 12677 |  |  | R
| kW Demand- Channel 92 | 92 | 6915 |  | 12678 | 12679 |  |  | R
| kW Demand- Channel 93 | 93 | 6916 |  | 12680 | 12681 |  |  | R
| kW Demand- Channel 94 | 94 | 6917 |  | 12682 | 12683 |  |  | R
| kW Demand- Channel 95 | 95 | 6918 |  | 12684 | 12685 |  |  | R
| kW Demand- Channel 96 | 96 | 6919 |  | 12686 | 12687 |  |  | R
| Max Current Demand |  | 6920 | 7015 | 12688 | 12879 |  |  | R | NV
| Max Current Demand - Channel 1 | 1 | 6920 |  | 12688 | 12689 |  |  | R | NV
| Max Current Demand - Channel 2 | 2 | 6921 |  | 12690 | 12691 |  |  | R | NV
| Max Current Demand - Channel 3 | 3 | 6922 |  | 12692 | 12693 |  |  | R | NV
| Max Current Demand - Channel 4 | 4 | 6923 |  | 12694 | 12695 |  |  | R | NV
| Max Current Demand - Channel 5 | 5 | 6924 |  | 12696 | 12697 |  |  | R | NV
| Max Current Demand - Channel 6 | 6 | 6925 |  | 12698 | 12699 |  |  | R | NV
| Max Current Demand - Channel 7 | 7 | 6926 |  | 12700 | 12701 |  |  | R | NV
| Max Current Demand - Channel 8 | 8 | 6927 |  | 12702 | 12703 |  |  | R | NV
| Max Current Demand - Channel 9 | 9 | 6928 |  | 12704 | 12705 |  |  | R | NV
| Max Current Demand - Channel 10 | 10 | 6929 |  | 12706 | 12707 |  |  | R | NV
| Max Current Demand - Channel 11 | 11 | 6930 |  | 12708 | 12709 |  |  | R | NV
| Max Current Demand - Channel 12 | 12 | 6931 |  | 12710 | 12711 |  |  | R | NV
| Max Current Demand - Channel 13 | 13 | 6932 |  | 12712 | 12713 |  |  | R | NV
| Max Current Demand - Channel 14 | 14 | 6933 |  | 12714 | 12715 |  |  | R | NV
| Max Current Demand - Channel 15 | 15 | 6934 |  | 12716 | 12717 |  |  | R | NV
| Max Current Demand - Channel 16 | 16 | 6935 |  | 12718 | 12719 |  |  | R | NV
| Max Current Demand - Channel 17 | 17 | 6936 |  | 12720 | 12721 |  |  | R | NV
| Max Current Demand - Channel 18 | 18 | 6937 |  | 12722 | 12723 |  |  | R | NV
| Max Current Demand - Channel 19 | 19 | 6938 |  | 12724 | 12725 |  |  | R | NV
| Max Current Demand - Channel 20 | 20 | 6939 |  | 12726 | 12727 |  |  | R | NV
| Max Current Demand - Channel 21 | 21 | 6940 |  | 12728 | 12729 |  |  | R | NV
| Max Current Demand - Channel 22 | 22 | 6941 |  | 12730 | 12731 |  |  | R | NV
| Max Current Demand - Channel 23 | 23 | 6942 |  | 12732 | 12733 |  |  | R | NV
| Max Current Demand - Channel 24 | 24 | 6943 |  | 12734 | 12735 |  |  | R | NV
| Max Current Demand - Channel 25 | 25 | 6944 |  | 12736 | 12737 |  |  | R | NV
| Max Current Demand - Channel 26 | 26 | 6945 |  | 12738 | 12739 |  |  | R | NV
| Max Current Demand - Channel 27 | 27 | 6946 |  | 12740 | 12741 |  |  | R | NV
| Max Current Demand - Channel 28 | 28 | 6947 |  | 12742 | 12743 |  |  | R | NV
| Max Current Demand - Channel 29 | 29 | 6948 |  | 12744 | 12745 |  |  | R | NV
| Max Current Demand - Channel 30 | 30 | 6949 |  | 12746 | 12747 |  |  | R | NV
| Max Current Demand - Channel 31 | 31 | 6950 |  | 12748 | 12749 |  |  | R | NV
| Max Current Demand - Channel 32 | 32 | 6951 |  | 12750 | 12751 |  |  | R | NV
| Max Current Demand - Channel 33 | 33 | 6952 |  | 12752 | 12753 |  |  | R | NV
| Max Current Demand - Channel 34 | 34 | 6953 |  | 12754 | 12755 |  |  | R | NV
| Max Current Demand - Channel 35 | 35 | 6954 |  | 12756 | 12757 |  |  | R | NV
| Max Current Demand - Channel 36 | 36 | 6955 |  | 12758 | 12759 |  |  | R | NV
| Max Current Demand - Channel 37 | 37 | 6956 |  | 12760 | 12761 |  |  | R | NV
| Max Current Demand - Channel 38 | 38 | 6957 |  | 12762 | 12763 |  |  | R | NV
| Max Current Demand - Channel 39 | 39 | 6958 |  | 12764 | 12765 |  |  | R | NV
| Max Current Demand - Channel 40 | 40 | 6959 |  | 12766 | 12767 |  |  | R | NV
| Max Current Demand - Channel 41 | 41 | 6960 |  | 12768 | 12769 |  |  | R | NV
| Max Current Demand - Channel 42 | 42 | 6961 |  | 12770 | 12771 |  |  | R | NV
| Max Current Demand - Channel 43 | 43 | 6962 |  | 12772 | 12773 |  |  | R | NV
| Max Current Demand - Channel 44 | 44 | 6963 |  | 12774 | 12775 |  |  | R | NV
| Max Current Demand - Channel 45 | 45 | 6964 |  | 12776 | 12777 |  |  | R | NV
| Max Current Demand - Channel 46 | 46 | 6965 |  | 12778 | 12779 |  |  | R | NV
| Max Current Demand - Channel 47 | 47 | 6966 |  | 12780 | 12781 |  |  | R | NV
| Max Current Demand - Channel 48 | 48 | 6967 |  | 12782 | 12783 |  |  | R | NV
| Max Current Demand - Channel 49 | 49 | 6968 |  | 12784 | 12785 |  |  | R | NV
| Max Current Demand - Channel 50 | 50 | 6969 |  | 12786 | 12787 |  |  | R | NV
| Max Current Demand - Channel 51 | 51 | 6970 |  | 12788 | 12789 |  |  | R | NV
| Max Current Demand - Channel 52 | 52 | 6971 |  | 12790 | 12791 |  |  | R | NV
| Max Current Demand - Channel 53 | 53 | 6972 |  | 12792 | 12793 |  |  | R | NV
| Max Current Demand - Channel 54 | 54 | 6973 |  | 12794 | 12795 |  |  | R | NV
| Max Current Demand - Channel 55 | 55 | 6974 |  | 12796 | 12797 |  |  | R | NV
| Max Current Demand - Channel 56 | 56 | 6975 |  | 12798 | 12799 |  |  | R | NV
| Max Current Demand - Channel 57 | 57 | 6976 |  | 12800 | 12801 |  |  | R | NV
| Max Current Demand - Channel 58 | 58 | 6977 |  | 12802 | 12803 |  |  | R | NV
| Max Current Demand - Channel 59 | 59 | 6978 |  | 12804 | 12805 |  |  | R | NV
| Max Current Demand - Channel 60 | 60 | 6979 |  | 12806 | 12807 |  |  | R | NV
| Max Current Demand - Channel 61 | 61 | 6980 |  | 12808 | 12809 |  |  | R | NV
| Max Current Demand - Channel 62 | 62 | 6981 |  | 12810 | 12811 |  |  | R | NV
| Max Current Demand - Channel 63 | 63 | 6982 |  | 12812 | 12813 |  |  | R | NV
| Max Current Demand - Channel 64 | 64 | 6983 |  | 12814 | 12815 |  |  | R | NV
| Max Current Demand - Channel 65 | 65 | 6984 |  | 12816 | 12817 |  |  | R | NV
| Max Current Demand - Channel 66 | 66 | 6985 |  | 12818 | 12819 |  |  | R | NV
| Max Current Demand - Channel 67 | 67 | 6986 |  | 12820 | 12821 |  |  | R | NV
| Max Current Demand - Channel 68 | 68 | 6987 |  | 12822 | 12823 |  |  | R | NV
| Max Current Demand - Channel 69 | 69 | 6988 |  | 12824 | 12825 |  |  | R | NV
| Max Current Demand - Channel 70 | 70 | 6989 |  | 12826 | 12827 |  |  | R | NV
| Max Current Demand - Channel 71 | 71 | 6990 |  | 12828 | 12829 |  |  | R | NV
| Max Current Demand - Channel 72 | 72 | 6991 |  | 12830 | 12831 |  |  | R | NV
| Max Current Demand - Channel 73 | 73 | 6992 |  | 12832 | 12833 |  |  | R | NV
| Max Current Demand - Channel 74 | 74 | 6993 |  | 12834 | 12835 |  |  | R | NV
| Max Current Demand - Channel 75 | 75 | 6994 |  | 12836 | 12837 |  |  | R | NV
| Max Current Demand - Channel 76 | 76 | 6995 |  | 12838 | 12839 |  |  | R | NV
| Max Current Demand - Channel 77 | 77 | 6996 |  | 12840 | 12841 |  |  | R | NV
| Max Current Demand - Channel 78 | 78 | 6997 |  | 12842 | 12843 |  |  | R | NV
| Max Current Demand - Channel 79 | 79 | 6998 |  | 12844 | 12845 |  |  | R | NV
| Max Current Demand - Channel 80 | 80 | 6999 |  | 12846 | 12847 |  |  | R | NV
| Max Current Demand - Channel 81 | 81 | 7000 |  | 12848 | 12849 |  |  | R | NV
| Max Current Demand - Channel 82 | 82 | 7001 |  | 12850 | 12851 |  |  | R | NV
| Max Current Demand - Channel 83 | 83 | 7002 |  | 12852 | 12853 |  |  | R | NV
| Max Current Demand - Channel 84 | 84 | 7003 |  | 12854 | 12855 |  |  | R | NV
| Max Current Demand - Channel 85 | 85 | 7004 |  | 12856 | 12857 |  |  | R | NV
| Max Current Demand - Channel 86 | 86 | 7005 |  | 12858 | 12859 |  |  | R | NV
| Max Current Demand - Channel 87 | 87 | 7006 |  | 12860 | 12861 |  |  | R | NV
| Max Current Demand - Channel 88 | 88 | 7007 |  | 12862 | 12863 |  |  | R | NV
| Max Current Demand - Channel 89 | 89 | 7008 |  | 12864 | 12865 |  |  | R | NV
| Max Current Demand - Channel 90 | 90 | 7009 |  | 12866 | 12867 |  |  | R | NV
| Max Current Demand - Channel 91 | 91 | 7010 |  | 12868 | 12869 |  |  | R | NV
| Max Current Demand - Channel 92 | 92 | 7011 |  | 12870 | 12871 |  |  | R | NV
| Max Current Demand - Channel 93 | 93 | 7012 |  | 12872 | 12873 |  |  | R | NV
| Max Current Demand - Channel 94 | 94 | 7013 |  | 12874 | 12875 |  |  | R | NV
| Max Current Demand - Channel 95 | 95 | 7014 |  | 12876 | 12877 |  |  | R | NV
| Max Current Demand - Channel 96 | 96 | 7015 |  | 12878 | 12879 |  |  | R | NV
| Max kW Demand |  | 7016 | 7111 | 12880 | 13071 |  |  | R | NV
| Max kW Demand - Channel 1 | 1 | 7016 |  | 12880 | 12881 |  |  | R | NV
| Max kW Demand - Channel 2 | 2 | 7017 |  | 12882 | 12883 |  |  | R | NV
| Max kW Demand - Channel 3 | 3 | 7018 |  | 12884 | 12885 |  |  | R | NV
| Max kW Demand - Channel 4 | 4 | 7019 |  | 12886 | 12887 |  |  | R | NV
| Max kW Demand - Channel 5 | 5 | 7020 |  | 12888 | 12889 |  |  | R | NV
| Max kW Demand - Channel 6 | 6 | 7021 |  | 12890 | 12891 |  |  | R | NV
| Max kW Demand - Channel 7 | 7 | 7022 |  | 12892 | 12893 |  |  | R | NV
| Max kW Demand - Channel 8 | 8 | 7023 |  | 12894 | 12895 |  |  | R | NV
| Max kW Demand - Channel 9 | 9 | 7024 |  | 12896 | 12897 |  |  | R | NV
| Max kW Demand - Channel 10 | 10 | 7025 |  | 12898 | 12899 |  |  | R | NV
| Max kW Demand - Channel 11 | 11 | 7026 |  | 12900 | 12901 |  |  | R | NV
| Max kW Demand - Channel 12 | 12 | 7027 |  | 12902 | 12903 |  |  | R | NV
| Max kW Demand - Channel 13 | 13 | 7028 |  | 12904 | 12905 |  |  | R | NV
| Max kW Demand - Channel 14 | 14 | 7029 |  | 12906 | 12907 |  |  | R | NV
| Max kW Demand - Channel 15 | 15 | 7030 |  | 12908 | 12909 |  |  | R | NV
| Max kW Demand - Channel 16 | 16 | 7031 |  | 12910 | 12911 |  |  | R | NV
| Max kW Demand - Channel 17 | 17 | 7032 |  | 12912 | 12913 |  |  | R | NV
| Max kW Demand - Channel 18 | 18 | 7033 |  | 12914 | 12915 |  |  | R | NV
| Max kW Demand - Channel 19 | 19 | 7034 |  | 12916 | 12917 |  |  | R | NV
| Max kW Demand - Channel 20 | 20 | 7035 |  | 12918 | 12919 |  |  | R | NV
| Max kW Demand - Channel 21 | 21 | 7036 |  | 12920 | 12921 |  |  | R | NV
| Max kW Demand - Channel 22 | 22 | 7037 |  | 12922 | 12923 |  |  | R | NV
| Max kW Demand - Channel 23 | 23 | 7038 |  | 12924 | 12925 |  |  | R | NV
| Max kW Demand - Channel 24 | 24 | 7039 |  | 12926 | 12927 |  |  | R | NV
| Max kW Demand - Channel 25 | 25 | 7040 |  | 12928 | 12929 |  |  | R | NV
| Max kW Demand - Channel 26 | 26 | 7041 |  | 12930 | 12931 |  |  | R | NV
| Max kW Demand - Channel 27 | 27 | 7042 |  | 12932 | 12933 |  |  | R | NV
| Max kW Demand - Channel 28 | 28 | 7043 |  | 12934 | 12935 |  |  | R | NV
| Max kW Demand - Channel 29 | 29 | 7044 |  | 12936 | 12937 |  |  | R | NV
| Max kW Demand - Channel 30 | 30 | 7045 |  | 12938 | 12939 |  |  | R | NV
| Max kW Demand - Channel 31 | 31 | 7046 |  | 12940 | 12941 |  |  | R | NV
| Max kW Demand - Channel 32 | 32 | 7047 |  | 12942 | 12943 |  |  | R | NV
| Max kW Demand - Channel 33 | 33 | 7048 |  | 12944 | 12945 |  |  | R | NV
| Max kW Demand - Channel 34 | 34 | 7049 |  | 12946 | 12947 |  |  | R | NV
| Max kW Demand - Channel 35 | 35 | 7050 |  | 12948 | 12949 |  |  | R | NV
| Max kW Demand - Channel 36 | 36 | 7051 |  | 12950 | 12951 |  |  | R | NV
| Max kW Demand - Channel 37 | 37 | 7052 |  | 12952 | 12953 |  |  | R | NV
| Max kW Demand - Channel 38 | 38 | 7053 |  | 12954 | 12955 |  |  | R | NV
| Max kW Demand - Channel 39 | 39 | 7054 |  | 12956 | 12957 |  |  | R | NV
| Max kW Demand - Channel 40 | 40 | 7055 |  | 12958 | 12959 |  |  | R | NV
| Max kW Demand - Channel 41 | 41 | 7056 |  | 12960 | 12961 |  |  | R | NV
| Max kW Demand - Channel 42 | 42 | 7057 |  | 12962 | 12963 |  |  | R | NV
| Max kW Demand - Channel 43 | 43 | 7058 |  | 12964 | 12965 |  |  | R | NV
| Max kW Demand - Channel 44 | 44 | 7059 |  | 12966 | 12967 |  |  | R | NV
| Max kW Demand - Channel 45 | 45 | 7060 |  | 12968 | 12969 |  |  | R | NV
| Max kW Demand - Channel 46 | 46 | 7061 |  | 12970 | 12971 |  |  | R | NV
| Max kW Demand - Channel 47 | 47 | 7062 |  | 12972 | 12973 |  |  | R | NV
| Max kW Demand - Channel 48 | 48 | 7063 |  | 12974 | 12975 |  |  | R | NV
| Max kW Demand - Channel 49 | 49 | 7064 |  | 12976 | 12977 |  |  | R | NV
| Max kW Demand - Channel 50 | 50 | 7065 |  | 12978 | 12979 |  |  | R | NV
| Max kW Demand - Channel 51 | 51 | 7066 |  | 12980 | 12981 |  |  | R | NV
| Max kW Demand - Channel 52 | 52 | 7067 |  | 12982 | 12983 |  |  | R | NV
| Max kW Demand - Channel 53 | 53 | 7068 |  | 12984 | 12985 |  |  | R | NV
| Max kW Demand - Channel 54 | 54 | 7069 |  | 12986 | 12987 |  |  | R | NV
| Max kW Demand - Channel 55 | 55 | 7070 |  | 12988 | 12989 |  |  | R | NV
| Max kW Demand - Channel 56 | 56 | 7071 |  | 12990 | 12991 |  |  | R | NV
| Max kW Demand - Channel 57 | 57 | 7072 |  | 12992 | 12993 |  |  | R | NV
| Max kW Demand - Channel 58 | 58 | 7073 |  | 12994 | 12995 |  |  | R | NV
| Max kW Demand - Channel 59 | 59 | 7074 |  | 12996 | 12997 |  |  | R | NV
| Max kW Demand - Channel 60 | 60 | 7075 |  | 12998 | 12999 |  |  | R | NV
| Max kW Demand - Channel 61 | 61 | 7076 |  | 13000 | 13001 |  |  | R | NV
| Max kW Demand - Channel 62 | 62 | 7077 |  | 13002 | 13003 |  |  | R | NV
| Max kW Demand - Channel 63 | 63 | 7078 |  | 13004 | 13005 |  |  | R | NV
| Max kW Demand - Channel 64 | 64 | 7079 |  | 13006 | 13007 |  |  | R | NV
| Max kW Demand - Channel 65 | 65 | 7080 |  | 13008 | 13009 |  |  | R | NV
| Max kW Demand - Channel 66 | 66 | 7081 |  | 13010 | 13011 |  |  | R | NV
| Max kW Demand - Channel 67 | 67 | 7082 |  | 13012 | 13013 |  |  | R | NV
| Max kW Demand - Channel 68 | 68 | 7083 |  | 13014 | 13015 |  |  | R | NV
| Max kW Demand - Channel 69 | 69 | 7084 |  | 13016 | 13017 |  |  | R | NV
| Max kW Demand - Channel 70 | 70 | 7085 |  | 13018 | 13019 |  |  | R | NV
| Max kW Demand - Channel 71 | 71 | 7086 |  | 13020 | 13021 |  |  | R | NV
| Max kW Demand - Channel 72 | 72 | 7087 |  | 13022 | 13023 |  |  | R | NV
| Max kW Demand - Channel 73 | 73 | 7088 |  | 13024 | 13025 |  |  | R | NV
| Max kW Demand - Channel 74 | 74 | 7089 |  | 13026 | 13027 |  |  | R | NV
| Max kW Demand - Channel 75 | 75 | 7090 |  | 13028 | 13029 |  |  | R | NV
| Max kW Demand - Channel 76 | 76 | 7091 |  | 13030 | 13031 |  |  | R | NV
| Max kW Demand - Channel 77 | 77 | 7092 |  | 13032 | 13033 |  |  | R | NV
| Max kW Demand - Channel 78 | 78 | 7093 |  | 13034 | 13035 |  |  | R | NV
| Max kW Demand - Channel 79 | 79 | 7094 |  | 13036 | 13037 |  |  | R | NV
| Max kW Demand - Channel 80 | 80 | 7095 |  | 13038 | 13039 |  |  | R | NV
| Max kW Demand - Channel 81 | 81 | 7096 |  | 13040 | 13041 |  |  | R | NV
| Max kW Demand - Channel 82 | 82 | 7097 |  | 13042 | 13043 |  |  | R | NV
| Max kW Demand - Channel 83 | 83 | 7098 |  | 13044 | 13045 |  |  | R | NV
| Max kW Demand - Channel 84 | 84 | 7099 |  | 13046 | 13047 |  |  | R | NV
| Max kW Demand - Channel 85 | 85 | 7100 |  | 13048 | 13049 |  |  | R | NV
| Max kW Demand - Channel 86 | 86 | 7101 |  | 13050 | 13051 |  |  | R | NV
| Max kW Demand - Channel 87 | 87 | 7102 |  | 13052 | 13053 |  |  | R | NV
| Max kW Demand - Channel 88 | 88 | 7103 |  | 13054 | 13055 |  |  | R | NV
| Max kW Demand - Channel 89 | 89 | 7104 |  | 13056 | 13057 |  |  | R | NV
| Max kW Demand - Channel 90 | 90 | 7105 |  | 13058 | 13059 |  |  | R | NV
| Max kW Demand - Channel 91 | 91 | 7106 |  | 13060 | 13061 |  |  | R | NV
| Max kW Demand - Channel 92 | 92 | 7107 |  | 13062 | 13063 |  |  | R | NV
| Max kW Demand - Channel 93 | 93 | 7108 |  | 13064 | 13065 |  |  | R | NV
| Max kW Demand - Channel 94 | 94 | 7109 |  | 13066 | 13067 |  |  | R | NV
| Max kW Demand - Channel 95 | 95 | 7110 |  | 13068 | 13069 |  |  | R | NV
| Max kW Demand - Channel 96 | 96 | 7111 |  | 13070 | 13071 |  |  | R | NV
| KWH Snapshot |  | 7112 | 7303 | 13072 | 13263 |  |  | R |  |  |  | 32 bit unsigned integer
| KWH Snapshot - Channel 1 | 1 | 7112 | 7113 | 13072 | 13073 |  |  | R
| KWH Snapshot - Channel 2 | 2 | 7114 | 7115 | 13074 | 13075 |  |  | R
| KWH Snapshot - Channel 3 | 3 | 7116 | 7117 | 13076 | 13077 |  |  | R
| KWH Snapshot - Channel 4 | 4 | 7118 | 7119 | 13078 | 13079 |  |  | R
| KWH Snapshot - Channel 5 | 5 | 7120 | 7121 | 13080 | 13081 |  |  | R
| KWH Snapshot - Channel 6 | 6 | 7122 | 7123 | 13082 | 13083 |  |  | R
| KWH Snapshot - Channel 7 | 7 | 7124 | 7125 | 13084 | 13085 |  |  | R
| KWH Snapshot - Channel 8 | 8 | 7126 | 7127 | 13086 | 13087 |  |  | R
| KWH Snapshot - Channel 9 | 9 | 7128 | 7129 | 13088 | 13089 |  |  | R
| KWH Snapshot - Channel 10 | 10 | 7130 | 7131 | 13090 | 13091 |  |  | R
| KWH Snapshot - Channel 11 | 11 | 7132 | 7133 | 13092 | 13093 |  |  | R
| KWH Snapshot - Channel 12 | 12 | 7134 | 7135 | 13094 | 13095 |  |  | R
| KWH Snapshot - Channel 13 | 13 | 7136 | 7137 | 13096 | 13097 |  |  | R
| KWH Snapshot - Channel 14 | 14 | 7138 | 7139 | 13098 | 13099 |  |  | R
| KWH Snapshot - Channel 15 | 15 | 7140 | 7141 | 13100 | 13101 |  |  | R
| KWH Snapshot - Channel 16 | 16 | 7142 | 7143 | 13102 | 13103 |  |  | R
| KWH Snapshot - Channel 17 | 17 | 7144 | 7145 | 13104 | 13105 |  |  | R
| KWH Snapshot - Channel 18 | 18 | 7146 | 7147 | 13106 | 13107 |  |  | R
| KWH Snapshot - Channel 19 | 19 | 7148 | 7149 | 13108 | 13109 |  |  | R
| KWH Snapshot - Channel 20 | 20 | 7150 | 7151 | 13110 | 13111 |  |  | R
| KWH Snapshot - Channel 21 | 21 | 7152 | 7153 | 13112 | 13113 |  |  | R
| KWH Snapshot - Channel 22 | 22 | 7154 | 7155 | 13114 | 13115 |  |  | R
| KWH Snapshot - Channel 23 | 23 | 7156 | 7157 | 13116 | 13117 |  |  | R
| KWH Snapshot - Channel 24 | 24 | 7158 | 7159 | 13118 | 13119 |  |  | R
| KWH Snapshot - Channel 25 | 25 | 7160 | 7161 | 13120 | 13121 |  |  | R
| KWH Snapshot - Channel 26 | 26 | 7162 | 7163 | 13122 | 13123 |  |  | R
| KWH Snapshot - Channel 27 | 27 | 7164 | 7165 | 13124 | 13125 |  |  | R
| KWH Snapshot - Channel 28 | 28 | 7166 | 7167 | 13126 | 13127 |  |  | R
| KWH Snapshot - Channel 29 | 29 | 7168 | 7169 | 13128 | 13129 |  |  | R
| KWH Snapshot - Channel 30 | 30 | 7170 | 7171 | 13130 | 13131 |  |  | R
| KWH Snapshot - Channel 31 | 31 | 7172 | 7173 | 13132 | 13133 |  |  | R
| KWH Snapshot - Channel 32 | 32 | 7174 | 7175 | 13134 | 13135 |  |  | R
| KWH Snapshot - Channel 33 | 33 | 7176 | 7177 | 13136 | 13137 |  |  | R
| KWH Snapshot - Channel 34 | 34 | 7178 | 7179 | 13138 | 13139 |  |  | R
| KWH Snapshot - Channel 35 | 35 | 7180 | 7181 | 13140 | 13141 |  |  | R
| KWH Snapshot - Channel 36 | 36 | 7182 | 7183 | 13142 | 13143 |  |  | R
| KWH Snapshot - Channel 37 | 37 | 7184 | 7185 | 13144 | 13145 |  |  | R
| KWH Snapshot - Channel 38 | 38 | 7186 | 7187 | 13146 | 13147 |  |  | R
| KWH Snapshot - Channel 39 | 39 | 7188 | 7189 | 13148 | 13149 |  |  | R
| KWH Snapshot - Channel 40 | 40 | 7190 | 7191 | 13150 | 13151 |  |  | R
| KWH Snapshot - Channel 41 | 41 | 7192 | 7193 | 13152 | 13153 |  |  | R
| KWH Snapshot - Channel 42 | 42 | 7194 | 7195 | 13154 | 13155 |  |  | R
| KWH Snapshot - Channel 43 | 43 | 7196 | 7197 | 13156 | 13157 |  |  | R
| KWH Snapshot - Channel 44 | 44 | 7198 | 7199 | 13158 | 13159 |  |  | R
| KWH Snapshot - Channel 45 | 45 | 7200 | 7201 | 13160 | 13161 |  |  | R
| KWH Snapshot - Channel 46 | 46 | 7202 | 7203 | 13162 | 13163 |  |  | R
| KWH Snapshot - Channel 47 | 47 | 7204 | 7205 | 13164 | 13165 |  |  | R
| KWH Snapshot - Channel 48 | 48 | 7206 | 7207 | 13166 | 13167 |  |  | R
| KWH Snapshot - Channel 49 | 49 | 7208 | 7209 | 13168 | 13169 |  |  | R
| KWH Snapshot - Channel 50 | 50 | 7210 | 7211 | 13170 | 13171 |  |  | R
| KWH Snapshot - Channel 51 | 51 | 7212 | 7213 | 13172 | 13173 |  |  | R
| KWH Snapshot - Channel 52 | 52 | 7214 | 7215 | 13174 | 13175 |  |  | R
| KWH Snapshot - Channel 53 | 53 | 7216 | 7217 | 13176 | 13177 |  |  | R
| KWH Snapshot - Channel 54 | 54 | 7218 | 7219 | 13178 | 13179 |  |  | R
| KWH Snapshot - Channel 55 | 55 | 7220 | 7221 | 13180 | 13181 |  |  | R
| KWH Snapshot - Channel 56 | 56 | 7222 | 7223 | 13182 | 13183 |  |  | R
| KWH Snapshot - Channel 57 | 57 | 7224 | 7225 | 13184 | 13185 |  |  | R
| KWH Snapshot - Channel 58 | 58 | 7226 | 7227 | 13186 | 13187 |  |  | R
| KWH Snapshot - Channel 59 | 59 | 7228 | 7229 | 13188 | 13189 |  |  | R
| KWH Snapshot - Channel 60 | 60 | 7230 | 7231 | 13190 | 13191 |  |  | R
| KWH Snapshot - Channel 61 | 61 | 7232 | 7233 | 13192 | 13193 |  |  | R
| KWH Snapshot - Channel 62 | 62 | 7234 | 7235 | 13194 | 13195 |  |  | R
| KWH Snapshot - Channel 63 | 63 | 7236 | 7237 | 13196 | 13197 |  |  | R
| KWH Snapshot - Channel 64 | 64 | 7238 | 7239 | 13198 | 13199 |  |  | R
| KWH Snapshot - Channel 65 | 65 | 7240 | 7241 | 13200 | 13201 |  |  | R
| KWH Snapshot - Channel 66 | 66 | 7242 | 7243 | 13202 | 13203 |  |  | R
| KWH Snapshot - Channel 67 | 67 | 7244 | 7245 | 13204 | 13205 |  |  | R
| KWH Snapshot - Channel 68 | 68 | 7246 | 7247 | 13206 | 13207 |  |  | R
| KWH Snapshot - Channel 69 | 69 | 7248 | 7249 | 13208 | 13209 |  |  | R
| KWH Snapshot - Channel 70 | 70 | 7250 | 7251 | 13210 | 13211 |  |  | R
| KWH Snapshot - Channel 71 | 71 | 7252 | 7253 | 13212 | 13213 |  |  | R
| KWH Snapshot - Channel 72 | 72 | 7254 | 7255 | 13214 | 13215 |  |  | R
| KWH Snapshot - Channel 73 | 73 | 7256 | 7257 | 13216 | 13217 |  |  | R
| KWH Snapshot - Channel 74 | 74 | 7258 | 7259 | 13218 | 13219 |  |  | R
| KWH Snapshot - Channel 75 | 75 | 7260 | 7261 | 13220 | 13221 |  |  | R
| KWH Snapshot - Channel 76 | 76 | 7262 | 7263 | 13222 | 13223 |  |  | R
| KWH Snapshot - Channel 77 | 77 | 7264 | 7265 | 13224 | 13225 |  |  | R
| KWH Snapshot - Channel 78 | 78 | 7266 | 7267 | 13226 | 13227 |  |  | R
| KWH Snapshot - Channel 79 | 79 | 7268 | 7269 | 13228 | 13229 |  |  | R
| KWH Snapshot - Channel 80 | 80 | 7270 | 7271 | 13230 | 13231 |  |  | R
| KWH Snapshot - Channel 81 | 81 | 7272 | 7273 | 13232 | 13233 |  |  | R
| KWH Snapshot - Channel 82 | 82 | 7274 | 7275 | 13234 | 13235 |  |  | R
| KWH Snapshot - Channel 83 | 83 | 7276 | 7277 | 13236 | 13237 |  |  | R
| KWH Snapshot - Channel 84 | 84 | 7278 | 7279 | 13238 | 13239 |  |  | R
| KWH Snapshot - Channel 85 | 85 | 7280 | 7281 | 13240 | 13241 |  |  | R
| KWH Snapshot - Channel 86 | 86 | 7282 | 7283 | 13242 | 13243 |  |  | R
| KWH Snapshot - Channel 87 | 87 | 7284 | 7285 | 13244 | 13245 |  |  | R
| KWH Snapshot - Channel 88 | 88 | 7286 | 7287 | 13246 | 13247 |  |  | R
| KWH Snapshot - Channel 89 | 89 | 7288 | 7289 | 13248 | 13249 |  |  | R
| KWH Snapshot - Channel 90 | 90 | 7290 | 7291 | 13250 | 13251 |  |  | R
| KWH Snapshot - Channel 91 | 91 | 7292 | 7293 | 13252 | 13253 |  |  | R
| KWH Snapshot - Channel 92 | 92 | 7294 | 7295 | 13254 | 13255 |  |  | R
| KWH Snapshot - Channel 93 | 93 | 7296 | 7297 | 13256 | 13257 |  |  | R
| KWH Snapshot - Channel 94 | 94 | 7298 | 7299 | 13258 | 13259 |  |  | R
| KWH Snapshot - Channel 95 | 95 | 7300 | 7301 | 13260 | 13261 |  |  | R
| KWH Snapshot - Channel 96 | 96 | 7302 | 7303 | 13262 | 13263 |  |  | R
| Reserved for Creset Factor |  | 7303 | 7398 | 11920 | 12111 |  |  | R
| Crest Factor - Channel 1 | 1 | 7303 |  | 11920 | 11921 |  |  | R
| Crest Factor - Channel 2 | 2 | 7304 |  | 11922 | 11923 |  |  | R
| Crest Factor - Channel 3 | 3 | 7305 |  | 11924 | 11925 |  |  | R
| Crest Factor - Channel 4 | 4 | 7306 |  | 11926 | 11927 |  |  | R
| Crest Factor - Channel 5 | 5 | 7307 |  | 11928 | 11929 |  |  | R
| Crest Factor - Channel 6 | 6 | 7308 |  | 11930 | 11931 |  |  | R
| Crest Factor - Channel 7 | 7 | 7309 |  | 11932 | 11933 |  |  | R
| Crest Factor - Channel 8 | 8 | 7310 |  | 11934 | 11935 |  |  | R
| Crest Factor - Channel 9 | 9 | 7311 |  | 11936 | 11937 |  |  | R
| Crest Factor - Channel 10 | 10 | 7312 |  | 11938 | 11939 |  |  | R
| Crest Factor - Channel 11 | 11 | 7313 |  | 11940 | 11941 |  |  | R
| Crest Factor - Channel 12 | 12 | 7314 |  | 11942 | 11943 |  |  | R
| Crest Factor - Channel 13 | 13 | 7315 |  | 11944 | 11945 |  |  | R
| Crest Factor - Channel 14 | 14 | 7316 |  | 11946 | 11947 |  |  | R
| Crest Factor - Channel 15 | 15 | 7317 |  | 11948 | 11949 |  |  | R
| Crest Factor - Channel 16 | 16 | 7318 |  | 11950 | 11951 |  |  | R
| Crest Factor - Channel 17 | 17 | 7319 |  | 11952 | 11953 |  |  | R
| Crest Factor - Channel 18 | 18 | 7320 |  | 11954 | 11955 |  |  | R
| Crest Factor - Channel 19 | 19 | 7321 |  | 11956 | 11957 |  |  | R
| Crest Factor - Channel 20 | 20 | 7322 |  | 11958 | 11959 |  |  | R
| Crest Factor - Channel 21 | 21 | 7323 |  | 11960 | 11961 |  |  | R
| Crest Factor - Channel 22 | 22 | 7324 |  | 11962 | 11963 |  |  | R
| Crest Factor - Channel 23 | 23 | 7325 |  | 11964 | 11965 |  |  | R
| Crest Factor - Channel 24 | 24 | 7326 |  | 11966 | 11967 |  |  | R
| Crest Factor - Channel 25 | 25 | 7327 |  | 11968 | 11969 |  |  | R
| Crest Factor - Channel 26 | 26 | 7328 |  | 11970 | 11971 |  |  | R
| Crest Factor - Channel 27 | 27 | 7329 |  | 11972 | 11973 |  |  | R
| Crest Factor - Channel 28 | 28 | 7330 |  | 11974 | 11975 |  |  | R
| Crest Factor - Channel 29 | 29 | 7331 |  | 11976 | 11977 |  |  | R
| Crest Factor - Channel 30 | 30 | 7332 |  | 11978 | 11979 |  |  | R
| Crest Factor - Channel 31 | 31 | 7333 |  | 11980 | 11981 |  |  | R
| Crest Factor - Channel 32 | 32 | 7334 |  | 11982 | 11983 |  |  | R
| Crest Factor - Channel 33 | 33 | 7335 |  | 11984 | 11985 |  |  | R
| Crest Factor - Channel 34 | 34 | 7336 |  | 11986 | 11987 |  |  | R
| Crest Factor - Channel 35 | 35 | 7337 |  | 11988 | 11989 |  |  | R
| Crest Factor - Channel 36 | 36 | 7338 |  | 11990 | 11991 |  |  | R
| Crest Factor - Channel 37 | 37 | 7339 |  | 11992 | 11993 |  |  | R
| Crest Factor - Channel 38 | 38 | 7340 |  | 11994 | 11995 |  |  | R
| Crest Factor - Channel 39 | 39 | 7341 |  | 11996 | 11997 |  |  | R
| Crest Factor - Channel 40 | 40 | 7342 |  | 11998 | 11999 |  |  | R
| Crest Factor - Channel 41 | 41 | 7343 |  | 12000 | 12001 |  |  | R
| Crest Factor - Channel 42 | 42 | 7344 |  | 12002 | 12003 |  |  | R
| Crest Factor - Channel 43 | 43 | 7345 |  | 12004 | 12005 |  |  | R
| Crest Factor - Channel 44 | 44 | 7346 |  | 12006 | 12007 |  |  | R
| Crest Factor - Channel 45 | 45 | 7347 |  | 12008 | 12009 |  |  | R
| Crest Factor - Channel 46 | 46 | 7348 |  | 12010 | 12011 |  |  | R
| Crest Factor - Channel 47 | 47 | 7349 |  | 12012 | 12013 |  |  | R
| Crest Factor - Channel 48 | 48 | 7350 |  | 12014 | 12015 |  |  | R
| Crest Factor - Channel 49 | 49 | 7351 |  | 12016 | 12017 |  |  | R
| Crest Factor - Channel 50 | 50 | 7352 |  | 12018 | 12019 |  |  | R
| Crest Factor - Channel 51 | 51 | 7353 |  | 12020 | 12021 |  |  | R
| Crest Factor - Channel 52 | 52 | 7354 |  | 12022 | 12023 |  |  | R
| Crest Factor - Channel 53 | 53 | 7355 |  | 12024 | 12025 |  |  | R
| Crest Factor - Channel 54 | 54 | 7356 |  | 12026 | 12027 |  |  | R
| Crest Factor - Channel 55 | 55 | 7357 |  | 12028 | 12029 |  |  | R
| Crest Factor - Channel 56 | 56 | 7358 |  | 12030 | 12031 |  |  | R
| Crest Factor - Channel 57 | 57 | 7359 |  | 12032 | 12033 |  |  | R
| Crest Factor - Channel 58 | 58 | 7360 |  | 12034 | 12035 |  |  | R
| Crest Factor - Channel 59 | 59 | 7361 |  | 12036 | 12037 |  |  | R
| Crest Factor - Channel 60 | 60 | 7362 |  | 12038 | 12039 |  |  | R
| Crest Factor - Channel 61 | 61 | 7363 |  | 12040 | 12041 |  |  | R
| Crest Factor - Channel 62 | 62 | 7364 |  | 12042 | 12043 |  |  | R
| Crest Factor - Channel 63 | 63 | 7365 |  | 12044 | 12045 |  |  | R
| Crest Factor - Channel 64 | 64 | 7366 |  | 12046 | 12047 |  |  | R
| Crest Factor - Channel 65 | 65 | 7367 |  | 12048 | 12049 |  |  | R
| Crest Factor - Channel 66 | 66 | 7368 |  | 12050 | 12051 |  |  | R
| Crest Factor - Channel 67 | 67 | 7369 |  | 12052 | 12053 |  |  | R
| Crest Factor - Channel 68 | 68 | 7370 |  | 12054 | 12055 |  |  | R
| Crest Factor - Channel 69 | 69 | 7371 |  | 12056 | 12057 |  |  | R
| Crest Factor - Channel 70 | 70 | 7372 |  | 12058 | 12059 |  |  | R
| Crest Factor - Channel 71 | 71 | 7373 |  | 12060 | 12061 |  |  | R
| Crest Factor - Channel 72 | 72 | 7374 |  | 12062 | 12063 |  |  | R
| Crest Factor - Channel 73 | 73 | 7375 |  | 12064 | 12065 |  |  | R
| Crest Factor - Channel 74 | 74 | 7376 |  | 12066 | 12067 |  |  | R
| Crest Factor - Channel 75 | 75 | 7377 |  | 12068 | 12069 |  |  | R
| Crest Factor - Channel 76 | 76 | 7378 |  | 12070 | 12071 |  |  | R
| Crest Factor - Channel 77 | 77 | 7379 |  | 12072 | 12073 |  |  | R
| Crest Factor - Channel 78 | 78 | 7380 |  | 12074 | 12075 |  |  | R
| Crest Factor - Channel 79 | 79 | 7381 |  | 12076 | 12077 |  |  | R
| Crest Factor - Channel 80 | 80 | 7382 |  | 12078 | 12079 |  |  | R
| Crest Factor - Channel 81 | 81 | 7383 |  | 12080 | 12081 |  |  | R
| Crest Factor - Channel 82 | 82 | 7384 |  | 12082 | 12083 |  |  | R
| Crest Factor - Channel 83 | 83 | 7385 |  | 12084 | 12085 |  |  | R
| Crest Factor - Channel 84 | 84 | 7386 |  | 12086 | 12087 |  |  | R
| Crest Factor - Channel 85 | 85 | 7387 |  | 12088 | 12089 |  |  | R
| Crest Factor - Channel 86 | 86 | 7388 |  | 12090 | 12091 |  |  | R
| Crest Factor - Channel 87 | 87 | 7389 |  | 12092 | 12093 |  |  | R
| Crest Factor - Channel 88 | 88 | 7390 |  | 12094 | 12095 |  |  | R
| Crest Factor - Channel 89 | 89 | 7391 |  | 12096 | 12097 |  |  | R
| Crest Factor - Channel 90 | 90 | 7392 |  | 12098 | 12099 |  |  | R
| Crest Factor - Channel 91 | 91 | 7393 |  | 12100 | 12101 |  |  | R
| Crest Factor - Channel 92 | 92 | 7394 |  | 12102 | 12103 |  |  | R
| Crest Factor - Channel 93 | 93 | 7395 |  | 12104 | 12105 |  |  | R
| Crest Factor - Channel 94 | 94 | 7396 |  | 12106 | 12107 |  |  | R
| Crest Factor - Channel 95 | 95 | 7397 |  | 12108 | 12109 |  |  | R
| Crest Factor - Channel 96 | 96 | 7398 |  | 12110 | 12111 |  |  | R
| Reserved for Temperature |  | 7399 | 7494 | 12112 | 12303 |  |  | R
| Temperature - Channel 1 | 1 | 7399 |  | 12112 | 12113 |  |  | R
| Temperature - Channel 2 | 2 | 7400 |  | 12114 | 12115 |  |  | R
| Temperature - Channel 3 | 3 | 7401 |  | 12116 | 12117 |  |  | R
| Temperature - Channel 4 | 4 | 7402 |  | 12118 | 12119 |  |  | R
| Temperature - Channel 5 | 5 | 7403 |  | 12120 | 12121 |  |  | R
| Temperature - Channel 6 | 6 | 7404 |  | 12122 | 12123 |  |  | R
| Temperature - Channel 7 | 7 | 7405 |  | 12124 | 12125 |  |  | R
| Temperature - Channel 8 | 8 | 7406 |  | 12126 | 12127 |  |  | R
| Temperature - Channel 9 | 9 | 7407 |  | 12128 | 12129 |  |  | R
| Temperature - Channel 10 | 10 | 7408 |  | 12130 | 12131 |  |  | R
| Temperature - Channel 11 | 11 | 7409 |  | 12132 | 12133 |  |  | R
| Temperature - Channel 12 | 12 | 7410 |  | 12134 | 12135 |  |  | R
| Temperature - Channel 13 | 13 | 7411 |  | 12136 | 12137 |  |  | R
| Temperature - Channel 14 | 14 | 7412 |  | 12138 | 12139 |  |  | R
| Temperature - Channel 15 | 15 | 7413 |  | 12140 | 12141 |  |  | R
| Temperature - Channel 16 | 16 | 7414 |  | 12142 | 12143 |  |  | R
| Temperature - Channel 17 | 17 | 7415 |  | 12144 | 12145 |  |  | R
| Temperature - Channel 18 | 18 | 7416 |  | 12146 | 12147 |  |  | R
| Temperature - Channel 19 | 19 | 7417 |  | 12148 | 12149 |  |  | R
| Temperature - Channel 20 | 20 | 7418 |  | 12150 | 12151 |  |  | R
| Temperature - Channel 21 | 21 | 7419 |  | 12152 | 12153 |  |  | R
| Temperature - Channel 22 | 22 | 7420 |  | 12154 | 12155 |  |  | R
| Temperature - Channel 23 | 23 | 7421 |  | 12156 | 12157 |  |  | R
| Temperature - Channel 24 | 24 | 7422 |  | 12158 | 12159 |  |  | R
| Temperature - Channel 25 | 25 | 7423 |  | 12160 | 12161 |  |  | R
| Temperature - Channel 26 | 26 | 7424 |  | 12162 | 12163 |  |  | R
| Temperature - Channel 27 | 27 | 7425 |  | 12164 | 12165 |  |  | R
| Temperature - Channel 28 | 28 | 7426 |  | 12166 | 12167 |  |  | R
| Temperature - Channel 29 | 29 | 7427 |  | 12168 | 12169 |  |  | R
| Temperature - Channel 30 | 30 | 7428 |  | 12170 | 12171 |  |  | R
| Temperature - Channel 31 | 31 | 7429 |  | 12172 | 12173 |  |  | R
| Temperature - Channel 32 | 32 | 7430 |  | 12174 | 12175 |  |  | R
| Temperature - Channel 33 | 33 | 7431 |  | 12176 | 12177 |  |  | R
| Temperature - Channel 34 | 34 | 7432 |  | 12178 | 12179 |  |  | R
| Temperature - Channel 35 | 35 | 7433 |  | 12180 | 12181 |  |  | R
| Temperature - Channel 36 | 36 | 7434 |  | 12182 | 12183 |  |  | R
| Temperature - Channel 37 | 37 | 7435 |  | 12184 | 12185 |  |  | R
| Temperature - Channel 38 | 38 | 7436 |  | 12186 | 12187 |  |  | R
| Temperature - Channel 39 | 39 | 7437 |  | 12188 | 12189 |  |  | R
| Temperature - Channel 40 | 40 | 7438 |  | 12190 | 12191 |  |  | R
| Temperature - Channel 41 | 41 | 7439 |  | 12192 | 12193 |  |  | R
| Temperature - Channel 42 | 42 | 7440 |  | 12194 | 12195 |  |  | R
| Temperature - Channel 43 | 43 | 7441 |  | 12196 | 12197 |  |  | R
| Temperature - Channel 44 | 44 | 7442 |  | 12198 | 12199 |  |  | R
| Temperature - Channel 45 | 45 | 7443 |  | 12200 | 12201 |  |  | R
| Temperature - Channel 46 | 46 | 7444 |  | 12202 | 12203 |  |  | R
| Temperature - Channel 47 | 47 | 7445 |  | 12204 | 12205 |  |  | R
| Temperature - Channel 48 | 48 | 7446 |  | 12206 | 12207 |  |  | R
| Temperature - Channel 49 | 49 | 7447 |  | 12208 | 12209 |  |  | R
| Temperature - Channel 50 | 50 | 7448 |  | 12210 | 12211 |  |  | R
| Temperature - Channel 51 | 51 | 7449 |  | 12212 | 12213 |  |  | R
| Temperature - Channel 52 | 52 | 7450 |  | 12214 | 12215 |  |  | R
| Temperature - Channel 53 | 53 | 7451 |  | 12216 | 12217 |  |  | R
| Temperature - Channel 54 | 54 | 7452 |  | 12218 | 12219 |  |  | R
| Temperature - Channel 55 | 55 | 7453 |  | 12220 | 12221 |  |  | R
| Temperature - Channel 56 | 56 | 7454 |  | 12222 | 12223 |  |  | R
| Temperature - Channel 57 | 57 | 7455 |  | 12224 | 12225 |  |  | R
| Temperature - Channel 58 | 58 | 7456 |  | 12226 | 12227 |  |  | R
| Temperature - Channel 59 | 59 | 7457 |  | 12228 | 12229 |  |  | R
| Temperature - Channel 60 | 60 | 7458 |  | 12230 | 12231 |  |  | R
| Temperature - Channel 61 | 61 | 7459 |  | 12232 | 12233 |  |  | R
| Temperature - Channel 62 | 62 | 7460 |  | 12234 | 12235 |  |  | R
| Temperature - Channel 63 | 63 | 7461 |  | 12236 | 12237 |  |  | R
| Temperature - Channel 64 | 64 | 7462 |  | 12238 | 12239 |  |  | R
| Temperature - Channel 65 | 65 | 7463 |  | 12240 | 12241 |  |  | R
| Temperature - Channel 66 | 66 | 7464 |  | 12242 | 12243 |  |  | R
| Temperature - Channel 67 | 67 | 7465 |  | 12244 | 12245 |  |  | R
| Temperature - Channel 68 | 68 | 7466 |  | 12246 | 12247 |  |  | R
| Temperature - Channel 69 | 69 | 7467 |  | 12248 | 12249 |  |  | R
| Temperature - Channel 70 | 70 | 7468 |  | 12250 | 12251 |  |  | R
| Temperature - Channel 71 | 71 | 7469 |  | 12252 | 12253 |  |  | R
| Temperature - Channel 72 | 72 | 7470 |  | 12254 | 12255 |  |  | R
| Temperature - Channel 73 | 73 | 7471 |  | 12256 | 12257 |  |  | R
| Temperature - Channel 74 | 74 | 7472 |  | 12258 | 12259 |  |  | R
| Temperature - Channel 75 | 75 | 7473 |  | 12260 | 12261 |  |  | R
| Temperature - Channel 76 | 76 | 7474 |  | 12262 | 12263 |  |  | R
| Temperature - Channel 77 | 77 | 7475 |  | 12264 | 12265 |  |  | R
| Temperature - Channel 78 | 78 | 7476 |  | 12266 | 12267 |  |  | R
| Temperature - Channel 79 | 79 | 7477 |  | 12268 | 12269 |  |  | R
| Temperature - Channel 80 | 80 | 7478 |  | 12270 | 12271 |  |  | R
| Temperature - Channel 81 | 81 | 7479 |  | 12272 | 12273 |  |  | R
| Temperature - Channel 82 | 82 | 7480 |  | 12274 | 12275 |  |  | R
| Temperature - Channel 83 | 83 | 7481 |  | 12276 | 12277 |  |  | R
| Temperature - Channel 84 | 84 | 7482 |  | 12278 | 12279 |  |  | R
| Temperature - Channel 85 | 85 | 7483 |  | 12280 | 12281 |  |  | R
| Temperature - Channel 86 | 86 | 7484 |  | 12282 | 12283 |  |  | R
| Temperature - Channel 87 | 87 | 7485 |  | 12284 | 12285 |  |  | R
| Temperature - Channel 88 | 88 | 7486 |  | 12286 | 12287 |  |  | R
| Temperature - Channel 89 | 89 | 7487 |  | 12288 | 12289 |  |  | R
| Temperature - Channel 90 | 90 | 7488 |  | 12290 | 12291 |  |  | R
| Temperature - Channel 91 | 91 | 7489 |  | 12292 | 12293 |  |  | R
| Temperature - Channel 92 | 92 | 7490 |  | 12294 | 12295 |  |  | R
| Temperature - Channel 93 | 93 | 7491 |  | 12296 | 12297 |  |  | R
| Temperature - Channel 94 | 94 | 7492 |  | 12298 | 12299 |  |  | R
| Temperature - Channel 95 | 95 | 7493 |  | 12300 | 12301 |  |  | R
| Temperature - Channel 96 | 96 | 7494 |  | 12302 | 12303 |  |  | R
Reading by Circuit | Circuit #1 | 1 | 15000 | 15276 | 15300 | 15489 | [6 empty] | Add 500 for next Circuit
Circuit Configuration
| Circuit Name (32 Register) |  | 15000 | 15031
| # of Channels Assigned |  | 15032
| Assigned Channel |  | 15033 | 15035
| Channel 1 |  | 15033
| Channel 2 |  | 15034
| Channel 3 |  | 15035
| CT Size |  | 15036 | 15038
| CT Size - Assigned Channel 1 |  | 15036
| CT Size - Assigned Channel 2 |  | 15037
| CT Size - Assigned Channel 3 |  | 15038
| Breaker Size |  | 15039 | 15041
| Breaker Size - Assigned Channel 1 |  | 15039
| Breaker Size - Assigned Channel 2 |  | 15040
| Breaker Size - Assigned Channel 3 |  | 15041
| Voltage Phase |  | 15042 | 15044
| Voltage Phase - Assigned Channel 1 |  | 15042
| Voltage Phase - Assigned Channel 2 |  | 15043
| Voltage Phase - Assigned Channel 3 |  | 15044
| Reset/Command All Phases |  | 15045
| Reset/Command |  | 15046 | 15048
| Reset/Command - Assigned Channel 1 |  | 15046
| Reset/Command - Assigned Channel 2 |  | 15047
| Reset/Command - Assigned Channel 3 |  | 15048
| CT Type/Compensation |  | 15049 | 15051
| CT Type/Compensation - Assigned Channel 1 |  | 15049
| CT Type/Compensation - Assigned Channel 2 |  | 15050
| CT Type/Compensation - Assigned Channel 3 |  | 15051
Total |  |  | 15100
| Energy Scale |  | 15100
| Power Scale |  | 15101
| Current Scale |  | 15102
| Voltage Scale |  | 15103
| Alarm Status - Latching |  | 15104
| Alarm Status - Non-Latching |  | 15105
| Frequency |  | 15106 |  | 15300 | 15301
| Voltages LN Average |  | 15107 |  | 15302 | 15303
| Voltage LL Average |  | 15108 |  | 15304 | 15305
| kWh |  | 15109 | 15110 | 15306 | 15307
| kVARh |  | 15111 | 15112 | 15308 | 15309
| kVAh |  | 15113 | 15114 | 15310 | 15311
| kW |  | 15114 |  | 15312 | 15313
| kVAR |  | 15115 |  | 15314 | 15315
| kVA |  | 15116 |  | 15316 | 15317
| Current |  | 15117 |  | 15318 | 15319
| Power Factor |  | 15118 |  | 15320 | 15321
| Current Angle |  | 15119 |  | 15322 | 15323
| Percent THD |  | 15120 |  | 15324 | 15325
| Max Current |  | 15121 |  | 15326 | 15327
| Max kW |  | 15122 |  | 15328 | 15329
| Current Demand |  | 15123 |  | 15330 | 15331
| kW Demand |  | 15124 |  | 15332 | 15333
| Max Current Demand |  | 15125 |  | 15334 | 15335
| Max kW Demand |  | 15126 |  | 15336 | 15337
| KWH Snapshot |  | 15127 | 15128 | 15338 | 15339
| Reserved for Creset Factor |  | 15128 |  | 15340 | 15341
| Reserved for Zero Current |  | 15129 |  | 15342 | 15343
| Reserved for Temperature |  | 15130 |  | 15344 | 15345
Channel 1
| Energy Scale |  | 15150
| Power Scale |  | 15150
| Current Scale |  | 15151
| Voltage Scale |  | 15152
| Alarm Status - Latching |  | 15153
| Alarm Status - Non-Latching |  | 15154
| kWh |  | 15155 | 15156 | 15350 | 15351
| kVARh |  | 15157 | 15158 | 15352 | 15353
| kVAh |  | 15159 | 15160 | 15354 | 15355
| kW |  | 15160 |  | 15356 | 15357
| kVAR |  | 15161 |  | 15358 | 15359
| kVA |  | 15162 |  | 15360 | 15361
| Current |  | 15163 |  | 15362 | 15363
| Power Factor |  | 15164 |  | 15364 | 15365
| Current Angle |  | 15165 |  | 15366 | 15367
| Percent THD |  | 15166 |  | 15368 | 15369
| Max Current |  | 15167 |  | 15370 | 15371
| Max kW |  | 15168 |  | 15372 | 15373
| Current Demand |  | 15169 |  | 15374 | 15375
| kW Demand |  | 15170 |  | 15376 | 15377
| Max Current Demand |  | 15171 |  | 15378 | 15379
| Max kW Demand |  | 15172 |  | 15380 | 15381
| KWH Snapshot |  | 15173 | 15174 | 15382 | 15383
| Reserved for Creset Factor |  | 15174 |  | 15384 | 15385
| Reserved for Zero Current |  | 15175 |  | 15386 | 15387
| Reserved for Temperature |  | 15176 |  | 15388 | 15389
Channel 2
| Energy Scale |  | 15200
| Power Scale |  | 15200
| Current Scale |  | 15201
| Voltage Scale |  | 15202
| Alarm Status - Latching |  | 15203
| Alarm Status - Non-Latching |  | 15204
| kWh |  | 15205 | 15206 | 15400 | 15401
| kVARh |  | 15207 | 15208 | 15402 | 15403
| kVAh |  | 15209 | 15210 | 15404 | 15405
| kW |  | 15210 |  | 15406 | 15407
| kVAR |  | 15211 |  | 15408 | 15409
| kVA |  | 15212 |  | 15410 | 15411
| Current |  | 15213 |  | 15412 | 15413
| Power Factor |  | 15214 |  | 15414 | 15415
| Current Angle |  | 15215 |  | 15416 | 15417
| Percent THD |  | 15216 |  | 15418 | 15419
| Max Current |  | 15217 |  | 15420 | 15421
| Max kW |  | 15218 |  | 15422 | 15423
| Current Demand |  | 15219 |  | 15424 | 15425
| kW Demand |  | 15220 |  | 15426 | 15427
| Max Current Demand |  | 15221 |  | 15428 | 15429
| Max kW Demand |  | 15222 |  | 15430 | 15431
| KWH Snapshot |  | 15223 | 15224 | 15432 | 15433
| Reserved for Creset Factor |  | 15224 |  | 15434 | 15435
| Reserved for Zero Current |  | 15225 |  | 15436 | 15437
| Reserved for Temperature |  | 15226 |  | 15438 | 15439
Channel 3
| Energy Scale |  | 15250
| Power Scale |  | 15250
| Current Scale |  | 15251
| Voltage Scale |  | 15252
| Alarm Status - Latching |  | 15253
| Alarm Status - Non-Latching |  | 15254
| kWh |  | 15255 | 15256 | 15450 | 15451
| kVARh |  | 15257 | 15258 | 15452 | 15453
| kVAh |  | 15259 | 15260 | 15454 | 15455
| kW |  | 15260 |  | 15456 | 15457
| kVAR |  | 15261 |  | 15458 | 15459
| kVA |  | 15262 |  | 15460 | 15461
| Current |  | 15263 |  | 15462 | 15463
| Power Factor |  | 15264 |  | 15464 | 15465
| Current Angle |  | 15265 |  | 15466 | 15467
| Percent THD |  | 15266 |  | 15468 | 15469
| Max Current |  | 15267 |  | 15470 | 15471
| Max kW |  | 15268 |  | 15472 | 15473
| Current Demand |  | 15269 |  | 15474 | 15475
| kW Demand |  | 15270 |  | 15476 | 15477
| Max Current Demand |  | 15271 |  | 15478 | 15479
| Max kW Demand |  | 15272 |  | 15480 | 15481
| KWH Snapshot |  | 15273 | 15274 | 15482 | 15483
| Reserved for Creset Factor |  | 15274 |  | 15484 | 15485
| Reserved for Zero Current |  | 15275 |  | 15486 | 15487
| Reserved for Temperature |  | 15276 |  | 15488 | 15489
| Circuit #2 | 2 | 15500 | 15776 | 15800 | 15989
| Circuit #3 | 3 | 16000 | 16276 | 16300 | 16489
| Circuit #4 | 4 | 16500 | 16776 | 16800 | 16989
| Circuit #5 | 5 | 17000 | 17276 | 17300 | 17489
| Circuit #6 | 6 | 17500 | 17776 | 17800 | 17989
| Circuit #7 | 7 | 18000 | 18276 | 18300 | 18489
| Circuit #8 | 8 | 18500 | 18776 | 18800 | 18989
| Circuit #9 | 9 | 19000 | 19276 | 19300 | 19489
| Circuit #10 | 10 | 19500 | 19776 | 19800 | 19989
| Circuit #11 | 11 | 20000 | 20276 | 20300 | 20489
| Circuit #12 | 12 | 20500 | 20776 | 20800 | 20989
| Circuit #13 | 13 | 21000 | 21276 | 21300 | 21489
| Circuit #14 | 14 | 21500 | 21776 | 21800 | 21989
| Circuit #15 | 15 | 22000 | 22276 | 22300 | 22489
| Circuit #16 | 16 | 22500 | 22776 | 22800 | 22989
| Circuit #17 | 17 | 23000 | 23276 | 23300 | 23489
| Circuit #18 | 18 | 23500 | 23776 | 23800 | 23989
| Circuit #19 | 19 | 24000 | 24276 | 24300 | 24489
| Circuit #20 | 20 | 24500 | 24776 | 24800 | 24989
| Circuit #21 | 21 | 25000 | 25276 | 25300 | 25489
| Circuit #22 | 22 | 25500 | 25776 | 25800 | 25989
| Circuit #23 | 23 | 26000 | 26276 | 26300 | 26489
| Circuit #24 | 24 | 26500 | 26776 | 26800 | 26989
| Circuit #25 | 25 | 27000 | 27276 | 27300 | 27489
| Circuit #26 | 26 | 27500 | 27776 | 27800 | 27989
| Circuit #27 | 27 | 28000 | 28276 | 28300 | 28489
| Circuit #28 | 28 | 28500 | 28776 | 28800 | 28989
| Circuit #29 | 29 | 29000 | 29276 | 29300 | 29489
| Circuit #30 | 30 | 29500 | 29776 | 29800 | 29989
| Circuit #31 | 31 | 30000 | 30276 | 30300 | 30489
| Circuit #32 | 32 | 30500 | 30776 | 30800 | 30989
| Circuit #33 | 33 | 31000 | 31276 | 31300 | 31489
| Circuit #34 | 34 | 31500 | 31776 | 31800 | 31989
| Circuit #35 | 35 | 32000 | 32276 | 32300 | 32489
| Circuit #36 | 36 | 32500 | 32776 | 32800 | 32989
| Circuit #37 | 37 | 33000 | 33276 | 33300 | 33489
| Circuit #38 | 38 | 33500 | 33776 | 33800 | 33989
| Circuit #39 | 39 | 34000 | 34276 | 34300 | 34489
| Circuit #40 | 40 | 34500 | 34776 | 34800 | 34989
| Circuit #41 | 41 | 35000 | 35276 | 35300 | 35489
| Circuit #42 | 42 | 35500 | 35776 | 35800 | 35989
| Circuit #43 | 43 | 36000 | 36276 | 36300 | 36489
| Circuit #44 | 44 | 36500 | 36776 | 36800 | 36989
| Circuit #45 | 45 | 37000 | 37276 | 37300 | 37489
| Circuit #46 | 46 | 37500 | 37776 | 37800 | 37989
| Circuit #47 | 47 | 38000 | 38276 | 38300 | 38489
| Circuit #48 | 48 | 38500 | 38776 | 38800 | 38989
| Circuit #49 | 49 | 39000 | 39276 | 39300 | 39489
| Circuit #50 | 50 | 39500 | 39776 | 39800 | 39989
| Circuit #51 | 51 | 40000 | 40276 | 40300 | 40489
| Circuit #52 | 52 | 40500 | 40776 | 40800 | 40989
| Circuit #53 | 53 | 41000 | 41276 | 41300 | 41489
| Circuit #54 | 54 | 41500 | 41776 | 41800 | 41989
| Circuit #55 | 55 | 42000 | 42276 | 42300 | 42489
| Circuit #56 | 56 | 42500 | 42776 | 42800 | 42989
| Circuit #57 | 57 | 43000 | 43276 | 43300 | 43489
| Circuit #58 | 58 | 43500 | 43776 | 43800 | 43989
| Circuit #59 | 59 | 44000 | 44276 | 44300 | 44489
| Circuit #60 | 60 | 44500 | 44776 | 44800 | 44989
| Circuit #61 | 61 | 45000 | 45276 | 45300 | 45489
| Circuit #62 | 62 | 45500 | 45776 | 45800 | 45989
| Circuit #63 | 63 | 46000 | 46276 | 46300 | 46489
| Circuit #64 | 64 | 46500 | 46776 | 46800 | 46989
| Circuit #65 | 65 | 47000 | 47276 | 47300 | 47489
| Circuit #66 | 66 | 47500 | 47776 | 47800 | 47989
| Circuit #67 | 67 | 48000 | 48276 | 48300 | 48489
| Circuit #68 | 68 | 48500 | 48776 | 48800 | 48989
| Circuit #69 | 69 | 49000 | 49276 | 49300 | 49489
| Circuit #70 | 70 | 49500 | 49776 | 49800 | 49989
| Circuit #71 | 71 | 50000 | 50276 | 50300 | 50489
| Circuit #72 | 72 | 50500 | 50776 | 50800 | 50989
| Circuit #73 | 73 | 51000 | 51276 | 51300 | 51489
| Circuit #74 | 74 | 51500 | 51776 | 51800 | 51989
| Circuit #75 | 75 | 52000 | 52276 | 52300 | 52489
| Circuit #76 | 76 | 52500 | 52776 | 52800 | 52989
| Circuit #77 | 77 | 53000 | 53276 | 53300 | 53489
| Circuit #78 | 78 | 53500 | 53776 | 53800 | 53989
| Circuit #79 | 79 | 54000 | 54276 | 54300 | 54489
| Circuit #80 | 80 | 54500 | 54776 | 54800 | 54989
| Circuit #81 | 81 | 55000 | 55276 | 55300 | 55489
| Circuit #82 | 82 | 55500 | 55776 | 55800 | 55989
| Circuit #83 | 83 | 56000 | 56276 | 56300 | 56489
| Circuit #84 | 84 | 56500 | 56776 | 56800 | 56989
| Circuit #85 | 85 | 57000 | 57276 | 57300 | 57489
| Circuit #86 | 86 | 57500 | 57776 | 57800 | 57989
| Circuit #87 | 87 | 58000 | 58276 | 58300 | 58489
| Circuit #88 | 88 | 58500 | 58776 | 58800 | 58989
| Circuit #89 | 89 | 59000 | 59276 | 59300 | 59489
| Circuit #90 | 90 | 59500 | 59776 | 59800 | 59989
| Circuit #91 | 91 | 60000 | 60276 | 60300 | 60489
| Circuit #92 | 92 | 60500 | 60776 | 60800 | 60989
| Circuit #93 | 93 | 61000 | 61276 | 61300 | 61489
| Circuit #94 | 94 | 61500 | 61776 | 61800 | 61989
| Circuit #95 | 95 | 62000 | 62276 | 62300 | 62489
| Circuit #96 | 96 | 62500 | 62776 | 62800 | 62989