## Pointmap
|  |  | Modbus Registers | [5 empty] | Bacnet Objects
|  |  | Integer |  |  |  | Float
| Description | # | Start (MSW) | End (LSW) | Scale | Type | MSW | LSW | Object Type | Instance # | R/W | NV | Units | Range | Notes
Meter Information
| Serial Number |  | 1 | 2 |  | UINT32 |  |  | Device Object | Serial_Number | R | NV
| Bootloader Version |  | 3 |  |  | UINT16 |  |  |  |  | R | NV
| Firmware Version |  | 4 |  |  | UINT16 |  |  | Device Object | Firmware_Revision | R | NV
| Device ID |  | 5 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 15172, 22000 | 15172 = Schneider Pointmap, 22000 = Incusense Pointmap (This Document)
| Power Up Counter |  | 6 |  |  | UINT16 |  |  |  |  | R | NV
| Uptime |  | 7 | 8 |  | UINT32 |  |  |  |  | R | NV | Seconds
| Device Health |  | 9 | [7 empty] | R | NV
| Smart Product ID #1 |  | 10 |  |  | UINT16 |  |  |  |  | R | NV |  | See Notes | 0=Nothing Connected, 1=MCM CT Card, 2=21 CT Strip 3 Aux(V1),3=18 CT Strip 3 Aux(V1), 4=Floating CT Strip, 5=23 CT Strip 1 Aux, 6=24 CT Strip, 7=Schneider Adapter, 8=21 CT Strip 3 Aux(V2), 9=18 CT Strip 3 Aux(V2), 10=Digital Input, 11=18 CT Strip 3 Aux(VP), 12=21 CT Strip 3 Aux(VP), 13=23 CT Strip 1 Aux(VP), 14=24 CT Strip(VP), 15=Busway 6CT, 16=Busway 3CT (VP) Indicates Product Supports Voltage Presence
| Smart Product ID #2 |  | 11 |  |  | UINT16 |  |  |  |  | R | NV
| Smart Product ID #3 |  | 12 |  |  | UINT16 |  |  |  |  | R | NV
| Smart Product ID #4 |  | 13 |  |  | UINT16 |  |  |  |  | R | NV
| Smart Port #1 Serial Number |  | 14 | 15 |  | UINT32 |  |  |  |  | R | NV |  |  | The Serial Number of the first device connected to the Smart Port will be displayed when multiple devices (i.e. Busway) are dasiy chained. Refer to Smart Port registers, starting at register 1942 for information about all devices connected to Smart Port.
| Smart Port #2 Serial Number |  | 16 | 17 |  | UINT32 |  |  |  |  | R | NV
| Smart Port #3 Serial Number |  | 18 | 19 |  | UINT32 |  |  |  |  | R | NV
| Smart Port #4 Serial Number |  | 20 | 21 |  | UINT32 |  |  |  |  | R | NV
| Smart Port #1 Firmware Version |  | 22 |  |  | UINT16 |  |  |  |  | R | NV |  |  | The Firmware Version of the first device connected to the Smart Port will be displayed when multiple devices (i.e. Busway) are daisy chained. Refer to Smart Port registers, starting at register 1942 for information about all devices connected to Smart Port.
| Smart Port #2 Firmware Version |  | 23 |  |  | UINT16 |  |  |  |  | R | NV
| Smart Port #3 Firmware Version |  | 24 |  |  | UINT16 |  |  |  |  | R | NV
| Smart Port #4 Firmware Version |  | 25 |  |  | UINT16 |  |  |  |  | R | NV
| MAC Address (Bit 33-48) |  | 26 | [5 empty] | Network Port | 1 | R | NV
| MAC Address (Bit 17-32) |  | 27 | [7 empty] | R | NV
| MAC Address (Bit 1-16) |  | 28 | [7 empty] | R | NV
| Brand Name (16 Registers) |  | 29 | 44 | [6 empty] | R | NV |  |  | Brand Name, Model Name and Device Name supports up to 32 characters (16 registers)
| Model Name (16 Register) |  | 45 | 60 |  |  |  |  | Device Object | Model_Name | R | NV
| Device Name (16 Registers) |  | 61 | 76 |  |  |  |  | Device Object | Object_Name | R/W | NV
Meter Configuration
| Demand # of Sub-Intervals |  | 100 |  |  | UINT16 |  |  | Analog Value | 1 | R/W | NV |  | 1 - 6
| Demand Sub-Interval Length |  | 101 |  |  | UINT16 |  |  | Analog Value | 2 | R/W | NV | Seconds | 0, 10 - 32767 | 0 = Sync to Comms
| Demand Time Stamp (Year) |  | 102 |  |  | UINT16 |  |  |  |  | R |  | Year |  | Years since 1900 (118 = 2018)
| Demand Time Stamp (Month) |  | 103 |  |  | UINT16 |  |  |  |  | R |  | Month | 0 - 11 | Month (0 = January)
| Demand Time Stamp (Day) |  | 104 |  |  | UINT16 |  |  |  |  | R |  | Day | 1 - 31 | Day of the Month
| Demand Time Stamp (Weekday) |  | 105 |  |  | UINT16 |  |  |  |  | R |  | Weekday | 0 - 6 | Weekday (1 = Monday)
| Demand Time Stamp (Hour) |  | 106 |  |  | UINT16 |  |  |  |  | R |  | Hour | 0 - 23 | Hour (13 = 1PM)
| Demand Time Stamp (Minute) |  | 107 |  |  | UINT16 |  |  |  |  | R |  | Minute | 0 - 59 | Minute
| Demand Time Stamp (Second) |  | 108 |  |  | UINT16 |  |  |  |  | R |  | Seconds | 0 - 59 | Second
Writing to RTC will disable NTP by clearing out URL and/or IP Address
| Real Time Clock (Year) |  | 109 |  |  | UINT16 |  |  | Device Object | Local_Date | R/W |  | Year |  | Years since 1900 (118 = 2018)
| Real Time Clock (Month) |  | 110 |  |  | UINT16 |  |  |  |  | R/W |  | Month | 0 - 11 | Month (0 = January)
| Real Time Clock (Day) |  | 111 |  |  | UINT16 |  |  |  |  | R/W |  | Day | 1 - 31 | Day of the Month
| Real Time Clock (Weekday) |  | 112 |  |  | UINT16 |  |  |  |  | R/W |  | Weekday | 0 - 6 | Weekday (1 = Monday)
| Real Time Clock (Hour) |  | 113 |  |  | UINT16 |  |  | Device Object | Local_Time | R/W |  | Hour | 0 - 23 | Hour (13 = 1PM)
| Real Time Clock (Min) |  | 114 |  |  | UINT16 |  |  |  |  | R/W |  | Minute | 0 - 59 | Minute
| Real Time Clock (Second) |  | 115 |  |  | UINT16 |  |  |  |  | R/W |  | Seconds | 0 - 59 | Second
| Digital Output #1 |  | 116 | [5 empty] | Binary Output | 1 | R/W |  |  | 0, 1
| Digital Output #2 |  | 117 | [5 empty] | Binary Output | 2 | R/W |  |  | 0, 1
| Digital Input #1 State |  | 118 | [5 empty] | Binary Input | 1 | R |  |  | 0, 1
| Digital Input #2 State |  | 119 | [5 empty] | Binary Input | 2 | R |  |  | 0, 1
| Digital Input #1 Counter |  | 120 | 121 |  | UINT32 |  |  |  |  | R/W | NV
| Digital Input #1 Counter |  | 122 | 123 |  | UINT32 |  |  |  |  | R/W | NV
| Modbus Slave Address |  | 124 |  |  | UINT16 |  |  |  |  | R/W | NV |  | 1 - 254
| Modbus TCP Port |  | 125 |  |  | UINT16 |  |  |  |  | R | NV |  | 502
| IP Address |  | 126 | 127 |  |  |  |  | Network Port | 1 | R/W | NV |  |  | Meter must be rebooted for new network settings to affect. Device can be rebooted remotely using Global Reset/Command (Register 192)
| Gateway |  | 128 | 129 | [6 empty] | R/W | NV
| Mask |  | 130 | 131 | [6 empty] | R/W | NV
| NTP |  | 132 | 133 | [6 empty] | R/W | NV |  |  | Write to NTP register over Modbus will clear the NTP string in webserver
| DNS |  | 134 | 135 | [6 empty] | R/W | NV
| DNS 2 |  | 136 | 137 | [6 empty] | R | NV
| SMTP |  | 138 | 139 | [6 empty] | R | NV
| Baudrate |  | 140 | 141 |  | UINT32 |  |  |  |  | R/W | NV | Baud | 0 - 4 | 0 = 9600, 1 = 19200, 2 = 38400, 3 = 57600, 4 = 76800 (Value can be written to MSW or LSW)
| Parity |  | 142 | [7 empty] | R | NV
| Stop Bits |  | 143 | [7 empty] | R | NV
| Dip Switch Enabled |  | 144 | [7 empty] | R/W | NV |  | 0, 1 | Bit0 - Enables Dipswitch for setting Modbus slave address
| Dips Switch Value |  | 145 |  |  | UINT16 |  |  |  |  | R |  |  |  | When Dip Switch is enabled, this value is used for Modbus Slave Address
| RS485 Gateway Passthrough Enabled |  | 146 | [7 empty] | R | NV
| Panel 1 (Smart Port 1&2) Configuration |  | 147 | [5 empty] | Analog Value | 3 | R/W | NV |  | 0 - 4 | 0 = Top Feed, 1 = Bottom Feed, 2 = Single Row Sequential, 3 = Single Row Odd/Even, 4 = Sequential
| Panel 2 (Smart Port 3&4) Configuration |  | 148 | [5 empty] | Analog Value | 4 | R/W | NV |  | 0 - 4
| CT Compensation Enabled |  | 149 | [5 empty] | Analog Value | 5 | R/W | NV |  | 0 - 3 | Bit0 - Enable CT Compensation for 1/3V CTs Bit1 - Legacy CT Compensation (Only used for Schneider Addapter Board)
Circuit Configuration
Global
| Global CT Size |  | 190 |  |  | UINT16 |  |  | Analog Value | 6 | R/W | NV |  | 0 - 32000 | (Always Reads 0) Writing this register will set all branches to same CT size
| Global Breaker Size |  | 191 |  |  | UINT16 |  |  | Analog Value | 7 | R/W | NV |  | 0 - 32000 | (Always Reads 0) Writing this register will set all branches to same breaker size
| Global Reset/Command |  | 192 |  |  | UINT16 |  |  | Analog Value | 8 | R/W | NV |  | See Notes | 12345 = Reboot Device, 20097 = Reset Max Demand, 24658 = Clear True Meter Assignment 24659 = Reset True Meter to Default, 26012 = New Demand SubInterval 26013 = Reset Demand, 29877 = Reset Max kW and Current, 31010 = Clear All Latching Alarms, 32123 = Start Waveform Capture (All Circuits)
| Global CT Type/Compensation |  | 193 | [5 empty] | Analog Value | 9 | R/W | NV |  |  | Not Yet Support (Always Reads 0)
| CT Size |  | 200 | 295 |  | UINT16 |  |  | Analog Value | 10 - 105 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 1 | 1 | 200 |  |  | UINT16 |  |  | Analog Value | 10 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 2 | 2 | 201 |  |  | UINT16 |  |  | Analog Value | 11 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 3 | 3 | 202 |  |  | UINT16 |  |  | Analog Value | 12 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 4 | 4 | 203 |  |  | UINT16 |  |  | Analog Value | 13 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 5 | 5 | 204 |  |  | UINT16 |  |  | Analog Value | 14 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 6 | 6 | 205 |  |  | UINT16 |  |  | Analog Value | 15 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 7 | 7 | 206 |  |  | UINT16 |  |  | Analog Value | 16 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 8 | 8 | 207 |  |  | UINT16 |  |  | Analog Value | 17 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 9 | 9 | 208 |  |  | UINT16 |  |  | Analog Value | 18 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 10 | 10 | 209 |  |  | UINT16 |  |  | Analog Value | 19 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 11 | 11 | 210 |  |  | UINT16 |  |  | Analog Value | 20 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 12 | 12 | 211 |  |  | UINT16 |  |  | Analog Value | 21 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 13 | 13 | 212 |  |  | UINT16 |  |  | Analog Value | 22 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 14 | 14 | 213 |  |  | UINT16 |  |  | Analog Value | 23 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 15 | 15 | 214 |  |  | UINT16 |  |  | Analog Value | 24 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 16 | 16 | 215 |  |  | UINT16 |  |  | Analog Value | 25 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 17 | 17 | 216 |  |  | UINT16 |  |  | Analog Value | 26 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 18 | 18 | 217 |  |  | UINT16 |  |  | Analog Value | 27 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 19 | 19 | 218 |  |  | UINT16 |  |  | Analog Value | 28 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 20 | 20 | 219 |  |  | UINT16 |  |  | Analog Value | 29 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 21 | 21 | 220 |  |  | UINT16 |  |  | Analog Value | 30 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 22 | 22 | 221 |  |  | UINT16 |  |  | Analog Value | 31 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 23 | 23 | 222 |  |  | UINT16 |  |  | Analog Value | 32 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 24 | 24 | 223 |  |  | UINT16 |  |  | Analog Value | 33 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 25 | 25 | 224 |  |  | UINT16 |  |  | Analog Value | 34 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 26 | 26 | 225 |  |  | UINT16 |  |  | Analog Value | 35 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 27 | 27 | 226 |  |  | UINT16 |  |  | Analog Value | 36 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 28 | 28 | 227 |  |  | UINT16 |  |  | Analog Value | 37 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 29 | 29 | 228 |  |  | UINT16 |  |  | Analog Value | 38 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 30 | 30 | 229 |  |  | UINT16 |  |  | Analog Value | 39 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 31 | 31 | 230 |  |  | UINT16 |  |  | Analog Value | 40 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 32 | 32 | 231 |  |  | UINT16 |  |  | Analog Value | 41 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 33 | 33 | 232 |  |  | UINT16 |  |  | Analog Value | 42 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 34 | 34 | 233 |  |  | UINT16 |  |  | Analog Value | 43 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 35 | 35 | 234 |  |  | UINT16 |  |  | Analog Value | 44 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 36 | 36 | 235 |  |  | UINT16 |  |  | Analog Value | 45 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 37 | 37 | 236 |  |  | UINT16 |  |  | Analog Value | 46 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 38 | 38 | 237 |  |  | UINT16 |  |  | Analog Value | 47 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 39 | 39 | 238 |  |  | UINT16 |  |  | Analog Value | 48 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 40 | 40 | 239 |  |  | UINT16 |  |  | Analog Value | 49 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 41 | 41 | 240 |  |  | UINT16 |  |  | Analog Value | 50 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 42 | 42 | 241 |  |  | UINT16 |  |  | Analog Value | 51 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 43 | 43 | 242 |  |  | UINT16 |  |  | Analog Value | 52 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 44 | 44 | 243 |  |  | UINT16 |  |  | Analog Value | 53 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 45 | 45 | 244 |  |  | UINT16 |  |  | Analog Value | 54 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 46 | 46 | 245 |  |  | UINT16 |  |  | Analog Value | 55 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 47 | 47 | 246 |  |  | UINT16 |  |  | Analog Value | 56 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 48 | 48 | 247 |  |  | UINT16 |  |  | Analog Value | 57 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 49 | 49 | 248 |  |  | UINT16 |  |  | Analog Value | 58 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 50 | 50 | 249 |  |  | UINT16 |  |  | Analog Value | 59 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 51 | 51 | 250 |  |  | UINT16 |  |  | Analog Value | 60 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 52 | 52 | 251 |  |  | UINT16 |  |  | Analog Value | 61 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 53 | 53 | 252 |  |  | UINT16 |  |  | Analog Value | 62 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 54 | 54 | 253 |  |  | UINT16 |  |  | Analog Value | 63 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 55 | 55 | 254 |  |  | UINT16 |  |  | Analog Value | 64 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 56 | 56 | 255 |  |  | UINT16 |  |  | Analog Value | 65 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 57 | 57 | 256 |  |  | UINT16 |  |  | Analog Value | 66 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 58 | 58 | 257 |  |  | UINT16 |  |  | Analog Value | 67 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 59 | 59 | 258 |  |  | UINT16 |  |  | Analog Value | 68 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 60 | 60 | 259 |  |  | UINT16 |  |  | Analog Value | 69 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 61 | 61 | 260 |  |  | UINT16 |  |  | Analog Value | 70 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 62 | 62 | 261 |  |  | UINT16 |  |  | Analog Value | 71 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 63 | 63 | 262 |  |  | UINT16 |  |  | Analog Value | 72 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 64 | 64 | 263 |  |  | UINT16 |  |  | Analog Value | 73 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 65 | 65 | 264 |  |  | UINT16 |  |  | Analog Value | 74 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 66 | 66 | 265 |  |  | UINT16 |  |  | Analog Value | 75 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 67 | 67 | 266 |  |  | UINT16 |  |  | Analog Value | 76 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 68 | 68 | 267 |  |  | UINT16 |  |  | Analog Value | 77 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 69 | 69 | 268 |  |  | UINT16 |  |  | Analog Value | 78 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 70 | 70 | 269 |  |  | UINT16 |  |  | Analog Value | 79 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 71 | 71 | 270 |  |  | UINT16 |  |  | Analog Value | 80 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 72 | 72 | 271 |  |  | UINT16 |  |  | Analog Value | 81 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 73 | 73 | 272 |  |  | UINT16 |  |  | Analog Value | 82 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 74 | 74 | 273 |  |  | UINT16 |  |  | Analog Value | 83 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 75 | 75 | 274 |  |  | UINT16 |  |  | Analog Value | 84 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 76 | 76 | 275 |  |  | UINT16 |  |  | Analog Value | 85 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 77 | 77 | 276 |  |  | UINT16 |  |  | Analog Value | 86 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 78 | 78 | 277 |  |  | UINT16 |  |  | Analog Value | 87 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 79 | 79 | 278 |  |  | UINT16 |  |  | Analog Value | 88 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 80 | 80 | 279 |  |  | UINT16 |  |  | Analog Value | 89 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 81 | 81 | 280 |  |  | UINT16 |  |  | Analog Value | 90 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 82 | 82 | 281 |  |  | UINT16 |  |  | Analog Value | 91 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 83 | 83 | 282 |  |  | UINT16 |  |  | Analog Value | 92 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 84 | 84 | 283 |  |  | UINT16 |  |  | Analog Value | 93 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 85 | 85 | 284 |  |  | UINT16 |  |  | Analog Value | 94 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 86 | 86 | 285 |  |  | UINT16 |  |  | Analog Value | 95 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 87 | 87 | 286 |  |  | UINT16 |  |  | Analog Value | 96 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 88 | 88 | 287 |  |  | UINT16 |  |  | Analog Value | 97 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 89 | 89 | 288 |  |  | UINT16 |  |  | Analog Value | 98 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 90 | 90 | 289 |  |  | UINT16 |  |  | Analog Value | 99 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 91 | 91 | 290 |  |  | UINT16 |  |  | Analog Value | 100 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 92 | 92 | 291 |  |  | UINT16 |  |  | Analog Value | 101 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 93 | 93 | 292 |  |  | UINT16 |  |  | Analog Value | 102 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 94 | 94 | 293 |  |  | UINT16 |  |  | Analog Value | 103 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 95 | 95 | 294 |  |  | UINT16 |  |  | Analog Value | 104 | R/W | NV | Amps | 0 - 32000
| CT Size - Circuit 96 | 96 | 295 |  |  | UINT16 |  |  | Analog Value | 105 | R/W | NV | Amps | 0 - 32000
| Breaker Size |  | 296 | 391 |  | UINT16 |  |  | Analog Value | 106 - 201 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 1 | 1 | 296 |  |  | UINT16 |  |  | Analog Value | 106 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 2 | 2 | 297 |  |  | UINT16 |  |  | Analog Value | 107 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 3 | 3 | 298 |  |  | UINT16 |  |  | Analog Value | 108 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 4 | 4 | 299 |  |  | UINT16 |  |  | Analog Value | 109 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 5 | 5 | 300 |  |  | UINT16 |  |  | Analog Value | 110 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 6 | 6 | 301 |  |  | UINT16 |  |  | Analog Value | 111 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 7 | 7 | 302 |  |  | UINT16 |  |  | Analog Value | 112 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 8 | 8 | 303 |  |  | UINT16 |  |  | Analog Value | 113 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 9 | 9 | 304 |  |  | UINT16 |  |  | Analog Value | 114 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 10 | 10 | 305 |  |  | UINT16 |  |  | Analog Value | 115 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 11 | 11 | 306 |  |  | UINT16 |  |  | Analog Value | 116 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 12 | 12 | 307 |  |  | UINT16 |  |  | Analog Value | 117 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 13 | 13 | 308 |  |  | UINT16 |  |  | Analog Value | 118 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 14 | 14 | 309 |  |  | UINT16 |  |  | Analog Value | 119 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 15 | 15 | 310 |  |  | UINT16 |  |  | Analog Value | 120 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 16 | 16 | 311 |  |  | UINT16 |  |  | Analog Value | 121 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 17 | 17 | 312 |  |  | UINT16 |  |  | Analog Value | 122 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 18 | 18 | 313 |  |  | UINT16 |  |  | Analog Value | 123 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 19 | 19 | 314 |  |  | UINT16 |  |  | Analog Value | 124 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 20 | 20 | 315 |  |  | UINT16 |  |  | Analog Value | 125 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 21 | 21 | 316 |  |  | UINT16 |  |  | Analog Value | 126 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 22 | 22 | 317 |  |  | UINT16 |  |  | Analog Value | 127 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 23 | 23 | 318 |  |  | UINT16 |  |  | Analog Value | 128 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 24 | 24 | 319 |  |  | UINT16 |  |  | Analog Value | 129 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 25 | 25 | 320 |  |  | UINT16 |  |  | Analog Value | 130 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 26 | 26 | 321 |  |  | UINT16 |  |  | Analog Value | 131 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 27 | 27 | 322 |  |  | UINT16 |  |  | Analog Value | 132 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 28 | 28 | 323 |  |  | UINT16 |  |  | Analog Value | 133 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 29 | 29 | 324 |  |  | UINT16 |  |  | Analog Value | 134 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 30 | 30 | 325 |  |  | UINT16 |  |  | Analog Value | 135 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 31 | 31 | 326 |  |  | UINT16 |  |  | Analog Value | 136 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 32 | 32 | 327 |  |  | UINT16 |  |  | Analog Value | 137 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 33 | 33 | 328 |  |  | UINT16 |  |  | Analog Value | 138 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 34 | 34 | 329 |  |  | UINT16 |  |  | Analog Value | 139 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 35 | 35 | 330 |  |  | UINT16 |  |  | Analog Value | 140 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 36 | 36 | 331 |  |  | UINT16 |  |  | Analog Value | 141 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 37 | 37 | 332 |  |  | UINT16 |  |  | Analog Value | 142 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 38 | 38 | 333 |  |  | UINT16 |  |  | Analog Value | 143 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 39 | 39 | 334 |  |  | UINT16 |  |  | Analog Value | 144 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 40 | 40 | 335 |  |  | UINT16 |  |  | Analog Value | 145 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 41 | 41 | 336 |  |  | UINT16 |  |  | Analog Value | 146 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 42 | 42 | 337 |  |  | UINT16 |  |  | Analog Value | 147 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 43 | 43 | 338 |  |  | UINT16 |  |  | Analog Value | 148 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 44 | 44 | 339 |  |  | UINT16 |  |  | Analog Value | 149 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 45 | 45 | 340 |  |  | UINT16 |  |  | Analog Value | 150 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 46 | 46 | 341 |  |  | UINT16 |  |  | Analog Value | 151 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 47 | 47 | 342 |  |  | UINT16 |  |  | Analog Value | 152 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 48 | 48 | 343 |  |  | UINT16 |  |  | Analog Value | 153 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 49 | 49 | 344 |  |  | UINT16 |  |  | Analog Value | 154 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 50 | 50 | 345 |  |  | UINT16 |  |  | Analog Value | 155 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 51 | 51 | 346 |  |  | UINT16 |  |  | Analog Value | 156 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 52 | 52 | 347 |  |  | UINT16 |  |  | Analog Value | 157 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 53 | 53 | 348 |  |  | UINT16 |  |  | Analog Value | 158 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 54 | 54 | 349 |  |  | UINT16 |  |  | Analog Value | 159 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 55 | 55 | 350 |  |  | UINT16 |  |  | Analog Value | 160 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 56 | 56 | 351 |  |  | UINT16 |  |  | Analog Value | 161 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 57 | 57 | 352 |  |  | UINT16 |  |  | Analog Value | 162 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 58 | 58 | 353 |  |  | UINT16 |  |  | Analog Value | 163 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 59 | 59 | 354 |  |  | UINT16 |  |  | Analog Value | 164 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 60 | 60 | 355 |  |  | UINT16 |  |  | Analog Value | 165 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 61 | 61 | 356 |  |  | UINT16 |  |  | Analog Value | 166 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 62 | 62 | 357 |  |  | UINT16 |  |  | Analog Value | 167 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 63 | 63 | 358 |  |  | UINT16 |  |  | Analog Value | 168 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 64 | 64 | 359 |  |  | UINT16 |  |  | Analog Value | 169 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 65 | 65 | 360 |  |  | UINT16 |  |  | Analog Value | 170 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 66 | 66 | 361 |  |  | UINT16 |  |  | Analog Value | 171 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 67 | 67 | 362 |  |  | UINT16 |  |  | Analog Value | 172 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 68 | 68 | 363 |  |  | UINT16 |  |  | Analog Value | 173 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 69 | 69 | 364 |  |  | UINT16 |  |  | Analog Value | 174 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 70 | 70 | 365 |  |  | UINT16 |  |  | Analog Value | 175 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 71 | 71 | 366 |  |  | UINT16 |  |  | Analog Value | 176 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 72 | 72 | 367 |  |  | UINT16 |  |  | Analog Value | 177 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 73 | 73 | 368 |  |  | UINT16 |  |  | Analog Value | 178 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 74 | 74 | 369 |  |  | UINT16 |  |  | Analog Value | 179 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 75 | 75 | 370 |  |  | UINT16 |  |  | Analog Value | 180 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 76 | 76 | 371 |  |  | UINT16 |  |  | Analog Value | 181 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 77 | 77 | 372 |  |  | UINT16 |  |  | Analog Value | 182 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 78 | 78 | 373 |  |  | UINT16 |  |  | Analog Value | 183 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 79 | 79 | 374 |  |  | UINT16 |  |  | Analog Value | 184 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 80 | 80 | 375 |  |  | UINT16 |  |  | Analog Value | 185 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 81 | 81 | 376 |  |  | UINT16 |  |  | Analog Value | 186 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 82 | 82 | 377 |  |  | UINT16 |  |  | Analog Value | 187 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 83 | 83 | 378 |  |  | UINT16 |  |  | Analog Value | 188 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 84 | 84 | 379 |  |  | UINT16 |  |  | Analog Value | 189 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 85 | 85 | 380 |  |  | UINT16 |  |  | Analog Value | 190 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 86 | 86 | 381 |  |  | UINT16 |  |  | Analog Value | 191 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 87 | 87 | 382 |  |  | UINT16 |  |  | Analog Value | 192 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 88 | 88 | 383 |  |  | UINT16 |  |  | Analog Value | 193 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 89 | 89 | 384 |  |  | UINT16 |  |  | Analog Value | 194 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 90 | 90 | 385 |  |  | UINT16 |  |  | Analog Value | 195 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 91 | 91 | 386 |  |  | UINT16 |  |  | Analog Value | 196 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 92 | 92 | 387 |  |  | UINT16 |  |  | Analog Value | 197 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 93 | 93 | 388 |  |  | UINT16 |  |  | Analog Value | 198 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 94 | 94 | 389 |  |  | UINT16 |  |  | Analog Value | 199 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 95 | 95 | 390 |  |  | UINT16 |  |  | Analog Value | 200 | R/W | NV | Amps | 0 - 32000
| Breaker Size - Circuit 96 | 96 | 391 |  |  | UINT16 |  |  | Analog Value | 201 | R/W | NV | Amps | 0 - 32000
| Voltage Phase |  | 392 | 487 |  | UINT16 |  |  | Analog Value | 202 - 297 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 1 | 1 | 392 |  |  | UINT16 |  |  | Analog Value | 202 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 2 | 2 | 393 |  |  | UINT16 |  |  | Analog Value | 203 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 3 | 3 | 394 |  |  | UINT16 |  |  | Analog Value | 204 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 4 | 4 | 395 |  |  | UINT16 |  |  | Analog Value | 205 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 5 | 5 | 396 |  |  | UINT16 |  |  | Analog Value | 206 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 6 | 6 | 397 |  |  | UINT16 |  |  | Analog Value | 207 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 7 | 7 | 398 |  |  | UINT16 |  |  | Analog Value | 208 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 8 | 8 | 399 |  |  | UINT16 |  |  | Analog Value | 209 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 9 | 9 | 400 |  |  | UINT16 |  |  | Analog Value | 210 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 10 | 10 | 401 |  |  | UINT16 |  |  | Analog Value | 211 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 11 | 11 | 402 |  |  | UINT16 |  |  | Analog Value | 212 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 12 | 12 | 403 |  |  | UINT16 |  |  | Analog Value | 213 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 13 | 13 | 404 |  |  | UINT16 |  |  | Analog Value | 214 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 14 | 14 | 405 |  |  | UINT16 |  |  | Analog Value | 215 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 15 | 15 | 406 |  |  | UINT16 |  |  | Analog Value | 216 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 16 | 16 | 407 |  |  | UINT16 |  |  | Analog Value | 217 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 17 | 17 | 408 |  |  | UINT16 |  |  | Analog Value | 218 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 18 | 18 | 409 |  |  | UINT16 |  |  | Analog Value | 219 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 19 | 19 | 410 |  |  | UINT16 |  |  | Analog Value | 220 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 20 | 20 | 411 |  |  | UINT16 |  |  | Analog Value | 221 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 21 | 21 | 412 |  |  | UINT16 |  |  | Analog Value | 222 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 22 | 22 | 413 |  |  | UINT16 |  |  | Analog Value | 223 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 23 | 23 | 414 |  |  | UINT16 |  |  | Analog Value | 224 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 24 | 24 | 415 |  |  | UINT16 |  |  | Analog Value | 225 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 25 | 25 | 416 |  |  | UINT16 |  |  | Analog Value | 226 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 26 | 26 | 417 |  |  | UINT16 |  |  | Analog Value | 227 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 27 | 27 | 418 |  |  | UINT16 |  |  | Analog Value | 228 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 28 | 28 | 419 |  |  | UINT16 |  |  | Analog Value | 229 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 29 | 29 | 420 |  |  | UINT16 |  |  | Analog Value | 230 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 30 | 30 | 421 |  |  | UINT16 |  |  | Analog Value | 231 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 31 | 31 | 422 |  |  | UINT16 |  |  | Analog Value | 232 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 32 | 32 | 423 |  |  | UINT16 |  |  | Analog Value | 233 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 33 | 33 | 424 |  |  | UINT16 |  |  | Analog Value | 234 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 34 | 34 | 425 |  |  | UINT16 |  |  | Analog Value | 235 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 35 | 35 | 426 |  |  | UINT16 |  |  | Analog Value | 236 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 36 | 36 | 427 |  |  | UINT16 |  |  | Analog Value | 237 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 37 | 37 | 428 |  |  | UINT16 |  |  | Analog Value | 238 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 38 | 38 | 429 |  |  | UINT16 |  |  | Analog Value | 239 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 39 | 39 | 430 |  |  | UINT16 |  |  | Analog Value | 240 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 40 | 40 | 431 |  |  | UINT16 |  |  | Analog Value | 241 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 41 | 41 | 432 |  |  | UINT16 |  |  | Analog Value | 242 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 42 | 42 | 433 |  |  | UINT16 |  |  | Analog Value | 243 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 43 | 43 | 434 |  |  | UINT16 |  |  | Analog Value | 244 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 44 | 44 | 435 |  |  | UINT16 |  |  | Analog Value | 245 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 45 | 45 | 436 |  |  | UINT16 |  |  | Analog Value | 246 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 46 | 46 | 437 |  |  | UINT16 |  |  | Analog Value | 247 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 47 | 47 | 438 |  |  | UINT16 |  |  | Analog Value | 248 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 48 | 48 | 439 |  |  | UINT16 |  |  | Analog Value | 249 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 49 | 49 | 440 |  |  | UINT16 |  |  | Analog Value | 250 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 50 | 50 | 441 |  |  | UINT16 |  |  | Analog Value | 251 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 51 | 51 | 442 |  |  | UINT16 |  |  | Analog Value | 252 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 52 | 52 | 443 |  |  | UINT16 |  |  | Analog Value | 253 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 53 | 53 | 444 |  |  | UINT16 |  |  | Analog Value | 254 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 54 | 54 | 445 |  |  | UINT16 |  |  | Analog Value | 255 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 55 | 55 | 446 |  |  | UINT16 |  |  | Analog Value | 256 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 56 | 56 | 447 |  |  | UINT16 |  |  | Analog Value | 257 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 57 | 57 | 448 |  |  | UINT16 |  |  | Analog Value | 258 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 58 | 58 | 449 |  |  | UINT16 |  |  | Analog Value | 259 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 59 | 59 | 450 |  |  | UINT16 |  |  | Analog Value | 260 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 60 | 60 | 451 |  |  | UINT16 |  |  | Analog Value | 261 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 61 | 61 | 452 |  |  | UINT16 |  |  | Analog Value | 262 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 62 | 62 | 453 |  |  | UINT16 |  |  | Analog Value | 263 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 63 | 63 | 454 |  |  | UINT16 |  |  | Analog Value | 264 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 64 | 64 | 455 |  |  | UINT16 |  |  | Analog Value | 265 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 65 | 65 | 456 |  |  | UINT16 |  |  | Analog Value | 266 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 66 | 66 | 457 |  |  | UINT16 |  |  | Analog Value | 267 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 67 | 67 | 458 |  |  | UINT16 |  |  | Analog Value | 268 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 68 | 68 | 459 |  |  | UINT16 |  |  | Analog Value | 269 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 69 | 69 | 460 |  |  | UINT16 |  |  | Analog Value | 270 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 70 | 70 | 461 |  |  | UINT16 |  |  | Analog Value | 271 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 71 | 71 | 462 |  |  | UINT16 |  |  | Analog Value | 272 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 72 | 72 | 463 |  |  | UINT16 |  |  | Analog Value | 273 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 73 | 73 | 464 |  |  | UINT16 |  |  | Analog Value | 274 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 74 | 74 | 465 |  |  | UINT16 |  |  | Analog Value | 275 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 75 | 75 | 466 |  |  | UINT16 |  |  | Analog Value | 276 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 76 | 76 | 467 |  |  | UINT16 |  |  | Analog Value | 277 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 77 | 77 | 468 |  |  | UINT16 |  |  | Analog Value | 278 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 78 | 78 | 469 |  |  | UINT16 |  |  | Analog Value | 279 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 79 | 79 | 470 |  |  | UINT16 |  |  | Analog Value | 280 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 80 | 80 | 471 |  |  | UINT16 |  |  | Analog Value | 281 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 81 | 81 | 472 |  |  | UINT16 |  |  | Analog Value | 282 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 82 | 82 | 473 |  |  | UINT16 |  |  | Analog Value | 283 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 83 | 83 | 474 |  |  | UINT16 |  |  | Analog Value | 284 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 84 | 84 | 475 |  |  | UINT16 |  |  | Analog Value | 285 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 85 | 85 | 476 |  |  | UINT16 |  |  | Analog Value | 286 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 86 | 86 | 477 |  |  | UINT16 |  |  | Analog Value | 287 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 87 | 87 | 478 |  |  | UINT16 |  |  | Analog Value | 288 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 88 | 88 | 479 |  |  | UINT16 |  |  | Analog Value | 289 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 89 | 89 | 480 |  |  | UINT16 |  |  | Analog Value | 290 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 90 | 90 | 481 |  |  | UINT16 |  |  | Analog Value | 291 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 91 | 91 | 482 |  |  | UINT16 |  |  | Analog Value | 292 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 92 | 92 | 483 |  |  | UINT16 |  |  | Analog Value | 293 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 93 | 93 | 484 |  |  | UINT16 |  |  | Analog Value | 294 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 94 | 94 | 485 |  |  | UINT16 |  |  | Analog Value | 295 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 95 | 95 | 486 |  |  | UINT16 |  |  | Analog Value | 296 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| Voltage Phase - Circuit 96 | 96 | 487 |  |  | UINT16 |  |  | Analog Value | 297 | R/W | NV |  | 0, 1, 2 | Voltage Phase: 0 = L1, 1 = L2, 2 = L3
| True Meter Assignment |  | 488 | 583 |  | UINT16 |  |  | Analog Value | 298 - 393 | R/W | NV |  | 0 - 96 | True Meter Assignment (Starting at register 15000), 0 = Disabled
| True Meter Assingment - Circuit 1 | 1 | 488 |  |  | UINT16 |  |  | Analog Value | 298 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 2 | 2 | 489 |  |  | UINT16 |  |  | Analog Value | 299 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 3 | 3 | 490 |  |  | UINT16 |  |  | Analog Value | 300 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 4 | 4 | 491 |  |  | UINT16 |  |  | Analog Value | 301 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 5 | 5 | 492 |  |  | UINT16 |  |  | Analog Value | 302 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 6 | 6 | 493 |  |  | UINT16 |  |  | Analog Value | 303 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 7 | 7 | 494 |  |  | UINT16 |  |  | Analog Value | 304 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 8 | 8 | 495 |  |  | UINT16 |  |  | Analog Value | 305 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 9 | 9 | 496 |  |  | UINT16 |  |  | Analog Value | 306 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 10 | 10 | 497 |  |  | UINT16 |  |  | Analog Value | 307 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 11 | 11 | 498 |  |  | UINT16 |  |  | Analog Value | 308 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 12 | 12 | 499 |  |  | UINT16 |  |  | Analog Value | 309 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 13 | 13 | 500 |  |  | UINT16 |  |  | Analog Value | 310 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 14 | 14 | 501 |  |  | UINT16 |  |  | Analog Value | 311 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 15 | 15 | 502 |  |  | UINT16 |  |  | Analog Value | 312 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 16 | 16 | 503 |  |  | UINT16 |  |  | Analog Value | 313 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 17 | 17 | 504 |  |  | UINT16 |  |  | Analog Value | 314 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 18 | 18 | 505 |  |  | UINT16 |  |  | Analog Value | 315 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 19 | 19 | 506 |  |  | UINT16 |  |  | Analog Value | 316 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 20 | 20 | 507 |  |  | UINT16 |  |  | Analog Value | 317 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 21 | 21 | 508 |  |  | UINT16 |  |  | Analog Value | 318 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 22 | 22 | 509 |  |  | UINT16 |  |  | Analog Value | 319 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 23 | 23 | 510 |  |  | UINT16 |  |  | Analog Value | 320 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 24 | 24 | 511 |  |  | UINT16 |  |  | Analog Value | 321 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 25 | 25 | 512 |  |  | UINT16 |  |  | Analog Value | 322 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 26 | 26 | 513 |  |  | UINT16 |  |  | Analog Value | 323 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 27 | 27 | 514 |  |  | UINT16 |  |  | Analog Value | 324 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 28 | 28 | 515 |  |  | UINT16 |  |  | Analog Value | 325 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 29 | 29 | 516 |  |  | UINT16 |  |  | Analog Value | 326 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 30 | 30 | 517 |  |  | UINT16 |  |  | Analog Value | 327 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 31 | 31 | 518 |  |  | UINT16 |  |  | Analog Value | 328 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 32 | 32 | 519 |  |  | UINT16 |  |  | Analog Value | 329 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 33 | 33 | 520 |  |  | UINT16 |  |  | Analog Value | 330 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 34 | 34 | 521 |  |  | UINT16 |  |  | Analog Value | 331 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 35 | 35 | 522 |  |  | UINT16 |  |  | Analog Value | 332 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 36 | 36 | 523 |  |  | UINT16 |  |  | Analog Value | 333 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 37 | 37 | 524 |  |  | UINT16 |  |  | Analog Value | 334 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 38 | 38 | 525 |  |  | UINT16 |  |  | Analog Value | 335 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 39 | 39 | 526 |  |  | UINT16 |  |  | Analog Value | 336 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 40 | 40 | 527 |  |  | UINT16 |  |  | Analog Value | 337 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 41 | 41 | 528 |  |  | UINT16 |  |  | Analog Value | 338 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 42 | 42 | 529 |  |  | UINT16 |  |  | Analog Value | 339 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 43 | 43 | 530 |  |  | UINT16 |  |  | Analog Value | 340 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 44 | 44 | 531 |  |  | UINT16 |  |  | Analog Value | 341 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 45 | 45 | 532 |  |  | UINT16 |  |  | Analog Value | 342 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 46 | 46 | 533 |  |  | UINT16 |  |  | Analog Value | 343 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 47 | 47 | 534 |  |  | UINT16 |  |  | Analog Value | 344 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 48 | 48 | 535 |  |  | UINT16 |  |  | Analog Value | 345 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 49 | 49 | 536 |  |  | UINT16 |  |  | Analog Value | 346 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 50 | 50 | 537 |  |  | UINT16 |  |  | Analog Value | 347 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 51 | 51 | 538 |  |  | UINT16 |  |  | Analog Value | 348 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 52 | 52 | 539 |  |  | UINT16 |  |  | Analog Value | 349 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 53 | 53 | 540 |  |  | UINT16 |  |  | Analog Value | 350 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 54 | 54 | 541 |  |  | UINT16 |  |  | Analog Value | 351 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 55 | 55 | 542 |  |  | UINT16 |  |  | Analog Value | 352 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 56 | 56 | 543 |  |  | UINT16 |  |  | Analog Value | 353 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 57 | 57 | 544 |  |  | UINT16 |  |  | Analog Value | 354 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 58 | 58 | 545 |  |  | UINT16 |  |  | Analog Value | 355 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 59 | 59 | 546 |  |  | UINT16 |  |  | Analog Value | 356 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 60 | 60 | 547 |  |  | UINT16 |  |  | Analog Value | 357 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 61 | 61 | 548 |  |  | UINT16 |  |  | Analog Value | 358 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 62 | 62 | 549 |  |  | UINT16 |  |  | Analog Value | 359 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 63 | 63 | 550 |  |  | UINT16 |  |  | Analog Value | 360 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 64 | 64 | 551 |  |  | UINT16 |  |  | Analog Value | 361 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 65 | 65 | 552 |  |  | UINT16 |  |  | Analog Value | 362 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 66 | 66 | 553 |  |  | UINT16 |  |  | Analog Value | 363 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 67 | 67 | 554 |  |  | UINT16 |  |  | Analog Value | 364 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 68 | 68 | 555 |  |  | UINT16 |  |  | Analog Value | 365 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 69 | 69 | 556 |  |  | UINT16 |  |  | Analog Value | 366 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 70 | 70 | 557 |  |  | UINT16 |  |  | Analog Value | 367 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 71 | 71 | 558 |  |  | UINT16 |  |  | Analog Value | 368 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 72 | 72 | 559 |  |  | UINT16 |  |  | Analog Value | 369 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 73 | 73 | 560 |  |  | UINT16 |  |  | Analog Value | 370 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 74 | 74 | 561 |  |  | UINT16 |  |  | Analog Value | 371 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 75 | 75 | 562 |  |  | UINT16 |  |  | Analog Value | 372 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 76 | 76 | 563 |  |  | UINT16 |  |  | Analog Value | 373 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 77 | 77 | 564 |  |  | UINT16 |  |  | Analog Value | 374 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 78 | 78 | 565 |  |  | UINT16 |  |  | Analog Value | 375 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 79 | 79 | 566 |  |  | UINT16 |  |  | Analog Value | 376 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 80 | 80 | 567 |  |  | UINT16 |  |  | Analog Value | 377 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 81 | 81 | 568 |  |  | UINT16 |  |  | Analog Value | 378 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 82 | 82 | 569 |  |  | UINT16 |  |  | Analog Value | 379 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 83 | 83 | 570 |  |  | UINT16 |  |  | Analog Value | 380 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 84 | 84 | 571 |  |  | UINT16 |  |  | Analog Value | 381 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 85 | 85 | 572 |  |  | UINT16 |  |  | Analog Value | 382 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 86 | 86 | 573 |  |  | UINT16 |  |  | Analog Value | 383 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 87 | 87 | 574 |  |  | UINT16 |  |  | Analog Value | 384 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 88 | 88 | 575 |  |  | UINT16 |  |  | Analog Value | 385 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 89 | 89 | 576 |  |  | UINT16 |  |  | Analog Value | 386 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 90 | 90 | 577 |  |  | UINT16 |  |  | Analog Value | 387 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 91 | 91 | 578 |  |  | UINT16 |  |  | Analog Value | 388 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 92 | 92 | 579 |  |  | UINT16 |  |  | Analog Value | 389 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 93 | 93 | 580 |  |  | UINT16 |  |  | Analog Value | 390 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 94 | 94 | 581 |  |  | UINT16 |  |  | Analog Value | 391 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 95 | 95 | 582 |  |  | UINT16 |  |  | Analog Value | 392 | R/W | NV |  | 0 - 96
| True Meter Assingment - Circuit 96 | 96 | 583 |  |  | UINT16 |  |  | Analog Value | 393 | R/W | NV |  | 0 - 96
| Reset/Command |  | 584 | 679 |  |  |  |  | Analog Value | 394 - 489 |  |  |  |  | 29877 = Reset Max kW and Current, 32123 = Waveform Capture (Only Selected Circuit)
| Reset/Command - Circuit 1 | 1 | 584 | [5 empty] | Analog Value | 394 | R/W | NV
| Reset/Command - Circuit 2 | 2 | 585 | [5 empty] | Analog Value | 395 | R/W | NV
| Reset/Command - Circuit 3 | 3 | 586 | [5 empty] | Analog Value | 396 | R/W | NV
| Reset/Command - Circuit 4 | 4 | 587 | [5 empty] | Analog Value | 397 | R/W | NV
| Reset/Command - Circuit 5 | 5 | 588 | [5 empty] | Analog Value | 398 | R/W | NV
| Reset/Command - Circuit 6 | 6 | 589 | [5 empty] | Analog Value | 399 | R/W | NV
| Reset/Command - Circuit 7 | 7 | 590 | [5 empty] | Analog Value | 400 | R/W | NV
| Reset/Command - Circuit 8 | 8 | 591 | [5 empty] | Analog Value | 401 | R/W | NV
| Reset/Command - Circuit 9 | 9 | 592 | [5 empty] | Analog Value | 402 | R/W | NV
| Reset/Command - Circuit 10 | 10 | 593 | [5 empty] | Analog Value | 403 | R/W | NV
| Reset/Command - Circuit 11 | 11 | 594 | [5 empty] | Analog Value | 404 | R/W | NV
| Reset/Command - Circuit 12 | 12 | 595 | [5 empty] | Analog Value | 405 | R/W | NV
| Reset/Command - Circuit 13 | 13 | 596 | [5 empty] | Analog Value | 406 | R/W | NV
| Reset/Command - Circuit 14 | 14 | 597 | [5 empty] | Analog Value | 407 | R/W | NV
| Reset/Command - Circuit 15 | 15 | 598 | [5 empty] | Analog Value | 408 | R/W | NV
| Reset/Command - Circuit 16 | 16 | 599 | [5 empty] | Analog Value | 409 | R/W | NV
| Reset/Command - Circuit 17 | 17 | 600 | [5 empty] | Analog Value | 410 | R/W | NV
| Reset/Command - Circuit 18 | 18 | 601 | [5 empty] | Analog Value | 411 | R/W | NV
| Reset/Command - Circuit 19 | 19 | 602 | [5 empty] | Analog Value | 412 | R/W | NV
| Reset/Command - Circuit 20 | 20 | 603 | [5 empty] | Analog Value | 413 | R/W | NV
| Reset/Command - Circuit 21 | 21 | 604 | [5 empty] | Analog Value | 414 | R/W | NV
| Reset/Command - Circuit 22 | 22 | 605 | [5 empty] | Analog Value | 415 | R/W | NV
| Reset/Command - Circuit 23 | 23 | 606 | [5 empty] | Analog Value | 416 | R/W | NV
| Reset/Command - Circuit 24 | 24 | 607 | [5 empty] | Analog Value | 417 | R/W | NV
| Reset/Command - Circuit 25 | 25 | 608 | [5 empty] | Analog Value | 418 | R/W | NV
| Reset/Command - Circuit 26 | 26 | 609 | [5 empty] | Analog Value | 419 | R/W | NV
| Reset/Command - Circuit 27 | 27 | 610 | [5 empty] | Analog Value | 420 | R/W | NV
| Reset/Command - Circuit 28 | 28 | 611 | [5 empty] | Analog Value | 421 | R/W | NV
| Reset/Command - Circuit 29 | 29 | 612 | [5 empty] | Analog Value | 422 | R/W | NV
| Reset/Command - Circuit 30 | 30 | 613 | [5 empty] | Analog Value | 423 | R/W | NV
| Reset/Command - Circuit 31 | 31 | 614 | [5 empty] | Analog Value | 424 | R/W | NV
| Reset/Command - Circuit 32 | 32 | 615 | [5 empty] | Analog Value | 425 | R/W | NV
| Reset/Command - Circuit 33 | 33 | 616 | [5 empty] | Analog Value | 426 | R/W | NV
| Reset/Command - Circuit 34 | 34 | 617 | [5 empty] | Analog Value | 427 | R/W | NV
| Reset/Command - Circuit 35 | 35 | 618 | [5 empty] | Analog Value | 428 | R/W | NV
| Reset/Command - Circuit 36 | 36 | 619 | [5 empty] | Analog Value | 429 | R/W | NV
| Reset/Command - Circuit 37 | 37 | 620 | [5 empty] | Analog Value | 430 | R/W | NV
| Reset/Command - Circuit 38 | 38 | 621 | [5 empty] | Analog Value | 431 | R/W | NV
| Reset/Command - Circuit 39 | 39 | 622 | [5 empty] | Analog Value | 432 | R/W | NV
| Reset/Command - Circuit 40 | 40 | 623 | [5 empty] | Analog Value | 433 | R/W | NV
| Reset/Command - Circuit 41 | 41 | 624 | [5 empty] | Analog Value | 434 | R/W | NV
| Reset/Command - Circuit 42 | 42 | 625 | [5 empty] | Analog Value | 435 | R/W | NV
| Reset/Command - Circuit 43 | 43 | 626 | [5 empty] | Analog Value | 436 | R/W | NV
| Reset/Command - Circuit 44 | 44 | 627 | [5 empty] | Analog Value | 437 | R/W | NV
| Reset/Command - Circuit 45 | 45 | 628 | [5 empty] | Analog Value | 438 | R/W | NV
| Reset/Command - Circuit 46 | 46 | 629 | [5 empty] | Analog Value | 439 | R/W | NV
| Reset/Command - Circuit 47 | 47 | 630 | [5 empty] | Analog Value | 440 | R/W | NV
| Reset/Command - Circuit 48 | 48 | 631 | [5 empty] | Analog Value | 441 | R/W | NV
| Reset/Command - Circuit 49 | 49 | 632 | [5 empty] | Analog Value | 442 | R/W | NV
| Reset/Command - Circuit 50 | 50 | 633 | [5 empty] | Analog Value | 443 | R/W | NV
| Reset/Command - Circuit 51 | 51 | 634 | [5 empty] | Analog Value | 444 | R/W | NV
| Reset/Command - Circuit 52 | 52 | 635 | [5 empty] | Analog Value | 445 | R/W | NV
| Reset/Command - Circuit 53 | 53 | 636 | [5 empty] | Analog Value | 446 | R/W | NV
| Reset/Command - Circuit 54 | 54 | 637 | [5 empty] | Analog Value | 447 | R/W | NV
| Reset/Command - Circuit 55 | 55 | 638 | [5 empty] | Analog Value | 448 | R/W | NV
| Reset/Command - Circuit 56 | 56 | 639 | [5 empty] | Analog Value | 449 | R/W | NV
| Reset/Command - Circuit 57 | 57 | 640 | [5 empty] | Analog Value | 450 | R/W | NV
| Reset/Command - Circuit 58 | 58 | 641 | [5 empty] | Analog Value | 451 | R/W | NV
| Reset/Command - Circuit 59 | 59 | 642 | [5 empty] | Analog Value | 452 | R/W | NV
| Reset/Command - Circuit 60 | 60 | 643 | [5 empty] | Analog Value | 453 | R/W | NV
| Reset/Command - Circuit 61 | 61 | 644 | [5 empty] | Analog Value | 454 | R/W | NV
| Reset/Command - Circuit 62 | 62 | 645 | [5 empty] | Analog Value | 455 | R/W | NV
| Reset/Command - Circuit 63 | 63 | 646 | [5 empty] | Analog Value | 456 | R/W | NV
| Reset/Command - Circuit 64 | 64 | 647 | [5 empty] | Analog Value | 457 | R/W | NV
| Reset/Command - Circuit 65 | 65 | 648 | [5 empty] | Analog Value | 458 | R/W | NV
| Reset/Command - Circuit 66 | 66 | 649 | [5 empty] | Analog Value | 459 | R/W | NV
| Reset/Command - Circuit 67 | 67 | 650 | [5 empty] | Analog Value | 460 | R/W | NV
| Reset/Command - Circuit 68 | 68 | 651 | [5 empty] | Analog Value | 461 | R/W | NV
| Reset/Command - Circuit 69 | 69 | 652 | [5 empty] | Analog Value | 462 | R/W | NV
| Reset/Command - Circuit 70 | 70 | 653 | [5 empty] | Analog Value | 463 | R/W | NV
| Reset/Command - Circuit 71 | 71 | 654 | [5 empty] | Analog Value | 464 | R/W | NV
| Reset/Command - Circuit 72 | 72 | 655 | [5 empty] | Analog Value | 465 | R/W | NV
| Reset/Command - Circuit 73 | 73 | 656 | [5 empty] | Analog Value | 466 | R/W | NV
| Reset/Command - Circuit 74 | 74 | 657 | [5 empty] | Analog Value | 467 | R/W | NV
| Reset/Command - Circuit 75 | 75 | 658 | [5 empty] | Analog Value | 468 | R/W | NV
| Reset/Command - Circuit 76 | 76 | 659 | [5 empty] | Analog Value | 469 | R/W | NV
| Reset/Command - Circuit 77 | 77 | 660 | [5 empty] | Analog Value | 470 | R/W | NV
| Reset/Command - Circuit 78 | 78 | 661 | [5 empty] | Analog Value | 471 | R/W | NV
| Reset/Command - Circuit 79 | 79 | 662 | [5 empty] | Analog Value | 472 | R/W | NV
| Reset/Command - Circuit 80 | 80 | 663 | [5 empty] | Analog Value | 473 | R/W | NV
| Reset/Command - Circuit 81 | 81 | 664 | [5 empty] | Analog Value | 474 | R/W | NV
| Reset/Command - Circuit 82 | 82 | 665 | [5 empty] | Analog Value | 475 | R/W | NV
| Reset/Command - Circuit 83 | 83 | 666 | [5 empty] | Analog Value | 476 | R/W | NV
| Reset/Command - Circuit 84 | 84 | 667 | [5 empty] | Analog Value | 477 | R/W | NV
| Reset/Command - Circuit 85 | 85 | 668 | [5 empty] | Analog Value | 478 | R/W | NV
| Reset/Command - Circuit 86 | 86 | 669 | [5 empty] | Analog Value | 479 | R/W | NV
| Reset/Command - Circuit 87 | 87 | 670 | [5 empty] | Analog Value | 480 | R/W | NV
| Reset/Command - Circuit 88 | 88 | 671 | [5 empty] | Analog Value | 481 | R/W | NV
| Reset/Command - Circuit 89 | 89 | 672 | [5 empty] | Analog Value | 482 | R/W | NV
| Reset/Command - Circuit 90 | 90 | 673 | [5 empty] | Analog Value | 483 | R/W | NV
| Reset/Command - Circuit 91 | 91 | 674 | [5 empty] | Analog Value | 484 | R/W | NV
| Reset/Command - Circuit 92 | 92 | 675 | [5 empty] | Analog Value | 485 | R/W | NV
| Reset/Command - Circuit 93 | 93 | 676 | [5 empty] | Analog Value | 486 | R/W | NV
| Reset/Command - Circuit 94 | 94 | 677 | [5 empty] | Analog Value | 487 | R/W | NV
| Reset/Command - Circuit 95 | 95 | 678 | [5 empty] | Analog Value | 488 | R/W | NV
| Reset/Command - Circuit 96 | 96 | 679 | [5 empty] | Analog Value | 489 | R/W | NV
| CT Type/Compensation |  | 680 | 775
| CT Type/Compensation - Circuit 1 | 1 | 680 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 2 | 2 | 681 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 3 | 3 | 682 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 4 | 4 | 683 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 5 | 5 | 684 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 6 | 6 | 685 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 7 | 7 | 686 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 8 | 8 | 687 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 9 | 9 | 688 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 10 | 10 | 689 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 11 | 11 | 690 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 12 | 12 | 691 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 13 | 13 | 692 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 14 | 14 | 693 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 15 | 15 | 694 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 16 | 16 | 695 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 17 | 17 | 696 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 18 | 18 | 697 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 19 | 19 | 698 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 20 | 20 | 699 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 21 | 21 | 700 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 22 | 22 | 701 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 23 | 23 | 702 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 24 | 24 | 703 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 25 | 25 | 704 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 26 | 26 | 705 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 27 | 27 | 706 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 28 | 28 | 707 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 29 | 29 | 708 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 30 | 30 | 709 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 31 | 31 | 710 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 32 | 32 | 711 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 33 | 33 | 712 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 34 | 34 | 713 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 35 | 35 | 714 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 36 | 36 | 715 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 37 | 37 | 716 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 38 | 38 | 717 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 39 | 39 | 718 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 40 | 40 | 719 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 41 | 41 | 720 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 42 | 42 | 721 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 43 | 43 | 722 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 44 | 44 | 723 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 45 | 45 | 724 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 46 | 46 | 725 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 47 | 47 | 726 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 48 | 48 | 727 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 49 | 49 | 728 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 50 | 50 | 729 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 51 | 51 | 730 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 52 | 52 | 731 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 53 | 53 | 732 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 54 | 54 | 733 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 55 | 55 | 734 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 56 | 56 | 735 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 57 | 57 | 736 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 58 | 58 | 737 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 59 | 59 | 738 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 60 | 60 | 739 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 61 | 61 | 740 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 62 | 62 | 741 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 63 | 63 | 742 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 64 | 64 | 743 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 65 | 65 | 744 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 66 | 66 | 745 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 67 | 67 | 746 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 68 | 68 | 747 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 69 | 69 | 748 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 70 | 70 | 749 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 71 | 71 | 750 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 72 | 72 | 751 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 73 | 73 | 752 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 74 | 74 | 753 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 75 | 75 | 754 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 76 | 76 | 755 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 77 | 77 | 756 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 78 | 78 | 757 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 79 | 79 | 758 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 80 | 80 | 759 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 81 | 81 | 760 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 82 | 82 | 761 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 83 | 83 | 762 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 84 | 84 | 763 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 85 | 85 | 764 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 86 | 86 | 765 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 87 | 87 | 766 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 88 | 88 | 767 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 89 | 89 | 768 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 90 | 90 | 769 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 91 | 91 | 770 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 92 | 92 | 771 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 93 | 93 | 772 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 94 | 94 | 773 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 95 | 95 | 774 | [7 empty] | R/W | NV
| CT Type/Compensation - Circuit 96 | 96 | 775 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment |  | 776 | 871
| Smart Port to Circuit Assignment - SP1, CH1 | SP1, CH1 | 776 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH2 | SP1, CH2 | 777 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH3 | SP1, CH3 | 778 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH4 | SP1, CH4 | 779 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH5 | SP1, CH5 | 780 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH6 | SP1, CH6 | 781 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH7 | SP1, CH7 | 782 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH8 | SP1, CH8 | 783 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH9 | SP1, CH9 | 784 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH10 | SP1, CH10 | 785 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH11 | SP1, CH11 | 786 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH12 | SP1, CH12 | 787 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH13 | SP1, CH13 | 788 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH14 | SP1, CH14 | 789 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH15 | SP1, CH15 | 790 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH16 | SP1, CH16 | 791 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH17 | SP1, CH17 | 792 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH18 | SP1, CH18 | 793 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH19 | SP1, CH19 | 794 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH20 | SP1, CH20 | 795 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH21 | SP1, CH21 | 796 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH22 | SP1, CH22 | 797 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH23 | SP1, CH23 | 798 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP1, CH24 | SP1, CH24 | 799 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH1 | SP2, CH1 | 800 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH2 | SP2, CH2 | 801 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH3 | SP2, CH3 | 802 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH4 | SP2, CH4 | 803 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH5 | SP2, CH5 | 804 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH6 | SP2, CH6 | 805 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH7 | SP2, CH7 | 806 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH8 | SP2, CH8 | 807 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH9 | SP2, CH9 | 808 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH10 | SP2, CH10 | 809 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH11 | SP2, CH11 | 810 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH12 | SP2, CH12 | 811 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH13 | SP2, CH13 | 812 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH14 | SP2, CH14 | 813 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH15 | SP2, CH15 | 814 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH16 | SP2, CH16 | 815 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH17 | SP2, CH17 | 816 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH18 | SP2, CH18 | 817 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH19 | SP2, CH19 | 818 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH20 | SP2, CH20 | 819 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH21 | SP2, CH21 | 820 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH22 | SP2, CH22 | 821 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH23 | SP2, CH23 | 822 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP2, CH24 | SP2, CH24 | 823 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH1 | SP3, CH1 | 824 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH2 | SP3, CH2 | 825 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH3 | SP3, CH3 | 826 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH4 | SP3, CH4 | 827 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH5 | SP3, CH5 | 828 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH6 | SP3, CH6 | 829 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH7 | SP3, CH7 | 830 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH8 | SP3, CH8 | 831 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH9 | SP3, CH9 | 832 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH10 | SP3, CH10 | 833 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH11 | SP3, CH11 | 834 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH12 | SP3, CH12 | 835 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH13 | SP3, CH13 | 836 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH14 | SP3, CH14 | 837 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH15 | SP3, CH15 | 838 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH16 | SP3, CH16 | 839 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH17 | SP3, CH17 | 840 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH18 | SP3, CH18 | 841 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH19 | SP3, CH19 | 842 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH20 | SP3, CH20 | 843 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH21 | SP3, CH21 | 844 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH22 | SP3, CH22 | 845 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH23 | SP3, CH23 | 846 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP3, CH24 | SP3, CH24 | 847 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH1 | SP4, CH1 | 848 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH2 | SP4, CH2 | 849 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH3 | SP4, CH3 | 850 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH4 | SP4, CH4 | 851 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH5 | SP4, CH5 | 852 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH6 | SP4, CH6 | 853 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH7 | SP4, CH7 | 854 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH8 | SP4, CH8 | 855 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH9 | SP4, CH9 | 856 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH10 | SP4, CH10 | 857 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH11 | SP4, CH11 | 858 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH12 | SP4, CH12 | 859 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH13 | SP4, CH13 | 860 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH14 | SP4, CH14 | 861 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH15 | SP4, CH15 | 862 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH16 | SP4, CH16 | 863 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH17 | SP4, CH17 | 864 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH18 | SP4, CH18 | 865 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH19 | SP4, CH19 | 866 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH20 | SP4, CH20 | 867 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH21 | SP4, CH21 | 868 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH22 | SP4, CH22 | 869 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH23 | SP4, CH23 | 870 | [7 empty] | R/W | NV
| Smart Port to Circuit Assignment - SP4, CH24 | SP4, CH24 | 871 | [7 empty] | R/W | NV
Alarm/Event Configuration
Voltage Alarm Configuration |  |  | 1000 | 1006
| Overvoltage Alarm Time Delay |  | 1000 |  |  | UINT16 |  |  |  |  | R/W | NV | Seconds | 0 - 32767
| Undervoltage Alarm Time Delay |  | 1001 |  |  | UINT16 |  |  |  |  | R/W | NV | Seconds | 0 - 32767
| Overvoltage Latching Alarm Threshold |  | 1002 |  |  | UINT16 |  |  |  |  | R/W | NV | Volts | 0 - 32767 | Volts Line to Line
| Undervotage Latching Alarm Threshold |  | 1003 |  |  | UINT16 |  |  |  |  | R/W | NV | Volts | 0 - 32767 | Volts Line to Line
| Overvoltage Non-Latching Alarm Threshold |  | 1004 |  |  | UINT16 |  |  |  |  | R/W | NV | Volts | 0 - 32767
| Undervoltage Non-Latching Alarm Threshold |  | 1005 |  |  | UINT16 |  |  |  |  | R/W | NV | Volts | 0 - 32767
| Voltage Alarm Hysteresis |  | 1006 |  |  | UINT16 |  |  |  |  | R/W | NV | Percent | 0 - 32767
Branch Alarm Configuration |  |  | 1007 | 1021
| High-High Latching Alarm Time Delay |  | 1007 |  |  | UINT16 |  |  |  |  | R/W | NV | Seconds
| High Latching Alarm Time Delay |  | 1008 |  |  | UINT16 |  |  |  |  | R/W | NV | Seconds | 0 - 32767
| Low Latching Alarm Time Delay |  | 1009 |  |  | UINT16 |  |  |  |  | R/W | NV | Seconds | 0 - 32767
| Low-Low Latching Alarm Time Delay |  | 1010 |  |  | UINT16 |  |  |  |  | R/W | NV | Seconds | 0 - 32767
| Latching Alarm On Time |  | 1011 |  |  | UINT16 |  |  |  |  | R/W | NV | Seconds | 0 - 32767
| Latching Alarm Off Time |  | 1012 |  |  | UINT16 |  |  |  |  | R/W | NV | Seconds | 0 - 32767
| High-High Latching Alarm Threshold |  | 1013 |  |  | UINT16 |  |  |  |  | R/W | NV | Percent | 0 - 1000
| High Latching Alarm Thresold |  | 1014 |  | -1 | UINT16 |  |  |  |  | R/W | NV | Percent | 0 - 1000 | Percent of Breaker Size (700 = 70%)
| Low Latching Alarm Threshold |  | 1015 |  | -1 | UINT16 |  |  |  |  | R/W | NV | Percent | 0 - 1000 | Percent of Breaker Size (100 = 10%)
| Low-Low Latchng Alarm Threhold |  | 1016 |  |  | UINT16 |  |  |  |  | R/W | NV | Percent | 0 - 1000
| Non-Latching High High Threshold |  | 1017 |  |  | UINT16 |  |  |  |  | R/W | NV | Percent | 0 - 1000
| Non-Latching High Alarm Threshold |  | 1018 |  |  | UINT16 |  |  |  |  | R/W | NV | Percent | 0 - 1000
| Non-Latching Low Alarm Threshold |  | 1019 |  |  | UINT16 |  |  |  |  | R/W | NV | Percent | 0 - 1000
| Non-Latching Low Low Threshold |  | 1020 |  |  | UINT16 |  |  |  |  | R/W | NV | Percent | 0 - 1000
| Non-Latching Hysteresis |  | 1021 |  |  | UINT16 |  |  |  |  | R/W | NV | Percent | 0 - 1000
Waveform Capture Configuration |  |  | 1100 | 1103
| Voltage Capture High RMS Threshold |  | 1100 |  |  | UINT16 |  |  |  |  | R/W | NV | Volts | 0 - 32767 | Volts LL (All line voltages will be captured on event)
| Voltage Capture Low RNS Threshold |  | 1101 |  |  | UINT16 |  |  |  |  | R/W | NV | Volts | 0 - 32767
| Current Capture High RMS Threshold |  | 1102 |  | -1 | UINT16 |  |  |  |  | R/W | NV | Percent | 0 - 1000 | Percent of Breaker Size (800 = 80%)
| Current Capture Low RMS Threshold |  | 1103 |  |  | UINT16 |  |  |  |  | R/W | NV | Percent | 0 - 1000
Alarms and Status
Global Alarm |  |  | 1200 | 1207
| Global Latching Alarm Status |  | 1200 | [7 empty] | R/W |  |  | See Notes | Summary of all Alarm Status Registers (96 Circuits and 3 Voltage) Bit1 = High Latching Alarm, Bit2 = Low Latching Alarm, Bit8 = Overvoltage Latching Alarm, Bit9 = Undervoltage Latching Alarm, Bit11 = Waveform Capture Triggered, Bit12 = Zero Current Detected, Bit13 = Presence of Voltage (All Other Bits are Currently Unused)
| Global Non-Latching Alarm Status |  | 1201 | [7 empty] | R
| Global Most Recent Latching Alarm Channel |  | 1202 | [7 empty] | R
| Global Most Recent Non-Latching Alarm Channel |  | 1203 | [7 empty] | R
| Total Number of Latching Channels In Alarm |  | 1204 | [7 empty] | R
| Total Number of Non-Latching Channels In Alarm |  | 1205 | [7 empty] | R
| Number of Waveform Capture Events |  | 1206 | [7 empty] | R
| Most Recent Waveform Capture Channel |  | 1207 | [7 empty] | R
Voltage Status
| Voltage Alarm Status |  | 1208 | 1210 | [6 empty] | R/W | NV |  | See Notes | Bit0 = Overvoltage Latching Alarm, Bit1 = Undervoltage Latching Alarm, Bit11 = Waveform Capture Triggered, (All Other Bits are Currently Unused)
| Voltage Alarm Status L1 |  | 1208 | [7 empty] | R/W
| Voltage Alarm Status L2 |  | 1209 | [7 empty] | R/W
| Voltage Alarm Status L3 |  | 1210 | [7 empty] | R/W
Branch Status
| Branch Alarm Status |  | 1211 | 1306 | [6 empty] | R/W | NV |  | See Notes | Bit1 = High Latching Alarm, Bit2 = Low Latching Alarm, Bit11 = Waveform Capture Triggered, Bit12 = Zero Current Detected, Bit13 = Presence of Voltage (All Other Bits are Currently Unused)
| Alarm Status - Circuit 1 | 1 | 1211 | [7 empty] | R/W | NV
| Alarm Status - Circuit 2 | 2 | 1212 | [7 empty] | R/W
| Alarm Status - Circuit 3 | 3 | 1213 | [7 empty] | R/W
| Alarm Status - Circuit 4 | 4 | 1214 | [7 empty] | R/W
| Alarm Status - Circuit 5 | 5 | 1215 | [7 empty] | R/W
| Alarm Status - Circuit 6 | 6 | 1216 | [7 empty] | R/W
| Alarm Status - Circuit 7 | 7 | 1217 | [7 empty] | R/W
| Alarm Status - Circuit 8 | 8 | 1218 | [7 empty] | R/W
| Alarm Status - Circuit 9 | 9 | 1219 | [7 empty] | R/W
| Alarm Status - Circuit 10 | 10 | 1220 | [7 empty] | R/W
| Alarm Status - Circuit 11 | 11 | 1221 | [7 empty] | R/W
| Alarm Status - Circuit 12 | 12 | 1222 | [7 empty] | R/W
| Alarm Status - Circuit 13 | 13 | 1223 | [7 empty] | R/W
| Alarm Status - Circuit 14 | 14 | 1224 | [7 empty] | R/W
| Alarm Status - Circuit 15 | 15 | 1225 | [7 empty] | R/W
| Alarm Status - Circuit 16 | 16 | 1226 | [7 empty] | R/W
| Alarm Status - Circuit 17 | 17 | 1227 | [7 empty] | R/W
| Alarm Status - Circuit 18 | 18 | 1228 | [7 empty] | R/W
| Alarm Status - Circuit 19 | 19 | 1229 | [7 empty] | R/W
| Alarm Status - Circuit 20 | 20 | 1230 | [7 empty] | R/W
| Alarm Status - Circuit 21 | 21 | 1231 | [7 empty] | R/W
| Alarm Status - Circuit 22 | 22 | 1232 | [7 empty] | R/W
| Alarm Status - Circuit 23 | 23 | 1233 | [7 empty] | R/W
| Alarm Status - Circuit 24 | 24 | 1234 | [7 empty] | R/W
| Alarm Status - Circuit 25 | 25 | 1235 | [7 empty] | R/W
| Alarm Status - Circuit 26 | 26 | 1236 | [7 empty] | R/W
| Alarm Status - Circuit 27 | 27 | 1237 | [7 empty] | R/W
| Alarm Status - Circuit 28 | 28 | 1238 | [7 empty] | R/W
| Alarm Status - Circuit 29 | 29 | 1239 | [7 empty] | R/W
| Alarm Status - Circuit 30 | 30 | 1240 | [7 empty] | R/W
| Alarm Status - Circuit 31 | 31 | 1241 | [7 empty] | R/W
| Alarm Status - Circuit 32 | 32 | 1242 | [7 empty] | R/W
| Alarm Status - Circuit 33 | 33 | 1243 | [7 empty] | R/W
| Alarm Status - Circuit 34 | 34 | 1244 | [7 empty] | R/W
| Alarm Status - Circuit 35 | 35 | 1245 | [7 empty] | R/W
| Alarm Status - Circuit 36 | 36 | 1246 | [7 empty] | R/W
| Alarm Status - Circuit 37 | 37 | 1247 | [7 empty] | R/W
| Alarm Status - Circuit 38 | 38 | 1248 | [7 empty] | R/W
| Alarm Status - Circuit 39 | 39 | 1249 | [7 empty] | R/W
| Alarm Status - Circuit 40 | 40 | 1250 | [7 empty] | R/W
| Alarm Status - Circuit 41 | 41 | 1251 | [7 empty] | R/W
| Alarm Status - Circuit 42 | 42 | 1252 | [7 empty] | R/W
| Alarm Status - Circuit 43 | 43 | 1253 | [7 empty] | R/W
| Alarm Status - Circuit 44 | 44 | 1254 | [7 empty] | R/W
| Alarm Status - Circuit 45 | 45 | 1255 | [7 empty] | R/W
| Alarm Status - Circuit 46 | 46 | 1256 | [7 empty] | R/W
| Alarm Status - Circuit 47 | 47 | 1257 | [7 empty] | R/W
| Alarm Status - Circuit 48 | 48 | 1258 | [7 empty] | R/W
| Alarm Status - Circuit 49 | 49 | 1259 | [7 empty] | R/W
| Alarm Status - Circuit 50 | 50 | 1260 | [7 empty] | R/W
| Alarm Status - Circuit 51 | 51 | 1261 | [7 empty] | R/W
| Alarm Status - Circuit 52 | 52 | 1262 | [7 empty] | R/W
| Alarm Status - Circuit 53 | 53 | 1263 | [7 empty] | R/W
| Alarm Status - Circuit 54 | 54 | 1264 | [7 empty] | R/W
| Alarm Status - Circuit 55 | 55 | 1265 | [7 empty] | R/W
| Alarm Status - Circuit 56 | 56 | 1266 | [7 empty] | R/W
| Alarm Status - Circuit 57 | 57 | 1267 | [7 empty] | R/W
| Alarm Status - Circuit 58 | 58 | 1268 | [7 empty] | R/W
| Alarm Status - Circuit 59 | 59 | 1269 | [7 empty] | R/W
| Alarm Status - Circuit 60 | 60 | 1270 | [7 empty] | R/W
| Alarm Status - Circuit 61 | 61 | 1271 | [7 empty] | R/W
| Alarm Status - Circuit 62 | 62 | 1272 | [7 empty] | R/W
| Alarm Status - Circuit 63 | 63 | 1273 | [7 empty] | R/W
| Alarm Status - Circuit 64 | 64 | 1274 | [7 empty] | R/W
| Alarm Status - Circuit 65 | 65 | 1275 | [7 empty] | R/W
| Alarm Status - Circuit 66 | 66 | 1276 | [7 empty] | R/W
| Alarm Status - Circuit 67 | 67 | 1277 | [7 empty] | R/W
| Alarm Status - Circuit 68 | 68 | 1278 | [7 empty] | R/W
| Alarm Status - Circuit 69 | 69 | 1279 | [7 empty] | R/W
| Alarm Status - Circuit 70 | 70 | 1280 | [7 empty] | R/W
| Alarm Status - Circuit 71 | 71 | 1281 | [7 empty] | R/W
| Alarm Status - Circuit 72 | 72 | 1282 | [7 empty] | R/W
| Alarm Status - Circuit 73 | 73 | 1283 | [7 empty] | R/W
| Alarm Status - Circuit 74 | 74 | 1284 | [7 empty] | R/W
| Alarm Status - Circuit 75 | 75 | 1285 | [7 empty] | R/W
| Alarm Status - Circuit 76 | 76 | 1286 | [7 empty] | R/W
| Alarm Status - Circuit 77 | 77 | 1287 | [7 empty] | R/W
| Alarm Status - Circuit 78 | 78 | 1288 | [7 empty] | R/W
| Alarm Status - Circuit 79 | 79 | 1289 | [7 empty] | R/W
| Alarm Status - Circuit 80 | 80 | 1290 | [7 empty] | R/W
| Alarm Status - Circuit 81 | 81 | 1291 | [7 empty] | R/W
| Alarm Status - Circuit 82 | 82 | 1292 | [7 empty] | R/W
| Alarm Status - Circuit 83 | 83 | 1293 | [7 empty] | R/W
| Alarm Status - Circuit 84 | 84 | 1294 | [7 empty] | R/W
| Alarm Status - Circuit 85 | 85 | 1295 | [7 empty] | R/W
| Alarm Status - Circuit 86 | 86 | 1296 | [7 empty] | R/W
| Alarm Status - Circuit 87 | 87 | 1297 | [7 empty] | R/W
| Alarm Status - Circuit 88 | 88 | 1298 | [7 empty] | R/W
| Alarm Status - Circuit 89 | 89 | 1299 | [7 empty] | R/W
| Alarm Status - Circuit 90 | 90 | 1300 | [7 empty] | R/W
| Alarm Status - Circuit 91 | 91 | 1301 | [7 empty] | R/W
| Alarm Status - Circuit 92 | 92 | 1302 | [7 empty] | R/W
| Alarm Status - Circuit 93 | 93 | 1303 | [7 empty] | R/W
| Alarm Status - Circuit 94 | 94 | 1304 | [7 empty] | R/W
| Alarm Status - Circuit 95 | 95 | 1305 | [7 empty] | R/W
| Alarm Status - Circuit 96 | 96 | 1306 | [7 empty] | R/W
| Alarm Summary Bit0 (6 Registers) |  | 1307 | 1312
| High Latching Alarm Summary (6 Registers) |  | 1313 | 1318
| Low Latching Alarm Summary (6 Registers) |  | 1319 | 1324
| Alarm Summary Bit3 (6 Registers) |  | 1325 | 1330
| Alarm Summary Bit4 (6 Registers) |  | 1331 | 1336
| Alarm Summary Bit5 (6 Registers) |  | 1337 | 1342
| Alarm Summary Bit6 (6 Registers) |  | 1343 | 1348
| Alarm Summary Bit7 (6 Registers) |  | 1349 | 1354
| Alarm Summary Bit8 (6 Registers) |  | 1355 | 1360
| Alarm Summary Bit9 (6 Registers) |  | 1361 | 1366
| Alarm Summary Bit10 (6 Registers) |  | 1367 | 1372
| Alarm Summary Bit11 (6 Registers) |  | 1373 | 1378
| Zero Current Summary (6 Registers) |  | 1379 | 1384
| Voltage Presence Summary (6 Registers) |  | 1385 | 1390
| Alarm Summary Bit14 (6 Registers) |  | 1391 | 1396
| Alarm Summary Bit15 (6 Registers) |  | 1397 | 1402
| Zero Current State |  | 1403 | 1498 |  | UINT16 |  |  | Analog Input | 1841 - 1936 |  |  |  |  | Zero Current State registers will be updated when current drops to 0A
| Branch Zero Current State - Circuit 1 | 1 | 1403 | [5 empty] | Analog Input | 1841 | R
| Branch Zero Current State - Circuit 2 | 2 | 1404 | [5 empty] | Analog Input | 1842 | R
| Branch Zero Current State - Circuit 3 | 3 | 1405 | [5 empty] | Analog Input | 1843 | R
| Branch Zero Current State - Circuit 4 | 4 | 1406 | [5 empty] | Analog Input | 1844 | R
| Branch Zero Current State - Circuit 5 | 5 | 1407 | [5 empty] | Analog Input | 1845 | R
| Branch Zero Current State - Circuit 6 | 6 | 1408 | [5 empty] | Analog Input | 1846 | R
| Branch Zero Current State - Circuit 7 | 7 | 1409 | [5 empty] | Analog Input | 1847 | R
| Branch Zero Current State - Circuit 8 | 8 | 1410 | [5 empty] | Analog Input | 1848 | R
| Branch Zero Current State - Circuit 9 | 9 | 1411 | [5 empty] | Analog Input | 1849 | R
| Branch Zero Current State - Circuit 10 | 10 | 1412 | [5 empty] | Analog Input | 1850 | R
| Branch Zero Current State - Circuit 11 | 11 | 1413 | [5 empty] | Analog Input | 1851 | R
| Branch Zero Current State - Circuit 12 | 12 | 1414 | [5 empty] | Analog Input | 1852 | R
| Branch Zero Current State - Circuit 13 | 13 | 1415 | [5 empty] | Analog Input | 1853 | R
| Branch Zero Current State - Circuit 14 | 14 | 1416 | [5 empty] | Analog Input | 1854 | R
| Branch Zero Current State - Circuit 15 | 15 | 1417 | [5 empty] | Analog Input | 1855 | R
| Branch Zero Current State - Circuit 16 | 16 | 1418 | [5 empty] | Analog Input | 1856 | R
| Branch Zero Current State - Circuit 17 | 17 | 1419 | [5 empty] | Analog Input | 1857 | R
| Branch Zero Current State - Circuit 18 | 18 | 1420 | [5 empty] | Analog Input | 1858 | R
| Branch Zero Current State - Circuit 19 | 19 | 1421 | [5 empty] | Analog Input | 1859 | R
| Branch Zero Current State - Circuit 20 | 20 | 1422 | [5 empty] | Analog Input | 1860 | R
| Branch Zero Current State - Circuit 21 | 21 | 1423 | [5 empty] | Analog Input | 1861 | R
| Branch Zero Current State - Circuit 22 | 22 | 1424 | [5 empty] | Analog Input | 1862 | R
| Branch Zero Current State - Circuit 23 | 23 | 1425 | [5 empty] | Analog Input | 1863 | R
| Branch Zero Current State - Circuit 24 | 24 | 1426 | [5 empty] | Analog Input | 1864 | R
| Branch Zero Current State - Circuit 25 | 25 | 1427 | [5 empty] | Analog Input | 1865 | R
| Branch Zero Current State - Circuit 26 | 26 | 1428 | [5 empty] | Analog Input | 1866 | R
| Branch Zero Current State - Circuit 27 | 27 | 1429 | [5 empty] | Analog Input | 1867 | R
| Branch Zero Current State - Circuit 28 | 28 | 1430 | [5 empty] | Analog Input | 1868 | R
| Branch Zero Current State - Circuit 29 | 29 | 1431 | [5 empty] | Analog Input | 1869 | R
| Branch Zero Current State - Circuit 30 | 30 | 1432 | [5 empty] | Analog Input | 1870 | R
| Branch Zero Current State - Circuit 31 | 31 | 1433 | [5 empty] | Analog Input | 1871 | R
| Branch Zero Current State - Circuit 32 | 32 | 1434 | [5 empty] | Analog Input | 1872 | R
| Branch Zero Current State - Circuit 33 | 33 | 1435 | [5 empty] | Analog Input | 1873 | R
| Branch Zero Current State - Circuit 34 | 34 | 1436 | [5 empty] | Analog Input | 1874 | R
| Branch Zero Current State - Circuit 35 | 35 | 1437 | [5 empty] | Analog Input | 1875 | R
| Branch Zero Current State - Circuit 36 | 36 | 1438 | [5 empty] | Analog Input | 1876 | R
| Branch Zero Current State - Circuit 37 | 37 | 1439 | [5 empty] | Analog Input | 1877 | R
| Branch Zero Current State - Circuit 38 | 38 | 1440 | [5 empty] | Analog Input | 1878 | R
| Branch Zero Current State - Circuit 39 | 39 | 1441 | [5 empty] | Analog Input | 1879 | R
| Branch Zero Current State - Circuit 40 | 40 | 1442 | [5 empty] | Analog Input | 1880 | R
| Branch Zero Current State - Circuit 41 | 41 | 1443 | [5 empty] | Analog Input | 1881 | R
| Branch Zero Current State - Circuit 42 | 42 | 1444 | [5 empty] | Analog Input | 1882 | R
| Branch Zero Current State - Circuit 43 | 43 | 1445 | [5 empty] | Analog Input | 1883 | R
| Branch Zero Current State - Circuit 44 | 44 | 1446 | [5 empty] | Analog Input | 1884 | R
| Branch Zero Current State - Circuit 45 | 45 | 1447 | [5 empty] | Analog Input | 1885 | R
| Branch Zero Current State - Circuit 46 | 46 | 1448 | [5 empty] | Analog Input | 1886 | R
| Branch Zero Current State - Circuit 47 | 47 | 1449 | [5 empty] | Analog Input | 1887 | R
| Branch Zero Current State - Circuit 48 | 48 | 1450 | [5 empty] | Analog Input | 1888 | R
| Branch Zero Current State - Circuit 49 | 49 | 1451 | [5 empty] | Analog Input | 1889 | R
| Branch Zero Current State - Circuit 50 | 50 | 1452 | [5 empty] | Analog Input | 1890 | R
| Branch Zero Current State - Circuit 51 | 51 | 1453 | [5 empty] | Analog Input | 1891 | R
| Branch Zero Current State - Circuit 52 | 52 | 1454 | [5 empty] | Analog Input | 1892 | R
| Branch Zero Current State - Circuit 53 | 53 | 1455 | [5 empty] | Analog Input | 1893 | R
| Branch Zero Current State - Circuit 54 | 54 | 1456 | [5 empty] | Analog Input | 1894 | R
| Branch Zero Current State - Circuit 55 | 55 | 1457 | [5 empty] | Analog Input | 1895 | R
| Branch Zero Current State - Circuit 56 | 56 | 1458 | [5 empty] | Analog Input | 1896 | R
| Branch Zero Current State - Circuit 57 | 57 | 1459 | [5 empty] | Analog Input | 1897 | R
| Branch Zero Current State - Circuit 58 | 58 | 1460 | [5 empty] | Analog Input | 1898 | R
| Branch Zero Current State - Circuit 59 | 59 | 1461 | [5 empty] | Analog Input | 1899 | R
| Branch Zero Current State - Circuit 60 | 60 | 1462 | [5 empty] | Analog Input | 1900 | R
| Branch Zero Current State - Circuit 61 | 61 | 1463 | [5 empty] | Analog Input | 1901 | R
| Branch Zero Current State - Circuit 62 | 62 | 1464 | [5 empty] | Analog Input | 1902 | R
| Branch Zero Current State - Circuit 63 | 63 | 1465 | [5 empty] | Analog Input | 1903 | R
| Branch Zero Current State - Circuit 64 | 64 | 1466 | [5 empty] | Analog Input | 1904 | R
| Branch Zero Current State - Circuit 65 | 65 | 1467 | [5 empty] | Analog Input | 1905 | R
| Branch Zero Current State - Circuit 66 | 66 | 1468 | [5 empty] | Analog Input | 1906 | R
| Branch Zero Current State - Circuit 67 | 67 | 1469 | [5 empty] | Analog Input | 1907 | R
| Branch Zero Current State - Circuit 68 | 68 | 1470 | [5 empty] | Analog Input | 1908 | R
| Branch Zero Current State - Circuit 69 | 69 | 1471 | [5 empty] | Analog Input | 1909 | R
| Branch Zero Current State - Circuit 70 | 70 | 1472 | [5 empty] | Analog Input | 1910 | R
| Branch Zero Current State - Circuit 71 | 71 | 1473 | [5 empty] | Analog Input | 1911 | R
| Branch Zero Current State - Circuit 72 | 72 | 1474 | [5 empty] | Analog Input | 1912 | R
| Branch Zero Current State - Circuit 73 | 73 | 1475 | [5 empty] | Analog Input | 1913 | R
| Branch Zero Current State - Circuit 74 | 74 | 1476 | [5 empty] | Analog Input | 1914 | R
| Branch Zero Current State - Circuit 75 | 75 | 1477 | [5 empty] | Analog Input | 1915 | R
| Branch Zero Current State - Circuit 76 | 76 | 1478 | [5 empty] | Analog Input | 1916 | R
| Branch Zero Current State - Circuit 77 | 77 | 1479 | [5 empty] | Analog Input | 1917 | R
| Branch Zero Current State - Circuit 78 | 78 | 1480 | [5 empty] | Analog Input | 1918 | R
| Branch Zero Current State - Circuit 79 | 79 | 1481 | [5 empty] | Analog Input | 1919 | R
| Branch Zero Current State - Circuit 80 | 80 | 1482 | [5 empty] | Analog Input | 1920 | R
| Branch Zero Current State - Circuit 81 | 81 | 1483 | [5 empty] | Analog Input | 1921 | R
| Branch Zero Current State - Circuit 82 | 82 | 1484 | [5 empty] | Analog Input | 1922 | R
| Branch Zero Current State - Circuit 83 | 83 | 1485 | [5 empty] | Analog Input | 1923 | R
| Branch Zero Current State - Circuit 84 | 84 | 1486 | [5 empty] | Analog Input | 1924 | R
| Branch Zero Current State - Circuit 85 | 85 | 1487 | [5 empty] | Analog Input | 1925 | R
| Branch Zero Current State - Circuit 86 | 86 | 1488 | [5 empty] | Analog Input | 1926 | R
| Branch Zero Current State - Circuit 87 | 87 | 1489 | [5 empty] | Analog Input | 1927 | R
| Branch Zero Current State - Circuit 88 | 88 | 1490 | [5 empty] | Analog Input | 1928 | R
| Branch Zero Current State - Circuit 89 | 89 | 1491 | [5 empty] | Analog Input | 1929 | R
| Branch Zero Current State - Circuit 90 | 90 | 1492 | [5 empty] | Analog Input | 1930 | R
| Branch Zero Current State - Circuit 91 | 91 | 1493 | [5 empty] | Analog Input | 1931 | R
| Branch Zero Current State - Circuit 92 | 92 | 1494 | [5 empty] | Analog Input | 1932 | R
| Branch Zero Current State - Circuit 93 | 93 | 1495 | [5 empty] | Analog Input | 1933 | R
| Branch Zero Current State - Circuit 94 | 94 | 1496 | [5 empty] | Analog Input | 1934 | R
| Branch Zero Current State - Circuit 95 | 95 | 1497 | [5 empty] | Analog Input | 1935 | R
| Branch Zero Current State - Circuit 96 | 96 | 1498 | [5 empty] | Analog Input | 1936 | R
Smart Port & Panel Information
| Smart Port 1/2 (Panel 1) Circuit Configuration |  | 1800 | [7 empty] | R/W | NV |  | 0 - 4 | 0 = Top Feed, 1 = Bottom Feed, 2 = Single Row Sequential, 3 = Single Row Odd/Even, 4 = Sequential (Duplicated from register 147 & 148)
| Smart Port 3/4 (Panel 2) Circuit Configuration |  | 1801 | [7 empty] | R/W | NV |  | 0 - 4
| Panel 1 Location (64 Registers) |  | 1802 | 1865 | [6 empty] | R/W | NV |  |  | Location string for Panel 1 and Panel 2, Each string supports up to 128 characters (64 registers)
| Panel 2 Location (64 Registers) |  | 1866 | 1929 | [6 empty] | R/W | NV
| Smart Port 1 Status |  | 1930 | [7 empty] | R |  |  | 0 - 3 | 0 = Nothing Detected, 1 = Status OK, 2 = Offline, 3 = Invalid Device Detected
| Smart Port 2 Status |  | 1931 | [7 empty] | R
| Smart Port 3 Status |  | 1932 | [7 empty] | R
| Smart Port 4 Status |  | 1933 | [7 empty] | R
| # of Devices Connected to Smart Port 1 |  | 1934
| # of Devices Connected to Smart Port 2 |  | 1935
| # of Devices Connected to Smart Port 3 |  | 1936
| # of Devices Connected to Smart Port 4 |  | 1937
| # of Active Channels on Smart Port 1 |  | 1938
| # of Active Channels on Smart Port 2 |  | 1939
| # of Active Channels on Smart Port 3 |  | 1940
| # of Active Channels on Smart Port 4 |  | 1941
Smart Port #1 Information
| Smart Port #1 Device #1 Product ID |  | 1942
| Smart Port #1 Device #2 Product ID |  | 1943
| Smart Port #1 Device #3 Product ID |  | 1944
| Smart Port #1 Device #4 Product ID |  | 1945
| Smart Port #1 Device #5 Product ID |  | 1946
| Smart Port #1 Device #6 Product ID |  | 1947
| Smart Port #1 Device #7 Product ID |  | 1948
| Smart Port #1 Device #8 Product ID |  | 1949
| Smart Port #1 Device #1 Serial Number |  | 1950 | 1951
| Smart Port #1 Device #2 Serial Number |  | 1952 | 1953
| Smart Port #1 Device #3 Serial Number |  | 1954 | 1955
| Smart Port #1 Device #4 Serial Number |  | 1956 | 1957
| Smart Port #1 Device #5 Serial Number |  | 1958 | 1959
| Smart Port #1 Device #6 Serial Number |  | 1960 | 1961
| Smart Port #1 Device #7 Serial Number |  | 1962 | 1963
| Smart Port #1 Device #8 Serial Number |  | 1964 | 1965
| Smart Port #1 Device #1 Firmware Version |  | 1966
| Smart Port #1 Device #2 Firmware Version |  | 1967
| Smart Port #1 Device #3 Firmware Version |  | 1968
| Smart Port #1 Device #4 Firmware Version |  | 1969
| Smart Port #1 Device #5 Firmware Version |  | 1970
| Smart Port #1 Device #6 Firmware Version |  | 1971
| Smart Port #1 Device #7 Firmware Version |  | 1972
| Smart Port #1 Device #8 Firmware Version |  | 1973
| Smart Port #1 Device #1 Status |  | 1974
| Smart Port #1 Device #2 Status |  | 1975
| Smart Port #1 Device #3 Status |  | 1976
| Smart Port #1 Device #4 Status |  | 1977
| Smart Port #1 Device #5 Status |  | 1978
| Smart Port #1 Device #6 Status |  | 1979
| Smart Port #1 Device #7 Status |  | 1980
| Smart Port #1 Device #8 Status |  | 1981
| Smart Port #1 Device #1 Name (20 Registers) |  | 1982 | 2001
| Smart Port #1 Device #2 Name (20 Registers) |  | 2002 | 2021
| Smart Port #1 Device #3 Name (20 Registers) |  | 2022 | 2041
| Smart Port #1 Device #4 Name (20 Registers) |  | 2042 | 2061
| Smart Port #1 Device #5 Name (20 Registers) |  | 2062 | 2081
| Smart Port #1 Device #6 Name (20 Registers) |  | 2082 | 2101
| Smart Port #1 Device #7 Name (20 Registers) |  | 2102 | 2121
| Smart Port #1 Device #8 Name (20 Registers) |  | 2122 | 2141
Smart Port #2 Information
| Smart Port #2 Device #1 Product ID |  | 2142
| Smart Port #2 Device #2 Product ID |  | 2143
| Smart Port #2 Device #3 Product ID |  | 2144
| Smart Port #2 Device #4 Product ID |  | 2145
| Smart Port #2 Device #5 Product ID |  | 2146
| Smart Port #2 Device #6 Product ID |  | 2147
| Smart Port #2 Device #7 Product ID |  | 2148
| Smart Port #2 Device #8 Product ID |  | 2149
| Smart Port #2 Device #1 Serial Number |  | 2150 | 2151
| Smart Port #2 Device #2 Serial Number |  | 2152 | 2153
| Smart Port #2 Device #3 Serial Number |  | 2154 | 2155
| Smart Port #2 Device #4 Serial Number |  | 2156 | 2157
| Smart Port #2 Device #5 Serial Number |  | 2158 | 2159
| Smart Port #2 Device #6 Serial Number |  | 2160 | 2161
| Smart Port #2 Device #7 Serial Number |  | 2162 | 2163
| Smart Port #2 Device #8 Serial Number |  | 2164 | 2165
| Smart Port #2 Device #1 Firmware Version |  | 2166
| Smart Port #2 Device #2 Firmware Version |  | 2167
| Smart Port #2 Device #3 Firmware Version |  | 2168
| Smart Port #2 Device #4 Firmware Version |  | 2169
| Smart Port #2 Device #5 Firmware Version |  | 2170
| Smart Port #2 Device #6 Firmware Version |  | 2171
| Smart Port #2 Device #7 Firmware Version |  | 2172
| Smart Port #2 Device #8 Firmware Version |  | 2173
| Smart Port #2 Device #1 Status |  | 2174
| Smart Port #2 Device #2 Status |  | 2175
| Smart Port #2 Device #3 Status |  | 2176
| Smart Port #2 Device #4 Status |  | 2177
| Smart Port #2 Device #5 Status |  | 2178
| Smart Port #2 Device #6 Status |  | 2179
| Smart Port #2 Device #7 Status |  | 2180
| Smart Port #2 Device #8 Status |  | 2181
| Smart Port #2 Device #1 Name (20 Registers) |  | 2182 | 2201
| Smart Port #2 Device #2 Name (20 Registers) |  | 2202 | 2221
| Smart Port #2 Device #3 Name (20 Registers) |  | 2222 | 2241
| Smart Port #2 Device #4 Name (20 Registers) |  | 2242 | 2261
| Smart Port #2 Device #5 Name (20 Registers) |  | 2262 | 2281
| Smart Port #2 Device #6 Name (20 Registers) |  | 2282 | 2301
| Smart Port #2 Device #7 Name (20 Registers) |  | 2302 | 2321
| Smart Port #2 Device #8 Name (20 Registers) |  | 2322 | 2341
Smart Port #3 Information
| Smart Port #3 Device #1 Product ID |  | 2342
| Smart Port #3 Device #2 Product ID |  | 2343
| Smart Port #3 Device #3 Product ID |  | 2344
| Smart Port #3 Device #4 Product ID |  | 2345
| Smart Port #3 Device #5 Product ID |  | 2346
| Smart Port #3 Device #6 Product ID |  | 2347
| Smart Port #3 Device #7 Product ID |  | 2348
| Smart Port #3 Device #8 Product ID |  | 2349
| Smart Port #3 Device #1 Serial Number |  | 2350 | 2351
| Smart Port #3 Device #2 Serial Number |  | 2352 | 2353
| Smart Port #3 Device #3 Serial Number |  | 2354 | 2355
| Smart Port #3 Device #4 Serial Number |  | 2356 | 2357
| Smart Port #3 Device #5 Serial Number |  | 2358 | 2359
| Smart Port #3 Device #6 Serial Number |  | 2360 | 2361
| Smart Port #3 Device #7 Serial Number |  | 2362 | 2363
| Smart Port #3 Device #8 Serial Number |  | 2364 | 2365
| Smart Port #3 Device #1 Firmware Version |  | 2366
| Smart Port #3 Device #2 Firmware Version |  | 2367
| Smart Port #3 Device #3 Firmware Version |  | 2368
| Smart Port #3 Device #4 Firmware Version |  | 2369
| Smart Port #3 Device #5 Firmware Version |  | 2370
| Smart Port #3 Device #6 Firmware Version |  | 2371
| Smart Port #3 Device #7 Firmware Version |  | 2372
| Smart Port #3 Device #8 Firmware Version |  | 2373
| Smart Port #3 Device #1 Status |  | 2374
| Smart Port #3 Device #2 Status |  | 2375
| Smart Port #3 Device #3 Status |  | 2376
| Smart Port #3 Device #4 Status |  | 2377
| Smart Port #3 Device #5 Status |  | 2378
| Smart Port #3 Device #6 Status |  | 2379
| Smart Port #3 Device #7 Status |  | 2380
| Smart Port #3 Device #8 Status |  | 2381
| Smart Port #3 Device #1 Name (20 Registers) |  | 2382 | 2401
| Smart Port #3 Device #2 Name (20 Registers) |  | 2402 | 2421
| Smart Port #3 Device #3 Name (20 Registers) |  | 2422 | 2441
| Smart Port #3 Device #4 Name (20 Registers) |  | 2442 | 2461
| Smart Port #3 Device #5 Name (20 Registers) |  | 2462 | 2481
| Smart Port #3 Device #6 Name (20 Registers) |  | 2482 | 2501
| Smart Port #3 Device #7 Name (20 Registers) |  | 2502 | 2521
| Smart Port #3 Device #8 Name (20 Registers) |  | 2522 | 2541
Smart Port #4 Information
| Smart Port #4 Device #1 Product ID |  | 2542
| Smart Port #4 Device #2 Product ID |  | 2543
| Smart Port #4 Device #3 Product ID |  | 2544
| Smart Port #4 Device #4 Product ID |  | 2545
| Smart Port #4 Device #5 Product ID |  | 2546
| Smart Port #4 Device #6 Product ID |  | 2547
| Smart Port #4 Device #7 Product ID |  | 2548
| Smart Port #4 Device #8 Product ID |  | 2549
| Smart Port #4 Device #1 Serial Number |  | 2550 | 2551
| Smart Port #4 Device #2 Serial Number |  | 2552 | 2553
| Smart Port #4 Device #3 Serial Number |  | 2554 | 2555
| Smart Port #4 Device #4 Serial Number |  | 2556 | 2557
| Smart Port #4 Device #5 Serial Number |  | 2558 | 2559
| Smart Port #4 Device #6 Serial Number |  | 2560 | 2561
| Smart Port #4 Device #7 Serial Number |  | 2562 | 2563
| Smart Port #4 Device #8 Serial Number |  | 2564 | 2565
| Smart Port #4 Device #1 Firmware Version |  | 2566
| Smart Port #4 Device #2 Firmware Version |  | 2567
| Smart Port #4 Device #3 Firmware Version |  | 2568
| Smart Port #4 Device #4 Firmware Version |  | 2569
| Smart Port #4 Device #5 Firmware Version |  | 2570
| Smart Port #4 Device #6 Firmware Version |  | 2571
| Smart Port #4 Device #7 Firmware Version |  | 2572
| Smart Port #4 Device #8 Firmware Version |  | 2573
| Smart Port #4 Device #1 Status |  | 2574
| Smart Port #4 Device #2 Status |  | 2575
| Smart Port #4 Device #3 Status |  | 2576
| Smart Port #4 Device #4 Status |  | 2577
| Smart Port #4 Device #5 Status |  | 2578
| Smart Port #4 Device #6 Status |  | 2579
| Smart Port #4 Device #7 Status |  | 2580
| Smart Port #4 Device #8 Status |  | 2581
| Smart Port #4 Device #1 Name (20 Registers) |  | 2582 | 2601
| Smart Port #4 Device #2 Name (20 Registers) |  | 2602 | 2621
| Smart Port #4 Device #3 Name (20 Registers) |  | 2622 | 2641
| Smart Port #4 Device #4 Name (20 Registers) |  | 2642 | 2661
| Smart Port #4 Device #5 Name (20 Registers) |  | 2662 | 2681
| Smart Port #4 Device #6 Name (20 Registers) |  | 2682 | 2701
| Smart Port #4 Device #7 Name (20 Registers) |  | 2702 | 2721
| Smart Port #4 Device #8 Name (20 Registers) |  | 2722 | 2741
Dynamic Smart Port | See Pointmap Based on Attached Card |  | 3000 | 3999
| Smart Port #1 (Dynamic Maps) |  | 3000 | 3249
| Smart Port #2 (Dynamic Maps) |  | 3250 | 3499
| Smart Port #3 (Dynamic Maps) |  | 3500 | 3749
| Smart Port #4 (Dynamic Maps) |  | 3750 | 3999
Reserved for AUX |  |  | 4000 | 4799
Voltage Readings
| Voltage Scale |  | 4800 |  |  | INT16 |  |  |  |  | R
| Frequency |  | 4801 |  | -2 | UINT16 | 4900 | 4901 | Analog Input | 1 | R |  | Hz |  | Derived from L1
| Voltage LN Average |  | 4802 |  | 4800 | UINT16 | 4902 | 4903 | Analog Input | 2 | R |  | Volts
| Voltage LL Average |  | 4803 |  | 4800 | UINT16 | 4904 | 4905 | Analog Input | 3 | R |  | Volts
| Voltage LN |  | 4804 | 4806 | 4800 | UINT16 | 4906 | 4911 | Analog Input | 4 - 6 | R |  | Volts
| Voltage L1 |  | 4804 |  | 4800 | UINT16 | 4906 | 4907 | Analog Input | 4 | R |  | Volts
| Voltage L2 |  | 4805 |  | 4800 | UINT16 | 4908 | 4909 | Analog Input | 5 | R |  | Volts
| Voltage L3 |  | 4806 |  | 4800 | UINT16 | 4910 | 4911 | Analog Input | 6 | R |  | Volts
| Voltage LL |  | 4807 | 4809 | 4800 | UINT16 | 4912 | 4917 | Analog Input | 7 - 9 | R |  | Volts
| Voltage L1 - L2 |  | 4807 |  | 4800 | UINT16 | 4912 | 4913 | Analog Input | 7 | R |  | Volts
| Voltage L2 - L3 |  | 4808 |  | 4800 | UINT16 | 4914 | 4915 | Analog Input | 8 | R |  | Volts
| Voltage L3 - L1 |  | 4809 |  | 4800 | UINT16 | 4916 | 4917 | Analog Input | 9 | R |  | Volts
| Percent THD |  | 4810 | 4813 | -1 | UINT16 | 4918 | 4925 | Analog Input | 10 - 13 | R |  | Percent
| Percent THD Average (L1, L2 & L3) |  | 4810 |  | -1 | UINT16 | 4918 | 4919 | Analog Input | 10 | R |  | Percent
| Percent THD - L1 |  | 4811 |  | -1 | UINT16 | 4920 | 4921 | Analog Input | 11 | R |  | Percent
| Percent THD - L2 |  | 4812 |  | -1 | UINT16 | 4922 | 4923 | Analog Input | 12 | R |  | Percent
| Percent THD - L3 |  | 4813 |  | -1 | UINT16 | 4924 | 4925 | Analog Input | 13 | R |  | Percent
| Voltage Angle |  | 4814 | 4816 | -1 | INT16 | 4926 | 4931 | Analog Input | 14 - 16 | R |  | Degrees
| L1 Angle |  | 4814 |  | -1 | INT16 | 4926 | 4927 | Analog Input | 14 | R |  | Degrees |  | Reference used to derive angle for other phases - Always Reads 0
| L2 Angle |  | 4815 |  | -1 | INT16 | 4928 | 4929 | Analog Input | 15 | R |  | Degrees
| L3 Angle |  | 4816 |  | -1 | INT16 | 4930 | 4931 | Analog Input | 16 | R |  | Degrees
Single Phase Reading by Type
| Energy Scale |  | 5000 | 5095 |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 1 | 1 | 5000 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 2 | 2 | 5001 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 3 | 3 | 5002 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 4 | 4 | 5003 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 5 | 5 | 5004 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 6 | 6 | 5005 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 7 | 7 | 5006 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 8 | 8 | 5007 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 9 | 9 | 5008 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 10 | 10 | 5009 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 11 | 11 | 5010 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 12 | 12 | 5011 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 13 | 13 | 5012 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 14 | 14 | 5013 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 15 | 15 | 5014 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 16 | 16 | 5015 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 17 | 17 | 5016 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 18 | 18 | 5017 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 19 | 19 | 5018 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 20 | 20 | 5019 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 21 | 21 | 5020 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 22 | 22 | 5021 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 23 | 23 | 5022 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 24 | 24 | 5023 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 25 | 25 | 5024 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 26 | 26 | 5025 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 27 | 27 | 5026 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 28 | 28 | 5027 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 29 | 29 | 5028 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 30 | 30 | 5029 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 31 | 31 | 5030 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 32 | 32 | 5031 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 33 | 33 | 5032 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 34 | 34 | 5033 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 35 | 35 | 5034 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 36 | 36 | 5035 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 37 | 37 | 5036 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 38 | 38 | 5037 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 39 | 39 | 5038 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 40 | 40 | 5039 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 41 | 41 | 5040 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 42 | 42 | 5041 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 43 | 43 | 5042 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 44 | 44 | 5043 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 45 | 45 | 5044 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 46 | 46 | 5045 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 47 | 47 | 5046 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 48 | 48 | 5047 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 49 | 49 | 5048 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 50 | 50 | 5049 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 51 | 51 | 5050 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 52 | 52 | 5051 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 53 | 53 | 5052 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 54 | 54 | 5053 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 55 | 55 | 5054 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 56 | 56 | 5055 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 57 | 57 | 5056 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 58 | 58 | 5057 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 59 | 59 | 5058 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 60 | 60 | 5059 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 61 | 61 | 5060 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 62 | 62 | 5061 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 63 | 63 | 5062 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 64 | 64 | 5063 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 65 | 65 | 5064 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 66 | 66 | 5065 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 67 | 67 | 5066 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 68 | 68 | 5067 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 69 | 69 | 5068 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 70 | 70 | 5069 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 71 | 71 | 5070 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 72 | 72 | 5071 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 73 | 73 | 5072 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 74 | 74 | 5073 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 75 | 75 | 5074 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 76 | 76 | 5075 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 77 | 77 | 5076 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 78 | 78 | 5077 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 79 | 79 | 5078 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 80 | 80 | 5079 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 81 | 81 | 5080 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 82 | 82 | 5081 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 83 | 83 | 5082 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 84 | 84 | 5083 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 85 | 85 | 5084 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 86 | 86 | 5085 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 87 | 87 | 5086 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 88 | 88 | 5087 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 89 | 89 | 5088 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 90 | 90 | 5089 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 91 | 91 | 5090 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 92 | 92 | 5091 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 93 | 93 | 5092 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 94 | 94 | 5093 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 95 | 95 | 5094 |  |  | INT16 |  |  |  |  | R
| Energy Scale - Circuit 96 | 96 | 5095 |  |  | INT16 |  |  |  |  | R
| Power Scale |  | 5096 | 5191 |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 1 | 1 | 5096 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 2 | 2 | 5097 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 3 | 3 | 5098 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 4 | 4 | 5099 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 5 | 5 | 5100 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 6 | 6 | 5101 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 7 | 7 | 5102 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 8 | 8 | 5103 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 9 | 9 | 5104 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 10 | 10 | 5105 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 11 | 11 | 5106 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 12 | 12 | 5107 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 13 | 13 | 5108 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 14 | 14 | 5109 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 15 | 15 | 5110 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 16 | 16 | 5111 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 17 | 17 | 5112 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 18 | 18 | 5113 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 19 | 19 | 5114 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 20 | 20 | 5115 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 21 | 21 | 5116 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 22 | 22 | 5117 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 23 | 23 | 5118 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 24 | 24 | 5119 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 25 | 25 | 5120 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 26 | 26 | 5121 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 27 | 27 | 5122 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 28 | 28 | 5123 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 29 | 29 | 5124 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 30 | 30 | 5125 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 31 | 31 | 5126 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 32 | 32 | 5127 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 33 | 33 | 5128 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 34 | 34 | 5129 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 35 | 35 | 5130 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 36 | 36 | 5131 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 37 | 37 | 5132 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 38 | 38 | 5133 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 39 | 39 | 5134 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 40 | 40 | 5135 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 41 | 41 | 5136 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 42 | 42 | 5137 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 43 | 43 | 5138 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 44 | 44 | 5139 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 45 | 45 | 5140 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 46 | 46 | 5141 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 47 | 47 | 5142 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 48 | 48 | 5143 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 49 | 49 | 5144 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 50 | 50 | 5145 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 51 | 51 | 5146 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 52 | 52 | 5147 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 53 | 53 | 5148 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 54 | 54 | 5149 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 55 | 55 | 5150 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 56 | 56 | 5151 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 57 | 57 | 5152 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 58 | 58 | 5153 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 59 | 59 | 5154 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 60 | 60 | 5155 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 61 | 61 | 5156 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 62 | 62 | 5157 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 63 | 63 | 5158 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 64 | 64 | 5159 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 65 | 65 | 5160 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 66 | 66 | 5161 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 67 | 67 | 5162 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 68 | 68 | 5163 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 69 | 69 | 5164 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 70 | 70 | 5165 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 71 | 71 | 5166 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 72 | 72 | 5167 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 73 | 73 | 5168 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 74 | 74 | 5169 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 75 | 75 | 5170 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 76 | 76 | 5171 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 77 | 77 | 5172 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 78 | 78 | 5173 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 79 | 79 | 5174 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 80 | 80 | 5175 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 81 | 81 | 5176 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 82 | 82 | 5177 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 83 | 83 | 5178 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 84 | 84 | 5179 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 85 | 85 | 5180 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 86 | 86 | 5181 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 87 | 87 | 5182 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 88 | 88 | 5183 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 89 | 89 | 5184 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 90 | 90 | 5185 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 91 | 91 | 5186 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 92 | 92 | 5187 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 93 | 93 | 5188 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 94 | 94 | 5189 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 95 | 95 | 5190 |  |  | INT16 |  |  |  |  | R
| Power Scale - Circuit 96 | 96 | 5191 |  |  | INT16 |  |  |  |  | R
| Current Scale |  | 5192 | 5287 |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 1 | 1 | 5192 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 2 | 2 | 5193 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 3 | 3 | 5194 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 4 | 4 | 5195 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 5 | 5 | 5196 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 6 | 6 | 5197 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 7 | 7 | 5198 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 8 | 8 | 5199 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 9 | 9 | 5200 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 10 | 10 | 5201 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 11 | 11 | 5202 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 12 | 12 | 5203 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 13 | 13 | 5204 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 14 | 14 | 5205 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 15 | 15 | 5206 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 16 | 16 | 5207 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 17 | 17 | 5208 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 18 | 18 | 5209 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 19 | 19 | 5210 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 20 | 20 | 5211 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 21 | 21 | 5212 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 22 | 22 | 5213 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 23 | 23 | 5214 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 24 | 24 | 5215 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 25 | 25 | 5216 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 26 | 26 | 5217 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 27 | 27 | 5218 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 28 | 28 | 5219 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 29 | 29 | 5220 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 30 | 30 | 5221 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 31 | 31 | 5222 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 32 | 32 | 5223 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 33 | 33 | 5224 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 34 | 34 | 5225 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 35 | 35 | 5226 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 36 | 36 | 5227 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 37 | 37 | 5228 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 38 | 38 | 5229 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 39 | 39 | 5230 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 40 | 40 | 5231 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 41 | 41 | 5232 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 42 | 42 | 5233 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 43 | 43 | 5234 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 44 | 44 | 5235 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 45 | 45 | 5236 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 46 | 46 | 5237 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 47 | 47 | 5238 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 48 | 48 | 5239 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 49 | 49 | 5240 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 50 | 50 | 5241 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 51 | 51 | 5242 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 52 | 52 | 5243 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 53 | 53 | 5244 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 54 | 54 | 5245 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 55 | 55 | 5246 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 56 | 56 | 5247 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 57 | 57 | 5248 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 58 | 58 | 5249 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 59 | 59 | 5250 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 60 | 60 | 5251 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 61 | 61 | 5252 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 62 | 62 | 5253 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 63 | 63 | 5254 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 64 | 64 | 5255 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 65 | 65 | 5256 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 66 | 66 | 5257 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 67 | 67 | 5258 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 68 | 68 | 5259 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 69 | 69 | 5260 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 70 | 70 | 5261 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 71 | 71 | 5262 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 72 | 72 | 5263 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 73 | 73 | 5264 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 74 | 74 | 5265 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 75 | 75 | 5266 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 76 | 76 | 5267 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 77 | 77 | 5268 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 78 | 78 | 5269 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 79 | 79 | 5270 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 80 | 80 | 5271 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 81 | 81 | 5272 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 82 | 82 | 5273 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 83 | 83 | 5274 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 84 | 84 | 5275 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 85 | 85 | 5276 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 86 | 86 | 5277 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 87 | 87 | 5278 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 88 | 88 | 5279 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 89 | 89 | 5280 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 90 | 90 | 5281 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 91 | 91 | 5282 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 92 | 92 | 5283 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 93 | 93 | 5284 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 94 | 94 | 5285 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 95 | 95 | 5286 |  |  | INT16 |  |  |  |  | R
| Current Scale - Circuit 96 | 96 | 5287 |  |  | INT16 |  |  |  |  | R
| kWh |  | 5288 | 5479 | Energy | UINT32 | 10000 | 10191 | Analog Input | 17 - 112 | R | NV | kWh
| kWh - Circuit 1 | 1 | 5288 | 5289 | 5000 | UINT32 | 10000 | 10001 | Analog Input | 17 | R | NV | kWh
| kWh - Circuit 2 | 2 | 5290 | 5291 | 5001 | UINT32 | 10002 | 10003 | Analog Input | 18 | R | NV | kWh
| kWh - Circuit 3 | 3 | 5292 | 5293 | 5002 | UINT32 | 10004 | 10005 | Analog Input | 19 | R | NV | kWh
| kWh - Circuit 4 | 4 | 5294 | 5295 | 5003 | UINT32 | 10006 | 10007 | Analog Input | 20 | R | NV | kWh
| kWh - Circuit 5 | 5 | 5296 | 5297 | 5004 | UINT32 | 10008 | 10009 | Analog Input | 21 | R | NV | kWh
| kWh - Circuit 6 | 6 | 5298 | 5299 | 5005 | UINT32 | 10010 | 10011 | Analog Input | 22 | R | NV | kWh
| kWh - Circuit 7 | 7 | 5300 | 5301 | 5006 | UINT32 | 10012 | 10013 | Analog Input | 23 | R | NV | kWh
| kWh - Circuit 8 | 8 | 5302 | 5303 | 5007 | UINT32 | 10014 | 10015 | Analog Input | 24 | R | NV | kWh
| kWh - Circuit 9 | 9 | 5304 | 5305 | 5008 | UINT32 | 10016 | 10017 | Analog Input | 25 | R | NV | kWh
| kWh - Circuit 10 | 10 | 5306 | 5307 | 5009 | UINT32 | 10018 | 10019 | Analog Input | 26 | R | NV | kWh
| kWh - Circuit 11 | 11 | 5308 | 5309 | 5010 | UINT32 | 10020 | 10021 | Analog Input | 27 | R | NV | kWh
| kWh - Circuit 12 | 12 | 5310 | 5311 | 5011 | UINT32 | 10022 | 10023 | Analog Input | 28 | R | NV | kWh
| kWh - Circuit 13 | 13 | 5312 | 5313 | 5012 | UINT32 | 10024 | 10025 | Analog Input | 29 | R | NV | kWh
| kWh - Circuit 14 | 14 | 5314 | 5315 | 5013 | UINT32 | 10026 | 10027 | Analog Input | 30 | R | NV | kWh
| kWh - Circuit 15 | 15 | 5316 | 5317 | 5014 | UINT32 | 10028 | 10029 | Analog Input | 31 | R | NV | kWh
| kWh - Circuit 16 | 16 | 5318 | 5319 | 5015 | UINT32 | 10030 | 10031 | Analog Input | 32 | R | NV | kWh
| kWh - Circuit 17 | 17 | 5320 | 5321 | 5016 | UINT32 | 10032 | 10033 | Analog Input | 33 | R | NV | kWh
| kWh - Circuit 18 | 18 | 5322 | 5323 | 5017 | UINT32 | 10034 | 10035 | Analog Input | 34 | R | NV | kWh
| kWh - Circuit 19 | 19 | 5324 | 5325 | 5018 | UINT32 | 10036 | 10037 | Analog Input | 35 | R | NV | kWh
| kWh - Circuit 20 | 20 | 5326 | 5327 | 5019 | UINT32 | 10038 | 10039 | Analog Input | 36 | R | NV | kWh
| kWh - Circuit 21 | 21 | 5328 | 5329 | 5020 | UINT32 | 10040 | 10041 | Analog Input | 37 | R | NV | kWh
| kWh - Circuit 22 | 22 | 5330 | 5331 | 5021 | UINT32 | 10042 | 10043 | Analog Input | 38 | R | NV | kWh
| kWh - Circuit 23 | 23 | 5332 | 5333 | 5022 | UINT32 | 10044 | 10045 | Analog Input | 39 | R | NV | kWh
| kWh - Circuit 24 | 24 | 5334 | 5335 | 5023 | UINT32 | 10046 | 10047 | Analog Input | 40 | R | NV | kWh
| kWh - Circuit 25 | 25 | 5336 | 5337 | 5024 | UINT32 | 10048 | 10049 | Analog Input | 41 | R | NV | kWh
| kWh - Circuit 26 | 26 | 5338 | 5339 | 5025 | UINT32 | 10050 | 10051 | Analog Input | 42 | R | NV | kWh
| kWh - Circuit 27 | 27 | 5340 | 5341 | 5026 | UINT32 | 10052 | 10053 | Analog Input | 43 | R | NV | kWh
| kWh - Circuit 28 | 28 | 5342 | 5343 | 5027 | UINT32 | 10054 | 10055 | Analog Input | 44 | R | NV | kWh
| kWh - Circuit 29 | 29 | 5344 | 5345 | 5028 | UINT32 | 10056 | 10057 | Analog Input | 45 | R | NV | kWh
| kWh - Circuit 30 | 30 | 5346 | 5347 | 5029 | UINT32 | 10058 | 10059 | Analog Input | 46 | R | NV | kWh
| kWh - Circuit 31 | 31 | 5348 | 5349 | 5030 | UINT32 | 10060 | 10061 | Analog Input | 47 | R | NV | kWh
| kWh - Circuit 32 | 32 | 5350 | 5351 | 5031 | UINT32 | 10062 | 10063 | Analog Input | 48 | R | NV | kWh
| kWh - Circuit 33 | 33 | 5352 | 5353 | 5032 | UINT32 | 10064 | 10065 | Analog Input | 49 | R | NV | kWh
| kWh - Circuit 34 | 34 | 5354 | 5355 | 5033 | UINT32 | 10066 | 10067 | Analog Input | 50 | R | NV | kWh
| kWh - Circuit 35 | 35 | 5356 | 5357 | 5034 | UINT32 | 10068 | 10069 | Analog Input | 51 | R | NV | kWh
| kWh - Circuit 36 | 36 | 5358 | 5359 | 5035 | UINT32 | 10070 | 10071 | Analog Input | 52 | R | NV | kWh
| kWh - Circuit 37 | 37 | 5360 | 5361 | 5036 | UINT32 | 10072 | 10073 | Analog Input | 53 | R | NV | kWh
| kWh - Circuit 38 | 38 | 5362 | 5363 | 5037 | UINT32 | 10074 | 10075 | Analog Input | 54 | R | NV | kWh
| kWh - Circuit 39 | 39 | 5364 | 5365 | 5038 | UINT32 | 10076 | 10077 | Analog Input | 55 | R | NV | kWh
| kWh - Circuit 40 | 40 | 5366 | 5367 | 5039 | UINT32 | 10078 | 10079 | Analog Input | 56 | R | NV | kWh
| kWh - Circuit 41 | 41 | 5368 | 5369 | 5040 | UINT32 | 10080 | 10081 | Analog Input | 57 | R | NV | kWh
| kWh - Circuit 42 | 42 | 5370 | 5371 | 5041 | UINT32 | 10082 | 10083 | Analog Input | 58 | R | NV | kWh
| kWh - Circuit 43 | 43 | 5372 | 5373 | 5042 | UINT32 | 10084 | 10085 | Analog Input | 59 | R | NV | kWh
| kWh - Circuit 44 | 44 | 5374 | 5375 | 5043 | UINT32 | 10086 | 10087 | Analog Input | 60 | R | NV | kWh
| kWh - Circuit 45 | 45 | 5376 | 5377 | 5044 | UINT32 | 10088 | 10089 | Analog Input | 61 | R | NV | kWh
| kWh - Circuit 46 | 46 | 5378 | 5379 | 5045 | UINT32 | 10090 | 10091 | Analog Input | 62 | R | NV | kWh
| kWh - Circuit 47 | 47 | 5380 | 5381 | 5046 | UINT32 | 10092 | 10093 | Analog Input | 63 | R | NV | kWh
| kWh - Circuit 48 | 48 | 5382 | 5383 | 5047 | UINT32 | 10094 | 10095 | Analog Input | 64 | R | NV | kWh
| kWh - Circuit 49 | 49 | 5384 | 5385 | 5048 | UINT32 | 10096 | 10097 | Analog Input | 65 | R | NV | kWh
| kWh - Circuit 50 | 50 | 5386 | 5387 | 5049 | UINT32 | 10098 | 10099 | Analog Input | 66 | R | NV | kWh
| kWh - Circuit 51 | 51 | 5388 | 5389 | 5050 | UINT32 | 10100 | 10101 | Analog Input | 67 | R | NV | kWh
| kWh - Circuit 52 | 52 | 5390 | 5391 | 5051 | UINT32 | 10102 | 10103 | Analog Input | 68 | R | NV | kWh
| kWh - Circuit 53 | 53 | 5392 | 5393 | 5052 | UINT32 | 10104 | 10105 | Analog Input | 69 | R | NV | kWh
| kWh - Circuit 54 | 54 | 5394 | 5395 | 5053 | UINT32 | 10106 | 10107 | Analog Input | 70 | R | NV | kWh
| kWh - Circuit 55 | 55 | 5396 | 5397 | 5054 | UINT32 | 10108 | 10109 | Analog Input | 71 | R | NV | kWh
| kWh - Circuit 56 | 56 | 5398 | 5399 | 5055 | UINT32 | 10110 | 10111 | Analog Input | 72 | R | NV | kWh
| kWh - Circuit 57 | 57 | 5400 | 5401 | 5056 | UINT32 | 10112 | 10113 | Analog Input | 73 | R | NV | kWh
| kWh - Circuit 58 | 58 | 5402 | 5403 | 5057 | UINT32 | 10114 | 10115 | Analog Input | 74 | R | NV | kWh
| kWh - Circuit 59 | 59 | 5404 | 5405 | 5058 | UINT32 | 10116 | 10117 | Analog Input | 75 | R | NV | kWh
| kWh - Circuit 60 | 60 | 5406 | 5407 | 5059 | UINT32 | 10118 | 10119 | Analog Input | 76 | R | NV | kWh
| kWh - Circuit 61 | 61 | 5408 | 5409 | 5060 | UINT32 | 10120 | 10121 | Analog Input | 77 | R | NV | kWh
| kWh - Circuit 62 | 62 | 5410 | 5411 | 5061 | UINT32 | 10122 | 10123 | Analog Input | 78 | R | NV | kWh
| kWh - Circuit 63 | 63 | 5412 | 5413 | 5062 | UINT32 | 10124 | 10125 | Analog Input | 79 | R | NV | kWh
| kWh - Circuit 64 | 64 | 5414 | 5415 | 5063 | UINT32 | 10126 | 10127 | Analog Input | 80 | R | NV | kWh
| kWh - Circuit 65 | 65 | 5416 | 5417 | 5064 | UINT32 | 10128 | 10129 | Analog Input | 81 | R | NV | kWh
| kWh - Circuit 66 | 66 | 5418 | 5419 | 5065 | UINT32 | 10130 | 10131 | Analog Input | 82 | R | NV | kWh
| kWh - Circuit 67 | 67 | 5420 | 5421 | 5066 | UINT32 | 10132 | 10133 | Analog Input | 83 | R | NV | kWh
| kWh - Circuit 68 | 68 | 5422 | 5423 | 5067 | UINT32 | 10134 | 10135 | Analog Input | 84 | R | NV | kWh
| kWh - Circuit 69 | 69 | 5424 | 5425 | 5068 | UINT32 | 10136 | 10137 | Analog Input | 85 | R | NV | kWh
| kWh - Circuit 70 | 70 | 5426 | 5427 | 5069 | UINT32 | 10138 | 10139 | Analog Input | 86 | R | NV | kWh
| kWh - Circuit 71 | 71 | 5428 | 5429 | 5070 | UINT32 | 10140 | 10141 | Analog Input | 87 | R | NV | kWh
| kWh - Circuit 72 | 72 | 5430 | 5431 | 5071 | UINT32 | 10142 | 10143 | Analog Input | 88 | R | NV | kWh
| kWh - Circuit 73 | 73 | 5432 | 5433 | 5072 | UINT32 | 10144 | 10145 | Analog Input | 89 | R | NV | kWh
| kWh - Circuit 74 | 74 | 5434 | 5435 | 5073 | UINT32 | 10146 | 10147 | Analog Input | 90 | R | NV | kWh
| kWh - Circuit 75 | 75 | 5436 | 5437 | 5074 | UINT32 | 10148 | 10149 | Analog Input | 91 | R | NV | kWh
| kWh - Circuit 76 | 76 | 5438 | 5439 | 5075 | UINT32 | 10150 | 10151 | Analog Input | 92 | R | NV | kWh
| kWh - Circuit 77 | 77 | 5440 | 5441 | 5076 | UINT32 | 10152 | 10153 | Analog Input | 93 | R | NV | kWh
| kWh - Circuit 78 | 78 | 5442 | 5443 | 5077 | UINT32 | 10154 | 10155 | Analog Input | 94 | R | NV | kWh
| kWh - Circuit 79 | 79 | 5444 | 5445 | 5078 | UINT32 | 10156 | 10157 | Analog Input | 95 | R | NV | kWh
| kWh - Circuit 80 | 80 | 5446 | 5447 | 5079 | UINT32 | 10158 | 10159 | Analog Input | 96 | R | NV | kWh
| kWh - Circuit 81 | 81 | 5448 | 5449 | 5080 | UINT32 | 10160 | 10161 | Analog Input | 97 | R | NV | kWh
| kWh - Circuit 82 | 82 | 5450 | 5451 | 5081 | UINT32 | 10162 | 10163 | Analog Input | 98 | R | NV | kWh
| kWh - Circuit 83 | 83 | 5452 | 5453 | 5082 | UINT32 | 10164 | 10165 | Analog Input | 99 | R | NV | kWh
| kWh - Circuit 84 | 84 | 5454 | 5455 | 5083 | UINT32 | 10166 | 10167 | Analog Input | 100 | R | NV | kWh
| kWh - Circuit 85 | 85 | 5456 | 5457 | 5084 | UINT32 | 10168 | 10169 | Analog Input | 101 | R | NV | kWh
| kWh - Circuit 86 | 86 | 5458 | 5459 | 5085 | UINT32 | 10170 | 10171 | Analog Input | 102 | R | NV | kWh
| kWh - Circuit 87 | 87 | 5460 | 5461 | 5086 | UINT32 | 10172 | 10173 | Analog Input | 103 | R | NV | kWh
| kWh - Circuit 88 | 88 | 5462 | 5463 | 5087 | UINT32 | 10174 | 10175 | Analog Input | 104 | R | NV | kWh
| kWh - Circuit 89 | 89 | 5464 | 5465 | 5088 | UINT32 | 10176 | 10177 | Analog Input | 105 | R | NV | kWh
| kWh - Circuit 90 | 90 | 5466 | 5467 | 5089 | UINT32 | 10178 | 10179 | Analog Input | 106 | R | NV | kWh
| kWh - Circuit 91 | 91 | 5468 | 5469 | 5090 | UINT32 | 10180 | 10181 | Analog Input | 107 | R | NV | kWh
| kWh - Circuit 92 | 92 | 5470 | 5471 | 5091 | UINT32 | 10182 | 10183 | Analog Input | 108 | R | NV | kWh
| kWh - Circuit 93 | 93 | 5472 | 5473 | 5092 | UINT32 | 10184 | 10185 | Analog Input | 109 | R | NV | kWh
| kWh - Circuit 94 | 94 | 5474 | 5475 | 5093 | UINT32 | 10186 | 10187 | Analog Input | 110 | R | NV | kWh
| kWh - Circuit 95 | 95 | 5476 | 5477 | 5094 | UINT32 | 10188 | 10189 | Analog Input | 111 | R | NV | kWh
| kWh - Circuit 96 | 96 | 5478 | 5479 | 5095 | UINT32 | 10190 | 10191 | Analog Input | 112 | R | NV | kWh
| kVARh |  | 5480 | 5671 | Energy | UINT32 | 10192 | 10383 | Analog Input | 113 - 208 | R | NV | kVARh
| kVARh - Circuit 1 | 1 | 5480 | 5481 | 5000 | UINT32 | 10192 | 10193 | Analog Input | 113 | R | NV | kVARh
| kVARh - Circuit 2 | 2 | 5482 | 5483 | 5001 | UINT32 | 10194 | 10195 | Analog Input | 114 | R | NV | kVARh
| kVARh - Circuit 3 | 3 | 5484 | 5485 | 5002 | UINT32 | 10196 | 10197 | Analog Input | 115 | R | NV | kVARh
| kVARh - Circuit 4 | 4 | 5486 | 5487 | 5003 | UINT32 | 10198 | 10199 | Analog Input | 116 | R | NV | kVARh
| kVARh - Circuit 5 | 5 | 5488 | 5489 | 5004 | UINT32 | 10200 | 10201 | Analog Input | 117 | R | NV | kVARh
| kVARh - Circuit 6 | 6 | 5490 | 5491 | 5005 | UINT32 | 10202 | 10203 | Analog Input | 118 | R | NV | kVARh
| kVARh - Circuit 7 | 7 | 5492 | 5493 | 5006 | UINT32 | 10204 | 10205 | Analog Input | 119 | R | NV | kVARh
| kVARh - Circuit 8 | 8 | 5494 | 5495 | 5007 | UINT32 | 10206 | 10207 | Analog Input | 120 | R | NV | kVARh
| kVARh - Circuit 9 | 9 | 5496 | 5497 | 5008 | UINT32 | 10208 | 10209 | Analog Input | 121 | R | NV | kVARh
| kVARh - Circuit 10 | 10 | 5498 | 5499 | 5009 | UINT32 | 10210 | 10211 | Analog Input | 122 | R | NV | kVARh
| kVARh - Circuit 11 | 11 | 5500 | 5501 | 5010 | UINT32 | 10212 | 10213 | Analog Input | 123 | R | NV | kVARh
| kVARh - Circuit 12 | 12 | 5502 | 5503 | 5011 | UINT32 | 10214 | 10215 | Analog Input | 124 | R | NV | kVARh
| kVARh - Circuit 13 | 13 | 5504 | 5505 | 5012 | UINT32 | 10216 | 10217 | Analog Input | 125 | R | NV | kVARh
| kVARh - Circuit 14 | 14 | 5506 | 5507 | 5013 | UINT32 | 10218 | 10219 | Analog Input | 126 | R | NV | kVARh
| kVARh - Circuit 15 | 15 | 5508 | 5509 | 5014 | UINT32 | 10220 | 10221 | Analog Input | 127 | R | NV | kVARh
| kVARh - Circuit 16 | 16 | 5510 | 5511 | 5015 | UINT32 | 10222 | 10223 | Analog Input | 128 | R | NV | kVARh
| kVARh - Circuit 17 | 17 | 5512 | 5513 | 5016 | UINT32 | 10224 | 10225 | Analog Input | 129 | R | NV | kVARh
| kVARh - Circuit 18 | 18 | 5514 | 5515 | 5017 | UINT32 | 10226 | 10227 | Analog Input | 130 | R | NV | kVARh
| kVARh - Circuit 19 | 19 | 5516 | 5517 | 5018 | UINT32 | 10228 | 10229 | Analog Input | 131 | R | NV | kVARh
| kVARh - Circuit 20 | 20 | 5518 | 5519 | 5019 | UINT32 | 10230 | 10231 | Analog Input | 132 | R | NV | kVARh
| kVARh - Circuit 21 | 21 | 5520 | 5521 | 5020 | UINT32 | 10232 | 10233 | Analog Input | 133 | R | NV | kVARh
| kVARh - Circuit 22 | 22 | 5522 | 5523 | 5021 | UINT32 | 10234 | 10235 | Analog Input | 134 | R | NV | kVARh
| kVARh - Circuit 23 | 23 | 5524 | 5525 | 5022 | UINT32 | 10236 | 10237 | Analog Input | 135 | R | NV | kVARh
| kVARh - Circuit 24 | 24 | 5526 | 5527 | 5023 | UINT32 | 10238 | 10239 | Analog Input | 136 | R | NV | kVARh
| kVARh - Circuit 25 | 25 | 5528 | 5529 | 5024 | UINT32 | 10240 | 10241 | Analog Input | 137 | R | NV | kVARh
| kVARh - Circuit 26 | 26 | 5530 | 5531 | 5025 | UINT32 | 10242 | 10243 | Analog Input | 138 | R | NV | kVARh
| kVARh - Circuit 27 | 27 | 5532 | 5533 | 5026 | UINT32 | 10244 | 10245 | Analog Input | 139 | R | NV | kVARh
| kVARh - Circuit 28 | 28 | 5534 | 5535 | 5027 | UINT32 | 10246 | 10247 | Analog Input | 140 | R | NV | kVARh
| kVARh - Circuit 29 | 29 | 5536 | 5537 | 5028 | UINT32 | 10248 | 10249 | Analog Input | 141 | R | NV | kVARh
| kVARh - Circuit 30 | 30 | 5538 | 5539 | 5029 | UINT32 | 10250 | 10251 | Analog Input | 142 | R | NV | kVARh
| kVARh - Circuit 31 | 31 | 5540 | 5541 | 5030 | UINT32 | 10252 | 10253 | Analog Input | 143 | R | NV | kVARh
| kVARh - Circuit 32 | 32 | 5542 | 5543 | 5031 | UINT32 | 10254 | 10255 | Analog Input | 144 | R | NV | kVARh
| kVARh - Circuit 33 | 33 | 5544 | 5545 | 5032 | UINT32 | 10256 | 10257 | Analog Input | 145 | R | NV | kVARh
| kVARh - Circuit 34 | 34 | 5546 | 5547 | 5033 | UINT32 | 10258 | 10259 | Analog Input | 146 | R | NV | kVARh
| kVARh - Circuit 35 | 35 | 5548 | 5549 | 5034 | UINT32 | 10260 | 10261 | Analog Input | 147 | R | NV | kVARh
| kVARh - Circuit 36 | 36 | 5550 | 5551 | 5035 | UINT32 | 10262 | 10263 | Analog Input | 148 | R | NV | kVARh
| kVARh - Circuit 37 | 37 | 5552 | 5553 | 5036 | UINT32 | 10264 | 10265 | Analog Input | 149 | R | NV | kVARh
| kVARh - Circuit 38 | 38 | 5554 | 5555 | 5037 | UINT32 | 10266 | 10267 | Analog Input | 150 | R | NV | kVARh
| kVARh - Circuit 39 | 39 | 5556 | 5557 | 5038 | UINT32 | 10268 | 10269 | Analog Input | 151 | R | NV | kVARh
| kVARh - Circuit 40 | 40 | 5558 | 5559 | 5039 | UINT32 | 10270 | 10271 | Analog Input | 152 | R | NV | kVARh
| kVARh - Circuit 41 | 41 | 5560 | 5561 | 5040 | UINT32 | 10272 | 10273 | Analog Input | 153 | R | NV | kVARh
| kVARh - Circuit 42 | 42 | 5562 | 5563 | 5041 | UINT32 | 10274 | 10275 | Analog Input | 154 | R | NV | kVARh
| kVARh - Circuit 43 | 43 | 5564 | 5565 | 5042 | UINT32 | 10276 | 10277 | Analog Input | 155 | R | NV | kVARh
| kVARh - Circuit 44 | 44 | 5566 | 5567 | 5043 | UINT32 | 10278 | 10279 | Analog Input | 156 | R | NV | kVARh
| kVARh - Circuit 45 | 45 | 5568 | 5569 | 5044 | UINT32 | 10280 | 10281 | Analog Input | 157 | R | NV | kVARh
| kVARh - Circuit 46 | 46 | 5570 | 5571 | 5045 | UINT32 | 10282 | 10283 | Analog Input | 158 | R | NV | kVARh
| kVARh - Circuit 47 | 47 | 5572 | 5573 | 5046 | UINT32 | 10284 | 10285 | Analog Input | 159 | R | NV | kVARh
| kVARh - Circuit 48 | 48 | 5574 | 5575 | 5047 | UINT32 | 10286 | 10287 | Analog Input | 160 | R | NV | kVARh
| kVARh - Circuit 49 | 49 | 5576 | 5577 | 5048 | UINT32 | 10288 | 10289 | Analog Input | 161 | R | NV | kVARh
| kVARh - Circuit 50 | 50 | 5578 | 5579 | 5049 | UINT32 | 10290 | 10291 | Analog Input | 162 | R | NV | kVARh
| kVARh - Circuit 51 | 51 | 5580 | 5581 | 5050 | UINT32 | 10292 | 10293 | Analog Input | 163 | R | NV | kVARh
| kVARh - Circuit 52 | 52 | 5582 | 5583 | 5051 | UINT32 | 10294 | 10295 | Analog Input | 164 | R | NV | kVARh
| kVARh - Circuit 53 | 53 | 5584 | 5585 | 5052 | UINT32 | 10296 | 10297 | Analog Input | 165 | R | NV | kVARh
| kVARh - Circuit 54 | 54 | 5586 | 5587 | 5053 | UINT32 | 10298 | 10299 | Analog Input | 166 | R | NV | kVARh
| kVARh - Circuit 55 | 55 | 5588 | 5589 | 5054 | UINT32 | 10300 | 10301 | Analog Input | 167 | R | NV | kVARh
| kVARh - Circuit 56 | 56 | 5590 | 5591 | 5055 | UINT32 | 10302 | 10303 | Analog Input | 168 | R | NV | kVARh
| kVARh - Circuit 57 | 57 | 5592 | 5593 | 5056 | UINT32 | 10304 | 10305 | Analog Input | 169 | R | NV | kVARh
| kVARh - Circuit 58 | 58 | 5594 | 5595 | 5057 | UINT32 | 10306 | 10307 | Analog Input | 170 | R | NV | kVARh
| kVARh - Circuit 59 | 59 | 5596 | 5597 | 5058 | UINT32 | 10308 | 10309 | Analog Input | 171 | R | NV | kVARh
| kVARh - Circuit 60 | 60 | 5598 | 5599 | 5059 | UINT32 | 10310 | 10311 | Analog Input | 172 | R | NV | kVARh
| kVARh - Circuit 61 | 61 | 5600 | 5601 | 5060 | UINT32 | 10312 | 10313 | Analog Input | 173 | R | NV | kVARh
| kVARh - Circuit 62 | 62 | 5602 | 5603 | 5061 | UINT32 | 10314 | 10315 | Analog Input | 174 | R | NV | kVARh
| kVARh - Circuit 63 | 63 | 5604 | 5605 | 5062 | UINT32 | 10316 | 10317 | Analog Input | 175 | R | NV | kVARh
| kVARh - Circuit 64 | 64 | 5606 | 5607 | 5063 | UINT32 | 10318 | 10319 | Analog Input | 176 | R | NV | kVARh
| kVARh - Circuit 65 | 65 | 5608 | 5609 | 5064 | UINT32 | 10320 | 10321 | Analog Input | 177 | R | NV | kVARh
| kVARh - Circuit 66 | 66 | 5610 | 5611 | 5065 | UINT32 | 10322 | 10323 | Analog Input | 178 | R | NV | kVARh
| kVARh - Circuit 67 | 67 | 5612 | 5613 | 5066 | UINT32 | 10324 | 10325 | Analog Input | 179 | R | NV | kVARh
| kVARh - Circuit 68 | 68 | 5614 | 5615 | 5067 | UINT32 | 10326 | 10327 | Analog Input | 180 | R | NV | kVARh
| kVARh - Circuit 69 | 69 | 5616 | 5617 | 5068 | UINT32 | 10328 | 10329 | Analog Input | 181 | R | NV | kVARh
| kVARh - Circuit 70 | 70 | 5618 | 5619 | 5069 | UINT32 | 10330 | 10331 | Analog Input | 182 | R | NV | kVARh
| kVARh - Circuit 71 | 71 | 5620 | 5621 | 5070 | UINT32 | 10332 | 10333 | Analog Input | 183 | R | NV | kVARh
| kVARh - Circuit 72 | 72 | 5622 | 5623 | 5071 | UINT32 | 10334 | 10335 | Analog Input | 184 | R | NV | kVARh
| kVARh - Circuit 73 | 73 | 5624 | 5625 | 5072 | UINT32 | 10336 | 10337 | Analog Input | 185 | R | NV | kVARh
| kVARh - Circuit 74 | 74 | 5626 | 5627 | 5073 | UINT32 | 10338 | 10339 | Analog Input | 186 | R | NV | kVARh
| kVARh - Circuit 75 | 75 | 5628 | 5629 | 5074 | UINT32 | 10340 | 10341 | Analog Input | 187 | R | NV | kVARh
| kVARh - Circuit 76 | 76 | 5630 | 5631 | 5075 | UINT32 | 10342 | 10343 | Analog Input | 188 | R | NV | kVARh
| kVARh - Circuit 77 | 77 | 5632 | 5633 | 5076 | UINT32 | 10344 | 10345 | Analog Input | 189 | R | NV | kVARh
| kVARh - Circuit 78 | 78 | 5634 | 5635 | 5077 | UINT32 | 10346 | 10347 | Analog Input | 190 | R | NV | kVARh
| kVARh - Circuit 79 | 79 | 5636 | 5637 | 5078 | UINT32 | 10348 | 10349 | Analog Input | 191 | R | NV | kVARh
| kVARh - Circuit 80 | 80 | 5638 | 5639 | 5079 | UINT32 | 10350 | 10351 | Analog Input | 192 | R | NV | kVARh
| kVARh - Circuit 81 | 81 | 5640 | 5641 | 5080 | UINT32 | 10352 | 10353 | Analog Input | 193 | R | NV | kVARh
| kVARh - Circuit 82 | 82 | 5642 | 5643 | 5081 | UINT32 | 10354 | 10355 | Analog Input | 194 | R | NV | kVARh
| kVARh - Circuit 83 | 83 | 5644 | 5645 | 5082 | UINT32 | 10356 | 10357 | Analog Input | 195 | R | NV | kVARh
| kVARh - Circuit 84 | 84 | 5646 | 5647 | 5083 | UINT32 | 10358 | 10359 | Analog Input | 196 | R | NV | kVARh
| kVARh - Circuit 85 | 85 | 5648 | 5649 | 5084 | UINT32 | 10360 | 10361 | Analog Input | 197 | R | NV | kVARh
| kVARh - Circuit 86 | 86 | 5650 | 5651 | 5085 | UINT32 | 10362 | 10363 | Analog Input | 198 | R | NV | kVARh
| kVARh - Circuit 87 | 87 | 5652 | 5653 | 5086 | UINT32 | 10364 | 10365 | Analog Input | 199 | R | NV | kVARh
| kVARh - Circuit 88 | 88 | 5654 | 5655 | 5087 | UINT32 | 10366 | 10367 | Analog Input | 200 | R | NV | kVARh
| kVARh - Circuit 89 | 89 | 5656 | 5657 | 5088 | UINT32 | 10368 | 10369 | Analog Input | 201 | R | NV | kVARh
| kVARh - Circuit 90 | 90 | 5658 | 5659 | 5089 | UINT32 | 10370 | 10371 | Analog Input | 202 | R | NV | kVARh
| kVARh - Circuit 91 | 91 | 5660 | 5661 | 5090 | UINT32 | 10372 | 10373 | Analog Input | 203 | R | NV | kVARh
| kVARh - Circuit 92 | 92 | 5662 | 5663 | 5091 | UINT32 | 10374 | 10375 | Analog Input | 204 | R | NV | kVARh
| kVARh - Circuit 93 | 93 | 5664 | 5665 | 5092 | UINT32 | 10376 | 10377 | Analog Input | 205 | R | NV | kVARh
| kVARh - Circuit 94 | 94 | 5666 | 5667 | 5093 | UINT32 | 10378 | 10379 | Analog Input | 206 | R | NV | kVARh
| kVARh - Circuit 95 | 95 | 5668 | 5669 | 5094 | UINT32 | 10380 | 10381 | Analog Input | 207 | R | NV | kVARh
| kVARh - Circuit 96 | 96 | 5670 | 5671 | 5095 | UINT32 | 10382 | 10383 | Analog Input | 208 | R | NV | kVARh
| kVAh |  | 5672 | 5863 | Energy | UINT32 | 10384 | 10575 | Analog Input | 209 - 304 | R | NV | kVAh
| kVAh - Circuit 1 | 1 | 5672 | 5673 | 5000 | UINT32 | 10384 | 10385 | Analog Input | 209 | R | NV | kVAh
| kVAh - Circuit 2 | 2 | 5674 | 5675 | 5001 | UINT32 | 10386 | 10387 | Analog Input | 210 | R | NV | kVAh
| kVAh - Circuit 3 | 3 | 5676 | 5677 | 5002 | UINT32 | 10388 | 10389 | Analog Input | 211 | R | NV | kVAh
| kVAh - Circuit 4 | 4 | 5678 | 5679 | 5003 | UINT32 | 10390 | 10391 | Analog Input | 212 | R | NV | kVAh
| kVAh - Circuit 5 | 5 | 5680 | 5681 | 5004 | UINT32 | 10392 | 10393 | Analog Input | 213 | R | NV | kVAh
| kVAh - Circuit 6 | 6 | 5682 | 5683 | 5005 | UINT32 | 10394 | 10395 | Analog Input | 214 | R | NV | kVAh
| kVAh - Circuit 7 | 7 | 5684 | 5685 | 5006 | UINT32 | 10396 | 10397 | Analog Input | 215 | R | NV | kVAh
| kVAh - Circuit 8 | 8 | 5686 | 5687 | 5007 | UINT32 | 10398 | 10399 | Analog Input | 216 | R | NV | kVAh
| kVAh - Circuit 9 | 9 | 5688 | 5689 | 5008 | UINT32 | 10400 | 10401 | Analog Input | 217 | R | NV | kVAh
| kVAh - Circuit 10 | 10 | 5690 | 5691 | 5009 | UINT32 | 10402 | 10403 | Analog Input | 218 | R | NV | kVAh
| kVAh - Circuit 11 | 11 | 5692 | 5693 | 5010 | UINT32 | 10404 | 10405 | Analog Input | 219 | R | NV | kVAh
| kVAh - Circuit 12 | 12 | 5694 | 5695 | 5011 | UINT32 | 10406 | 10407 | Analog Input | 220 | R | NV | kVAh
| kVAh - Circuit 13 | 13 | 5696 | 5697 | 5012 | UINT32 | 10408 | 10409 | Analog Input | 221 | R | NV | kVAh
| kVAh - Circuit 14 | 14 | 5698 | 5699 | 5013 | UINT32 | 10410 | 10411 | Analog Input | 222 | R | NV | kVAh
| kVAh - Circuit 15 | 15 | 5700 | 5701 | 5014 | UINT32 | 10412 | 10413 | Analog Input | 223 | R | NV | kVAh
| kVAh - Circuit 16 | 16 | 5702 | 5703 | 5015 | UINT32 | 10414 | 10415 | Analog Input | 224 | R | NV | kVAh
| kVAh - Circuit 17 | 17 | 5704 | 5705 | 5016 | UINT32 | 10416 | 10417 | Analog Input | 225 | R | NV | kVAh
| kVAh - Circuit 18 | 18 | 5706 | 5707 | 5017 | UINT32 | 10418 | 10419 | Analog Input | 226 | R | NV | kVAh
| kVAh - Circuit 19 | 19 | 5708 | 5709 | 5018 | UINT32 | 10420 | 10421 | Analog Input | 227 | R | NV | kVAh
| kVAh - Circuit 20 | 20 | 5710 | 5711 | 5019 | UINT32 | 10422 | 10423 | Analog Input | 228 | R | NV | kVAh
| kVAh - Circuit 21 | 21 | 5712 | 5713 | 5020 | UINT32 | 10424 | 10425 | Analog Input | 229 | R | NV | kVAh
| kVAh - Circuit 22 | 22 | 5714 | 5715 | 5021 | UINT32 | 10426 | 10427 | Analog Input | 230 | R | NV | kVAh
| kVAh - Circuit 23 | 23 | 5716 | 5717 | 5022 | UINT32 | 10428 | 10429 | Analog Input | 231 | R | NV | kVAh
| kVAh - Circuit 24 | 24 | 5718 | 5719 | 5023 | UINT32 | 10430 | 10431 | Analog Input | 232 | R | NV | kVAh
| kVAh - Circuit 25 | 25 | 5720 | 5721 | 5024 | UINT32 | 10432 | 10433 | Analog Input | 233 | R | NV | kVAh
| kVAh - Circuit 26 | 26 | 5722 | 5723 | 5025 | UINT32 | 10434 | 10435 | Analog Input | 234 | R | NV | kVAh
| kVAh - Circuit 27 | 27 | 5724 | 5725 | 5026 | UINT32 | 10436 | 10437 | Analog Input | 235 | R | NV | kVAh
| kVAh - Circuit 28 | 28 | 5726 | 5727 | 5027 | UINT32 | 10438 | 10439 | Analog Input | 236 | R | NV | kVAh
| kVAh - Circuit 29 | 29 | 5728 | 5729 | 5028 | UINT32 | 10440 | 10441 | Analog Input | 237 | R | NV | kVAh
| kVAh - Circuit 30 | 30 | 5730 | 5731 | 5029 | UINT32 | 10442 | 10443 | Analog Input | 238 | R | NV | kVAh
| kVAh - Circuit 31 | 31 | 5732 | 5733 | 5030 | UINT32 | 10444 | 10445 | Analog Input | 239 | R | NV | kVAh
| kVAh - Circuit 32 | 32 | 5734 | 5735 | 5031 | UINT32 | 10446 | 10447 | Analog Input | 240 | R | NV | kVAh
| kVAh - Circuit 33 | 33 | 5736 | 5737 | 5032 | UINT32 | 10448 | 10449 | Analog Input | 241 | R | NV | kVAh
| kVAh - Circuit 34 | 34 | 5738 | 5739 | 5033 | UINT32 | 10450 | 10451 | Analog Input | 242 | R | NV | kVAh
| kVAh - Circuit 35 | 35 | 5740 | 5741 | 5034 | UINT32 | 10452 | 10453 | Analog Input | 243 | R | NV | kVAh
| kVAh - Circuit 36 | 36 | 5742 | 5743 | 5035 | UINT32 | 10454 | 10455 | Analog Input | 244 | R | NV | kVAh
| kVAh - Circuit 37 | 37 | 5744 | 5745 | 5036 | UINT32 | 10456 | 10457 | Analog Input | 245 | R | NV | kVAh
| kVAh - Circuit 38 | 38 | 5746 | 5747 | 5037 | UINT32 | 10458 | 10459 | Analog Input | 246 | R | NV | kVAh
| kVAh - Circuit 39 | 39 | 5748 | 5749 | 5038 | UINT32 | 10460 | 10461 | Analog Input | 247 | R | NV | kVAh
| kVAh - Circuit 40 | 40 | 5750 | 5751 | 5039 | UINT32 | 10462 | 10463 | Analog Input | 248 | R | NV | kVAh
| kVAh - Circuit 41 | 41 | 5752 | 5753 | 5040 | UINT32 | 10464 | 10465 | Analog Input | 249 | R | NV | kVAh
| kVAh - Circuit 42 | 42 | 5754 | 5755 | 5041 | UINT32 | 10466 | 10467 | Analog Input | 250 | R | NV | kVAh
| kVAh - Circuit 43 | 43 | 5756 | 5757 | 5042 | UINT32 | 10468 | 10469 | Analog Input | 251 | R | NV | kVAh
| kVAh - Circuit 44 | 44 | 5758 | 5759 | 5043 | UINT32 | 10470 | 10471 | Analog Input | 252 | R | NV | kVAh
| kVAh - Circuit 45 | 45 | 5760 | 5761 | 5044 | UINT32 | 10472 | 10473 | Analog Input | 253 | R | NV | kVAh
| kVAh - Circuit 46 | 46 | 5762 | 5763 | 5045 | UINT32 | 10474 | 10475 | Analog Input | 254 | R | NV | kVAh
| kVAh - Circuit 47 | 47 | 5764 | 5765 | 5046 | UINT32 | 10476 | 10477 | Analog Input | 255 | R | NV | kVAh
| kVAh - Circuit 48 | 48 | 5766 | 5767 | 5047 | UINT32 | 10478 | 10479 | Analog Input | 256 | R | NV | kVAh
| kVAh - Circuit 49 | 49 | 5768 | 5769 | 5048 | UINT32 | 10480 | 10481 | Analog Input | 257 | R | NV | kVAh
| kVAh - Circuit 50 | 50 | 5770 | 5771 | 5049 | UINT32 | 10482 | 10483 | Analog Input | 258 | R | NV | kVAh
| kVAh - Circuit 51 | 51 | 5772 | 5773 | 5050 | UINT32 | 10484 | 10485 | Analog Input | 259 | R | NV | kVAh
| kVAh - Circuit 52 | 52 | 5774 | 5775 | 5051 | UINT32 | 10486 | 10487 | Analog Input | 260 | R | NV | kVAh
| kVAh - Circuit 53 | 53 | 5776 | 5777 | 5052 | UINT32 | 10488 | 10489 | Analog Input | 261 | R | NV | kVAh
| kVAh - Circuit 54 | 54 | 5778 | 5779 | 5053 | UINT32 | 10490 | 10491 | Analog Input | 262 | R | NV | kVAh
| kVAh - Circuit 55 | 55 | 5780 | 5781 | 5054 | UINT32 | 10492 | 10493 | Analog Input | 263 | R | NV | kVAh
| kVAh - Circuit 56 | 56 | 5782 | 5783 | 5055 | UINT32 | 10494 | 10495 | Analog Input | 264 | R | NV | kVAh
| kVAh - Circuit 57 | 57 | 5784 | 5785 | 5056 | UINT32 | 10496 | 10497 | Analog Input | 265 | R | NV | kVAh
| kVAh - Circuit 58 | 58 | 5786 | 5787 | 5057 | UINT32 | 10498 | 10499 | Analog Input | 266 | R | NV | kVAh
| kVAh - Circuit 59 | 59 | 5788 | 5789 | 5058 | UINT32 | 10500 | 10501 | Analog Input | 267 | R | NV | kVAh
| kVAh - Circuit 60 | 60 | 5790 | 5791 | 5059 | UINT32 | 10502 | 10503 | Analog Input | 268 | R | NV | kVAh
| kVAh - Circuit 61 | 61 | 5792 | 5793 | 5060 | UINT32 | 10504 | 10505 | Analog Input | 269 | R | NV | kVAh
| kVAh - Circuit 62 | 62 | 5794 | 5795 | 5061 | UINT32 | 10506 | 10507 | Analog Input | 270 | R | NV | kVAh
| kVAh - Circuit 63 | 63 | 5796 | 5797 | 5062 | UINT32 | 10508 | 10509 | Analog Input | 271 | R | NV | kVAh
| kVAh - Circuit 64 | 64 | 5798 | 5799 | 5063 | UINT32 | 10510 | 10511 | Analog Input | 272 | R | NV | kVAh
| kVAh - Circuit 65 | 65 | 5800 | 5801 | 5064 | UINT32 | 10512 | 10513 | Analog Input | 273 | R | NV | kVAh
| kVAh - Circuit 66 | 66 | 5802 | 5803 | 5065 | UINT32 | 10514 | 10515 | Analog Input | 274 | R | NV | kVAh
| kVAh - Circuit 67 | 67 | 5804 | 5805 | 5066 | UINT32 | 10516 | 10517 | Analog Input | 275 | R | NV | kVAh
| kVAh - Circuit 68 | 68 | 5806 | 5807 | 5067 | UINT32 | 10518 | 10519 | Analog Input | 276 | R | NV | kVAh
| kVAh - Circuit 69 | 69 | 5808 | 5809 | 5068 | UINT32 | 10520 | 10521 | Analog Input | 277 | R | NV | kVAh
| kVAh - Circuit 70 | 70 | 5810 | 5811 | 5069 | UINT32 | 10522 | 10523 | Analog Input | 278 | R | NV | kVAh
| kVAh - Circuit 71 | 71 | 5812 | 5813 | 5070 | UINT32 | 10524 | 10525 | Analog Input | 279 | R | NV | kVAh
| kVAh - Circuit 72 | 72 | 5814 | 5815 | 5071 | UINT32 | 10526 | 10527 | Analog Input | 280 | R | NV | kVAh
| kVAh - Circuit 73 | 73 | 5816 | 5817 | 5072 | UINT32 | 10528 | 10529 | Analog Input | 281 | R | NV | kVAh
| kVAh - Circuit 74 | 74 | 5818 | 5819 | 5073 | UINT32 | 10530 | 10531 | Analog Input | 282 | R | NV | kVAh
| kVAh - Circuit 75 | 75 | 5820 | 5821 | 5074 | UINT32 | 10532 | 10533 | Analog Input | 283 | R | NV | kVAh
| kVAh - Circuit 76 | 76 | 5822 | 5823 | 5075 | UINT32 | 10534 | 10535 | Analog Input | 284 | R | NV | kVAh
| kVAh - Circuit 77 | 77 | 5824 | 5825 | 5076 | UINT32 | 10536 | 10537 | Analog Input | 285 | R | NV | kVAh
| kVAh - Circuit 78 | 78 | 5826 | 5827 | 5077 | UINT32 | 10538 | 10539 | Analog Input | 286 | R | NV | kVAh
| kVAh - Circuit 79 | 79 | 5828 | 5829 | 5078 | UINT32 | 10540 | 10541 | Analog Input | 287 | R | NV | kVAh
| kVAh - Circuit 80 | 80 | 5830 | 5831 | 5079 | UINT32 | 10542 | 10543 | Analog Input | 288 | R | NV | kVAh
| kVAh - Circuit 81 | 81 | 5832 | 5833 | 5080 | UINT32 | 10544 | 10545 | Analog Input | 289 | R | NV | kVAh
| kVAh - Circuit 82 | 82 | 5834 | 5835 | 5081 | UINT32 | 10546 | 10547 | Analog Input | 290 | R | NV | kVAh
| kVAh - Circuit 83 | 83 | 5836 | 5837 | 5082 | UINT32 | 10548 | 10549 | Analog Input | 291 | R | NV | kVAh
| kVAh - Circuit 84 | 84 | 5838 | 5839 | 5083 | UINT32 | 10550 | 10551 | Analog Input | 292 | R | NV | kVAh
| kVAh - Circuit 85 | 85 | 5840 | 5841 | 5084 | UINT32 | 10552 | 10553 | Analog Input | 293 | R | NV | kVAh
| kVAh - Circuit 86 | 86 | 5842 | 5843 | 5085 | UINT32 | 10554 | 10555 | Analog Input | 294 | R | NV | kVAh
| kVAh - Circuit 87 | 87 | 5844 | 5845 | 5086 | UINT32 | 10556 | 10557 | Analog Input | 295 | R | NV | kVAh
| kVAh - Circuit 88 | 88 | 5846 | 5847 | 5087 | UINT32 | 10558 | 10559 | Analog Input | 296 | R | NV | kVAh
| kVAh - Circuit 89 | 89 | 5848 | 5849 | 5088 | UINT32 | 10560 | 10561 | Analog Input | 297 | R | NV | kVAh
| kVAh - Circuit 90 | 90 | 5850 | 5851 | 5089 | UINT32 | 10562 | 10563 | Analog Input | 298 | R | NV | kVAh
| kVAh - Circuit 91 | 91 | 5852 | 5853 | 5090 | UINT32 | 10564 | 10565 | Analog Input | 299 | R | NV | kVAh
| kVAh - Circuit 92 | 92 | 5854 | 5855 | 5091 | UINT32 | 10566 | 10567 | Analog Input | 300 | R | NV | kVAh
| kVAh - Circuit 93 | 93 | 5856 | 5857 | 5092 | UINT32 | 10568 | 10569 | Analog Input | 301 | R | NV | kVAh
| kVAh - Circuit 94 | 94 | 5858 | 5859 | 5093 | UINT32 | 10570 | 10571 | Analog Input | 302 | R | NV | kVAh
| kVAh - Circuit 95 | 95 | 5860 | 5861 | 5094 | UINT32 | 10572 | 10573 | Analog Input | 303 | R | NV | kVAh
| kVAh - Circuit 96 | 96 | 5862 | 5863 | 5095 | UINT32 | 10574 | 10575 | Analog Input | 304 | R | NV | kVAh
| kW |  | 5864 | 5959 | Power | UINT16 | 10576 | 10767 | Analog Input | 305 - 400 | R |  | kW
| kW - Circuit 1 | 1 | 5864 |  | 5096 | UINT16 | 10576 | 10577 | Analog Input | 305 | R |  | kW
| kW - Circuit 2 | 2 | 5865 |  | 5097 | UINT16 | 10578 | 10579 | Analog Input | 306 | R |  | kW
| kW - Circuit 3 | 3 | 5866 |  | 5098 | UINT16 | 10580 | 10581 | Analog Input | 307 | R |  | kW
| kW - Circuit 4 | 4 | 5867 |  | 5099 | UINT16 | 10582 | 10583 | Analog Input | 308 | R |  | kW
| kW - Circuit 5 | 5 | 5868 |  | 5100 | UINT16 | 10584 | 10585 | Analog Input | 309 | R |  | kW
| kW - Circuit 6 | 6 | 5869 |  | 5101 | UINT16 | 10586 | 10587 | Analog Input | 310 | R |  | kW
| kW - Circuit 7 | 7 | 5870 |  | 5102 | UINT16 | 10588 | 10589 | Analog Input | 311 | R |  | kW
| kW - Circuit 8 | 8 | 5871 |  | 5103 | UINT16 | 10590 | 10591 | Analog Input | 312 | R |  | kW
| kW - Circuit 9 | 9 | 5872 |  | 5104 | UINT16 | 10592 | 10593 | Analog Input | 313 | R |  | kW
| kW - Circuit 10 | 10 | 5873 |  | 5105 | UINT16 | 10594 | 10595 | Analog Input | 314 | R |  | kW
| kW - Circuit 11 | 11 | 5874 |  | 5106 | UINT16 | 10596 | 10597 | Analog Input | 315 | R |  | kW
| kW - Circuit 12 | 12 | 5875 |  | 5107 | UINT16 | 10598 | 10599 | Analog Input | 316 | R |  | kW
| kW - Circuit 13 | 13 | 5876 |  | 5108 | UINT16 | 10600 | 10601 | Analog Input | 317 | R |  | kW
| kW - Circuit 14 | 14 | 5877 |  | 5109 | UINT16 | 10602 | 10603 | Analog Input | 318 | R |  | kW
| kW - Circuit 15 | 15 | 5878 |  | 5110 | UINT16 | 10604 | 10605 | Analog Input | 319 | R |  | kW
| kW - Circuit 16 | 16 | 5879 |  | 5111 | UINT16 | 10606 | 10607 | Analog Input | 320 | R |  | kW
| kW - Circuit 17 | 17 | 5880 |  | 5112 | UINT16 | 10608 | 10609 | Analog Input | 321 | R |  | kW
| kW - Circuit 18 | 18 | 5881 |  | 5113 | UINT16 | 10610 | 10611 | Analog Input | 322 | R |  | kW
| kW - Circuit 19 | 19 | 5882 |  | 5114 | UINT16 | 10612 | 10613 | Analog Input | 323 | R |  | kW
| kW - Circuit 20 | 20 | 5883 |  | 5115 | UINT16 | 10614 | 10615 | Analog Input | 324 | R |  | kW
| kW - Circuit 21 | 21 | 5884 |  | 5116 | UINT16 | 10616 | 10617 | Analog Input | 325 | R |  | kW
| kW - Circuit 22 | 22 | 5885 |  | 5117 | UINT16 | 10618 | 10619 | Analog Input | 326 | R |  | kW
| kW - Circuit 23 | 23 | 5886 |  | 5118 | UINT16 | 10620 | 10621 | Analog Input | 327 | R |  | kW
| kW - Circuit 24 | 24 | 5887 |  | 5119 | UINT16 | 10622 | 10623 | Analog Input | 328 | R |  | kW
| kW - Circuit 25 | 25 | 5888 |  | 5120 | UINT16 | 10624 | 10625 | Analog Input | 329 | R |  | kW
| kW - Circuit 26 | 26 | 5889 |  | 5121 | UINT16 | 10626 | 10627 | Analog Input | 330 | R |  | kW
| kW - Circuit 27 | 27 | 5890 |  | 5122 | UINT16 | 10628 | 10629 | Analog Input | 331 | R |  | kW
| kW - Circuit 28 | 28 | 5891 |  | 5123 | UINT16 | 10630 | 10631 | Analog Input | 332 | R |  | kW
| kW - Circuit 29 | 29 | 5892 |  | 5124 | UINT16 | 10632 | 10633 | Analog Input | 333 | R |  | kW
| kW - Circuit 30 | 30 | 5893 |  | 5125 | UINT16 | 10634 | 10635 | Analog Input | 334 | R |  | kW
| kW - Circuit 31 | 31 | 5894 |  | 5126 | UINT16 | 10636 | 10637 | Analog Input | 335 | R |  | kW
| kW - Circuit 32 | 32 | 5895 |  | 5127 | UINT16 | 10638 | 10639 | Analog Input | 336 | R |  | kW
| kW - Circuit 33 | 33 | 5896 |  | 5128 | UINT16 | 10640 | 10641 | Analog Input | 337 | R |  | kW
| kW - Circuit 34 | 34 | 5897 |  | 5129 | UINT16 | 10642 | 10643 | Analog Input | 338 | R |  | kW
| kW - Circuit 35 | 35 | 5898 |  | 5130 | UINT16 | 10644 | 10645 | Analog Input | 339 | R |  | kW
| kW - Circuit 36 | 36 | 5899 |  | 5131 | UINT16 | 10646 | 10647 | Analog Input | 340 | R |  | kW
| kW - Circuit 37 | 37 | 5900 |  | 5132 | UINT16 | 10648 | 10649 | Analog Input | 341 | R |  | kW
| kW - Circuit 38 | 38 | 5901 |  | 5133 | UINT16 | 10650 | 10651 | Analog Input | 342 | R |  | kW
| kW - Circuit 39 | 39 | 5902 |  | 5134 | UINT16 | 10652 | 10653 | Analog Input | 343 | R |  | kW
| kW - Circuit 40 | 40 | 5903 |  | 5135 | UINT16 | 10654 | 10655 | Analog Input | 344 | R |  | kW
| kW - Circuit 41 | 41 | 5904 |  | 5136 | UINT16 | 10656 | 10657 | Analog Input | 345 | R |  | kW
| kW - Circuit 42 | 42 | 5905 |  | 5137 | UINT16 | 10658 | 10659 | Analog Input | 346 | R |  | kW
| kW - Circuit 43 | 43 | 5906 |  | 5138 | UINT16 | 10660 | 10661 | Analog Input | 347 | R |  | kW
| kW - Circuit 44 | 44 | 5907 |  | 5139 | UINT16 | 10662 | 10663 | Analog Input | 348 | R |  | kW
| kW - Circuit 45 | 45 | 5908 |  | 5140 | UINT16 | 10664 | 10665 | Analog Input | 349 | R |  | kW
| kW - Circuit 46 | 46 | 5909 |  | 5141 | UINT16 | 10666 | 10667 | Analog Input | 350 | R |  | kW
| kW - Circuit 47 | 47 | 5910 |  | 5142 | UINT16 | 10668 | 10669 | Analog Input | 351 | R |  | kW
| kW - Circuit 48 | 48 | 5911 |  | 5143 | UINT16 | 10670 | 10671 | Analog Input | 352 | R |  | kW
| kW - Circuit 49 | 49 | 5912 |  | 5144 | UINT16 | 10672 | 10673 | Analog Input | 353 | R |  | kW
| kW - Circuit 50 | 50 | 5913 |  | 5145 | UINT16 | 10674 | 10675 | Analog Input | 354 | R |  | kW
| kW - Circuit 51 | 51 | 5914 |  | 5146 | UINT16 | 10676 | 10677 | Analog Input | 355 | R |  | kW
| kW - Circuit 52 | 52 | 5915 |  | 5147 | UINT16 | 10678 | 10679 | Analog Input | 356 | R |  | kW
| kW - Circuit 53 | 53 | 5916 |  | 5148 | UINT16 | 10680 | 10681 | Analog Input | 357 | R |  | kW
| kW - Circuit 54 | 54 | 5917 |  | 5149 | UINT16 | 10682 | 10683 | Analog Input | 358 | R |  | kW
| kW - Circuit 55 | 55 | 5918 |  | 5150 | UINT16 | 10684 | 10685 | Analog Input | 359 | R |  | kW
| kW - Circuit 56 | 56 | 5919 |  | 5151 | UINT16 | 10686 | 10687 | Analog Input | 360 | R |  | kW
| kW - Circuit 57 | 57 | 5920 |  | 5152 | UINT16 | 10688 | 10689 | Analog Input | 361 | R |  | kW
| kW - Circuit 58 | 58 | 5921 |  | 5153 | UINT16 | 10690 | 10691 | Analog Input | 362 | R |  | kW
| kW - Circuit 59 | 59 | 5922 |  | 5154 | UINT16 | 10692 | 10693 | Analog Input | 363 | R |  | kW
| kW - Circuit 60 | 60 | 5923 |  | 5155 | UINT16 | 10694 | 10695 | Analog Input | 364 | R |  | kW
| kW - Circuit 61 | 61 | 5924 |  | 5156 | UINT16 | 10696 | 10697 | Analog Input | 365 | R |  | kW
| kW - Circuit 62 | 62 | 5925 |  | 5157 | UINT16 | 10698 | 10699 | Analog Input | 366 | R |  | kW
| kW - Circuit 63 | 63 | 5926 |  | 5158 | UINT16 | 10700 | 10701 | Analog Input | 367 | R |  | kW
| kW - Circuit 64 | 64 | 5927 |  | 5159 | UINT16 | 10702 | 10703 | Analog Input | 368 | R |  | kW
| kW - Circuit 65 | 65 | 5928 |  | 5160 | UINT16 | 10704 | 10705 | Analog Input | 369 | R |  | kW
| kW - Circuit 66 | 66 | 5929 |  | 5161 | UINT16 | 10706 | 10707 | Analog Input | 370 | R |  | kW
| kW - Circuit 67 | 67 | 5930 |  | 5162 | UINT16 | 10708 | 10709 | Analog Input | 371 | R |  | kW
| kW - Circuit 68 | 68 | 5931 |  | 5163 | UINT16 | 10710 | 10711 | Analog Input | 372 | R |  | kW
| kW - Circuit 69 | 69 | 5932 |  | 5164 | UINT16 | 10712 | 10713 | Analog Input | 373 | R |  | kW
| kW - Circuit 70 | 70 | 5933 |  | 5165 | UINT16 | 10714 | 10715 | Analog Input | 374 | R |  | kW
| kW - Circuit 71 | 71 | 5934 |  | 5166 | UINT16 | 10716 | 10717 | Analog Input | 375 | R |  | kW
| kW - Circuit 72 | 72 | 5935 |  | 5167 | UINT16 | 10718 | 10719 | Analog Input | 376 | R |  | kW
| kW - Circuit 73 | 73 | 5936 |  | 5168 | UINT16 | 10720 | 10721 | Analog Input | 377 | R |  | kW
| kW - Circuit 74 | 74 | 5937 |  | 5169 | UINT16 | 10722 | 10723 | Analog Input | 378 | R |  | kW
| kW - Circuit 75 | 75 | 5938 |  | 5170 | UINT16 | 10724 | 10725 | Analog Input | 379 | R |  | kW
| kW - Circuit 76 | 76 | 5939 |  | 5171 | UINT16 | 10726 | 10727 | Analog Input | 380 | R |  | kW
| kW - Circuit 77 | 77 | 5940 |  | 5172 | UINT16 | 10728 | 10729 | Analog Input | 381 | R |  | kW
| kW - Circuit 78 | 78 | 5941 |  | 5173 | UINT16 | 10730 | 10731 | Analog Input | 382 | R |  | kW
| kW - Circuit 79 | 79 | 5942 |  | 5174 | UINT16 | 10732 | 10733 | Analog Input | 383 | R |  | kW
| kW - Circuit 80 | 80 | 5943 |  | 5175 | UINT16 | 10734 | 10735 | Analog Input | 384 | R |  | kW
| kW - Circuit 81 | 81 | 5944 |  | 5176 | UINT16 | 10736 | 10737 | Analog Input | 385 | R |  | kW
| kW - Circuit 82 | 82 | 5945 |  | 5177 | UINT16 | 10738 | 10739 | Analog Input | 386 | R |  | kW
| kW - Circuit 83 | 83 | 5946 |  | 5178 | UINT16 | 10740 | 10741 | Analog Input | 387 | R |  | kW
| kW - Circuit 84 | 84 | 5947 |  | 5179 | UINT16 | 10742 | 10743 | Analog Input | 388 | R |  | kW
| kW - Circuit 85 | 85 | 5948 |  | 5180 | UINT16 | 10744 | 10745 | Analog Input | 389 | R |  | kW
| kW - Circuit 86 | 86 | 5949 |  | 5181 | UINT16 | 10746 | 10747 | Analog Input | 390 | R |  | kW
| kW - Circuit 87 | 87 | 5950 |  | 5182 | UINT16 | 10748 | 10749 | Analog Input | 391 | R |  | kW
| kW - Circuit 88 | 88 | 5951 |  | 5183 | UINT16 | 10750 | 10751 | Analog Input | 392 | R |  | kW
| kW - Circuit 89 | 89 | 5952 |  | 5184 | UINT16 | 10752 | 10753 | Analog Input | 393 | R |  | kW
| kW - Circuit 90 | 90 | 5953 |  | 5185 | UINT16 | 10754 | 10755 | Analog Input | 394 | R |  | kW
| kW - Circuit 91 | 91 | 5954 |  | 5186 | UINT16 | 10756 | 10757 | Analog Input | 395 | R |  | kW
| kW - Circuit 92 | 92 | 5955 |  | 5187 | UINT16 | 10758 | 10759 | Analog Input | 396 | R |  | kW
| kW - Circuit 93 | 93 | 5956 |  | 5188 | UINT16 | 10760 | 10761 | Analog Input | 397 | R |  | kW
| kW - Circuit 94 | 94 | 5957 |  | 5189 | UINT16 | 10762 | 10763 | Analog Input | 398 | R |  | kW
| kW - Circuit 95 | 95 | 5958 |  | 5190 | UINT16 | 10764 | 10765 | Analog Input | 399 | R |  | kW
| kW - Circuit 96 | 96 | 5959 |  | 5191 | UINT16 | 10766 | 10767 | Analog Input | 400 | R |  | kW
| kVAR |  | 5960 | 6055 | Power | UINT16 | 10768 | 10959 | Analog Input | 401 - 496 | R |  | kVAR
| kVAR - Circuit 1 | 1 | 5960 |  | 5096 | UINT16 | 10768 | 10769 | Analog Input | 401 | R |  | kVAR
| kVAR - Circuit 2 | 2 | 5961 |  | 5097 | UINT16 | 10770 | 10771 | Analog Input | 402 | R |  | kVAR
| kVAR - Circuit 3 | 3 | 5962 |  | 5098 | UINT16 | 10772 | 10773 | Analog Input | 403 | R |  | kVAR
| kVAR - Circuit 4 | 4 | 5963 |  | 5099 | UINT16 | 10774 | 10775 | Analog Input | 404 | R |  | kVAR
| kVAR - Circuit 5 | 5 | 5964 |  | 5100 | UINT16 | 10776 | 10777 | Analog Input | 405 | R |  | kVAR
| kVAR - Circuit 6 | 6 | 5965 |  | 5101 | UINT16 | 10778 | 10779 | Analog Input | 406 | R |  | kVAR
| kVAR - Circuit 7 | 7 | 5966 |  | 5102 | UINT16 | 10780 | 10781 | Analog Input | 407 | R |  | kVAR
| kVAR - Circuit 8 | 8 | 5967 |  | 5103 | UINT16 | 10782 | 10783 | Analog Input | 408 | R |  | kVAR
| kVAR - Circuit 9 | 9 | 5968 |  | 5104 | UINT16 | 10784 | 10785 | Analog Input | 409 | R |  | kVAR
| kVAR - Circuit 10 | 10 | 5969 |  | 5105 | UINT16 | 10786 | 10787 | Analog Input | 410 | R |  | kVAR
| kVAR - Circuit 11 | 11 | 5970 |  | 5106 | UINT16 | 10788 | 10789 | Analog Input | 411 | R |  | kVAR
| kVAR - Circuit 12 | 12 | 5971 |  | 5107 | UINT16 | 10790 | 10791 | Analog Input | 412 | R |  | kVAR
| kVAR - Circuit 13 | 13 | 5972 |  | 5108 | UINT16 | 10792 | 10793 | Analog Input | 413 | R |  | kVAR
| kVAR - Circuit 14 | 14 | 5973 |  | 5109 | UINT16 | 10794 | 10795 | Analog Input | 414 | R |  | kVAR
| kVAR - Circuit 15 | 15 | 5974 |  | 5110 | UINT16 | 10796 | 10797 | Analog Input | 415 | R |  | kVAR
| kVAR - Circuit 16 | 16 | 5975 |  | 5111 | UINT16 | 10798 | 10799 | Analog Input | 416 | R |  | kVAR
| kVAR - Circuit 17 | 17 | 5976 |  | 5112 | UINT16 | 10800 | 10801 | Analog Input | 417 | R |  | kVAR
| kVAR - Circuit 18 | 18 | 5977 |  | 5113 | UINT16 | 10802 | 10803 | Analog Input | 418 | R |  | kVAR
| kVAR - Circuit 19 | 19 | 5978 |  | 5114 | UINT16 | 10804 | 10805 | Analog Input | 419 | R |  | kVAR
| kVAR - Circuit 20 | 20 | 5979 |  | 5115 | UINT16 | 10806 | 10807 | Analog Input | 420 | R |  | kVAR
| kVAR - Circuit 21 | 21 | 5980 |  | 5116 | UINT16 | 10808 | 10809 | Analog Input | 421 | R |  | kVAR
| kVAR - Circuit 22 | 22 | 5981 |  | 5117 | UINT16 | 10810 | 10811 | Analog Input | 422 | R |  | kVAR
| kVAR - Circuit 23 | 23 | 5982 |  | 5118 | UINT16 | 10812 | 10813 | Analog Input | 423 | R |  | kVAR
| kVAR - Circuit 24 | 24 | 5983 |  | 5119 | UINT16 | 10814 | 10815 | Analog Input | 424 | R |  | kVAR
| kVAR - Circuit 25 | 25 | 5984 |  | 5120 | UINT16 | 10816 | 10817 | Analog Input | 425 | R |  | kVAR
| kVAR - Circuit 26 | 26 | 5985 |  | 5121 | UINT16 | 10818 | 10819 | Analog Input | 426 | R |  | kVAR
| kVAR - Circuit 27 | 27 | 5986 |  | 5122 | UINT16 | 10820 | 10821 | Analog Input | 427 | R |  | kVAR
| kVAR - Circuit 28 | 28 | 5987 |  | 5123 | UINT16 | 10822 | 10823 | Analog Input | 428 | R |  | kVAR
| kVAR - Circuit 29 | 29 | 5988 |  | 5124 | UINT16 | 10824 | 10825 | Analog Input | 429 | R |  | kVAR
| kVAR - Circuit 30 | 30 | 5989 |  | 5125 | UINT16 | 10826 | 10827 | Analog Input | 430 | R |  | kVAR
| kVAR - Circuit 31 | 31 | 5990 |  | 5126 | UINT16 | 10828 | 10829 | Analog Input | 431 | R |  | kVAR
| kVAR - Circuit 32 | 32 | 5991 |  | 5127 | UINT16 | 10830 | 10831 | Analog Input | 432 | R |  | kVAR
| kVAR - Circuit 33 | 33 | 5992 |  | 5128 | UINT16 | 10832 | 10833 | Analog Input | 433 | R |  | kVAR
| kVAR - Circuit 34 | 34 | 5993 |  | 5129 | UINT16 | 10834 | 10835 | Analog Input | 434 | R |  | kVAR
| kVAR - Circuit 35 | 35 | 5994 |  | 5130 | UINT16 | 10836 | 10837 | Analog Input | 435 | R |  | kVAR
| kVAR - Circuit 36 | 36 | 5995 |  | 5131 | UINT16 | 10838 | 10839 | Analog Input | 436 | R |  | kVAR
| kVAR - Circuit 37 | 37 | 5996 |  | 5132 | UINT16 | 10840 | 10841 | Analog Input | 437 | R |  | kVAR
| kVAR - Circuit 38 | 38 | 5997 |  | 5133 | UINT16 | 10842 | 10843 | Analog Input | 438 | R |  | kVAR
| kVAR - Circuit 39 | 39 | 5998 |  | 5134 | UINT16 | 10844 | 10845 | Analog Input | 439 | R |  | kVAR
| kVAR - Circuit 40 | 40 | 5999 |  | 5135 | UINT16 | 10846 | 10847 | Analog Input | 440 | R |  | kVAR
| kVAR - Circuit 41 | 41 | 6000 |  | 5136 | UINT16 | 10848 | 10849 | Analog Input | 441 | R |  | kVAR
| kVAR - Circuit 42 | 42 | 6001 |  | 5137 | UINT16 | 10850 | 10851 | Analog Input | 442 | R |  | kVAR
| kVAR - Circuit 43 | 43 | 6002 |  | 5138 | UINT16 | 10852 | 10853 | Analog Input | 443 | R |  | kVAR
| kVAR - Circuit 44 | 44 | 6003 |  | 5139 | UINT16 | 10854 | 10855 | Analog Input | 444 | R |  | kVAR
| kVAR - Circuit 45 | 45 | 6004 |  | 5140 | UINT16 | 10856 | 10857 | Analog Input | 445 | R |  | kVAR
| kVAR - Circuit 46 | 46 | 6005 |  | 5141 | UINT16 | 10858 | 10859 | Analog Input | 446 | R |  | kVAR
| kVAR - Circuit 47 | 47 | 6006 |  | 5142 | UINT16 | 10860 | 10861 | Analog Input | 447 | R |  | kVAR
| kVAR - Circuit 48 | 48 | 6007 |  | 5143 | UINT16 | 10862 | 10863 | Analog Input | 448 | R |  | kVAR
| kVAR - Circuit 49 | 49 | 6008 |  | 5144 | UINT16 | 10864 | 10865 | Analog Input | 449 | R |  | kVAR
| kVAR - Circuit 50 | 50 | 6009 |  | 5145 | UINT16 | 10866 | 10867 | Analog Input | 450 | R |  | kVAR
| kVAR - Circuit 51 | 51 | 6010 |  | 5146 | UINT16 | 10868 | 10869 | Analog Input | 451 | R |  | kVAR
| kVAR - Circuit 52 | 52 | 6011 |  | 5147 | UINT16 | 10870 | 10871 | Analog Input | 452 | R |  | kVAR
| kVAR - Circuit 53 | 53 | 6012 |  | 5148 | UINT16 | 10872 | 10873 | Analog Input | 453 | R |  | kVAR
| kVAR - Circuit 54 | 54 | 6013 |  | 5149 | UINT16 | 10874 | 10875 | Analog Input | 454 | R |  | kVAR
| kVAR - Circuit 55 | 55 | 6014 |  | 5150 | UINT16 | 10876 | 10877 | Analog Input | 455 | R |  | kVAR
| kVAR - Circuit 56 | 56 | 6015 |  | 5151 | UINT16 | 10878 | 10879 | Analog Input | 456 | R |  | kVAR
| kVAR - Circuit 57 | 57 | 6016 |  | 5152 | UINT16 | 10880 | 10881 | Analog Input | 457 | R |  | kVAR
| kVAR - Circuit 58 | 58 | 6017 |  | 5153 | UINT16 | 10882 | 10883 | Analog Input | 458 | R |  | kVAR
| kVAR - Circuit 59 | 59 | 6018 |  | 5154 | UINT16 | 10884 | 10885 | Analog Input | 459 | R |  | kVAR
| kVAR - Circuit 60 | 60 | 6019 |  | 5155 | UINT16 | 10886 | 10887 | Analog Input | 460 | R |  | kVAR
| kVAR - Circuit 61 | 61 | 6020 |  | 5156 | UINT16 | 10888 | 10889 | Analog Input | 461 | R |  | kVAR
| kVAR - Circuit 62 | 62 | 6021 |  | 5157 | UINT16 | 10890 | 10891 | Analog Input | 462 | R |  | kVAR
| kVAR - Circuit 63 | 63 | 6022 |  | 5158 | UINT16 | 10892 | 10893 | Analog Input | 463 | R |  | kVAR
| kVAR - Circuit 64 | 64 | 6023 |  | 5159 | UINT16 | 10894 | 10895 | Analog Input | 464 | R |  | kVAR
| kVAR - Circuit 65 | 65 | 6024 |  | 5160 | UINT16 | 10896 | 10897 | Analog Input | 465 | R |  | kVAR
| kVAR - Circuit 66 | 66 | 6025 |  | 5161 | UINT16 | 10898 | 10899 | Analog Input | 466 | R |  | kVAR
| kVAR - Circuit 67 | 67 | 6026 |  | 5162 | UINT16 | 10900 | 10901 | Analog Input | 467 | R |  | kVAR
| kVAR - Circuit 68 | 68 | 6027 |  | 5163 | UINT16 | 10902 | 10903 | Analog Input | 468 | R |  | kVAR
| kVAR - Circuit 69 | 69 | 6028 |  | 5164 | UINT16 | 10904 | 10905 | Analog Input | 469 | R |  | kVAR
| kVAR - Circuit 70 | 70 | 6029 |  | 5165 | UINT16 | 10906 | 10907 | Analog Input | 470 | R |  | kVAR
| kVAR - Circuit 71 | 71 | 6030 |  | 5166 | UINT16 | 10908 | 10909 | Analog Input | 471 | R |  | kVAR
| kVAR - Circuit 72 | 72 | 6031 |  | 5167 | UINT16 | 10910 | 10911 | Analog Input | 472 | R |  | kVAR
| kVAR - Circuit 73 | 73 | 6032 |  | 5168 | UINT16 | 10912 | 10913 | Analog Input | 473 | R |  | kVAR
| kVAR - Circuit 74 | 74 | 6033 |  | 5169 | UINT16 | 10914 | 10915 | Analog Input | 474 | R |  | kVAR
| kVAR - Circuit 75 | 75 | 6034 |  | 5170 | UINT16 | 10916 | 10917 | Analog Input | 475 | R |  | kVAR
| kVAR - Circuit 76 | 76 | 6035 |  | 5171 | UINT16 | 10918 | 10919 | Analog Input | 476 | R |  | kVAR
| kVAR - Circuit 77 | 77 | 6036 |  | 5172 | UINT16 | 10920 | 10921 | Analog Input | 477 | R |  | kVAR
| kVAR - Circuit 78 | 78 | 6037 |  | 5173 | UINT16 | 10922 | 10923 | Analog Input | 478 | R |  | kVAR
| kVAR - Circuit 79 | 79 | 6038 |  | 5174 | UINT16 | 10924 | 10925 | Analog Input | 479 | R |  | kVAR
| kVAR - Circuit 80 | 80 | 6039 |  | 5175 | UINT16 | 10926 | 10927 | Analog Input | 480 | R |  | kVAR
| kVAR - Circuit 81 | 81 | 6040 |  | 5176 | UINT16 | 10928 | 10929 | Analog Input | 481 | R |  | kVAR
| kVAR - Circuit 82 | 82 | 6041 |  | 5177 | UINT16 | 10930 | 10931 | Analog Input | 482 | R |  | kVAR
| kVAR - Circuit 83 | 83 | 6042 |  | 5178 | UINT16 | 10932 | 10933 | Analog Input | 483 | R |  | kVAR
| kVAR - Circuit 84 | 84 | 6043 |  | 5179 | UINT16 | 10934 | 10935 | Analog Input | 484 | R |  | kVAR
| kVAR - Circuit 85 | 85 | 6044 |  | 5180 | UINT16 | 10936 | 10937 | Analog Input | 485 | R |  | kVAR
| kVAR - Circuit 86 | 86 | 6045 |  | 5181 | UINT16 | 10938 | 10939 | Analog Input | 486 | R |  | kVAR
| kVAR - Circuit 87 | 87 | 6046 |  | 5182 | UINT16 | 10940 | 10941 | Analog Input | 487 | R |  | kVAR
| kVAR - Circuit 88 | 88 | 6047 |  | 5183 | UINT16 | 10942 | 10943 | Analog Input | 488 | R |  | kVAR
| kVAR - Circuit 89 | 89 | 6048 |  | 5184 | UINT16 | 10944 | 10945 | Analog Input | 489 | R |  | kVAR
| kVAR - Circuit 90 | 90 | 6049 |  | 5185 | UINT16 | 10946 | 10947 | Analog Input | 490 | R |  | kVAR
| kVAR - Circuit 91 | 91 | 6050 |  | 5186 | UINT16 | 10948 | 10949 | Analog Input | 491 | R |  | kVAR
| kVAR - Circuit 92 | 92 | 6051 |  | 5187 | UINT16 | 10950 | 10951 | Analog Input | 492 | R |  | kVAR
| kVAR - Circuit 93 | 93 | 6052 |  | 5188 | UINT16 | 10952 | 10953 | Analog Input | 493 | R |  | kVAR
| kVAR - Circuit 94 | 94 | 6053 |  | 5189 | UINT16 | 10954 | 10955 | Analog Input | 494 | R |  | kVAR
| kVAR - Circuit 95 | 95 | 6054 |  | 5190 | UINT16 | 10956 | 10957 | Analog Input | 495 | R |  | kVAR
| kVAR - Circuit 96 | 96 | 6055 |  | 5191 | UINT16 | 10958 | 10959 | Analog Input | 496 | R |  | kVAR
| kVA |  | 6056 | 6151 | Power | UINT16 | 10960 | 11151 | Analog Input | 497 - 592 | R |  | kVA
| kVA - Circuit 1 | 1 | 6056 |  | 5096 | UINT16 | 10960 | 10961 | Analog Input | 497 | R |  | kVA
| kVA - Circuit 2 | 2 | 6057 |  | 5097 | UINT16 | 10962 | 10963 | Analog Input | 498 | R |  | kVA
| kVA - Circuit 3 | 3 | 6058 |  | 5098 | UINT16 | 10964 | 10965 | Analog Input | 499 | R |  | kVA
| kVA - Circuit 4 | 4 | 6059 |  | 5099 | UINT16 | 10966 | 10967 | Analog Input | 500 | R |  | kVA
| kVA - Circuit 5 | 5 | 6060 |  | 5100 | UINT16 | 10968 | 10969 | Analog Input | 501 | R |  | kVA
| kVA - Circuit 6 | 6 | 6061 |  | 5101 | UINT16 | 10970 | 10971 | Analog Input | 502 | R |  | kVA
| kVA - Circuit 7 | 7 | 6062 |  | 5102 | UINT16 | 10972 | 10973 | Analog Input | 503 | R |  | kVA
| kVA - Circuit 8 | 8 | 6063 |  | 5103 | UINT16 | 10974 | 10975 | Analog Input | 504 | R |  | kVA
| kVA - Circuit 9 | 9 | 6064 |  | 5104 | UINT16 | 10976 | 10977 | Analog Input | 505 | R |  | kVA
| kVA - Circuit 10 | 10 | 6065 |  | 5105 | UINT16 | 10978 | 10979 | Analog Input | 506 | R |  | kVA
| kVA - Circuit 11 | 11 | 6066 |  | 5106 | UINT16 | 10980 | 10981 | Analog Input | 507 | R |  | kVA
| kVA - Circuit 12 | 12 | 6067 |  | 5107 | UINT16 | 10982 | 10983 | Analog Input | 508 | R |  | kVA
| kVA - Circuit 13 | 13 | 6068 |  | 5108 | UINT16 | 10984 | 10985 | Analog Input | 509 | R |  | kVA
| kVA - Circuit 14 | 14 | 6069 |  | 5109 | UINT16 | 10986 | 10987 | Analog Input | 510 | R |  | kVA
| kVA - Circuit 15 | 15 | 6070 |  | 5110 | UINT16 | 10988 | 10989 | Analog Input | 511 | R |  | kVA
| kVA - Circuit 16 | 16 | 6071 |  | 5111 | UINT16 | 10990 | 10991 | Analog Input | 512 | R |  | kVA
| kVA - Circuit 17 | 17 | 6072 |  | 5112 | UINT16 | 10992 | 10993 | Analog Input | 513 | R |  | kVA
| kVA - Circuit 18 | 18 | 6073 |  | 5113 | UINT16 | 10994 | 10995 | Analog Input | 514 | R |  | kVA
| kVA - Circuit 19 | 19 | 6074 |  | 5114 | UINT16 | 10996 | 10997 | Analog Input | 515 | R |  | kVA
| kVA - Circuit 20 | 20 | 6075 |  | 5115 | UINT16 | 10998 | 10999 | Analog Input | 516 | R |  | kVA
| kVA - Circuit 21 | 21 | 6076 |  | 5116 | UINT16 | 11000 | 11001 | Analog Input | 517 | R |  | kVA
| kVA - Circuit 22 | 22 | 6077 |  | 5117 | UINT16 | 11002 | 11003 | Analog Input | 518 | R |  | kVA
| kVA - Circuit 23 | 23 | 6078 |  | 5118 | UINT16 | 11004 | 11005 | Analog Input | 519 | R |  | kVA
| kVA - Circuit 24 | 24 | 6079 |  | 5119 | UINT16 | 11006 | 11007 | Analog Input | 520 | R |  | kVA
| kVA - Circuit 25 | 25 | 6080 |  | 5120 | UINT16 | 11008 | 11009 | Analog Input | 521 | R |  | kVA
| kVA - Circuit 26 | 26 | 6081 |  | 5121 | UINT16 | 11010 | 11011 | Analog Input | 522 | R |  | kVA
| kVA - Circuit 27 | 27 | 6082 |  | 5122 | UINT16 | 11012 | 11013 | Analog Input | 523 | R |  | kVA
| kVA - Circuit 28 | 28 | 6083 |  | 5123 | UINT16 | 11014 | 11015 | Analog Input | 524 | R |  | kVA
| kVA - Circuit 29 | 29 | 6084 |  | 5124 | UINT16 | 11016 | 11017 | Analog Input | 525 | R |  | kVA
| kVA - Circuit 30 | 30 | 6085 |  | 5125 | UINT16 | 11018 | 11019 | Analog Input | 526 | R |  | kVA
| kVA - Circuit 31 | 31 | 6086 |  | 5126 | UINT16 | 11020 | 11021 | Analog Input | 527 | R |  | kVA
| kVA - Circuit 32 | 32 | 6087 |  | 5127 | UINT16 | 11022 | 11023 | Analog Input | 528 | R |  | kVA
| kVA - Circuit 33 | 33 | 6088 |  | 5128 | UINT16 | 11024 | 11025 | Analog Input | 529 | R |  | kVA
| kVA - Circuit 34 | 34 | 6089 |  | 5129 | UINT16 | 11026 | 11027 | Analog Input | 530 | R |  | kVA
| kVA - Circuit 35 | 35 | 6090 |  | 5130 | UINT16 | 11028 | 11029 | Analog Input | 531 | R |  | kVA
| kVA - Circuit 36 | 36 | 6091 |  | 5131 | UINT16 | 11030 | 11031 | Analog Input | 532 | R |  | kVA
| kVA - Circuit 37 | 37 | 6092 |  | 5132 | UINT16 | 11032 | 11033 | Analog Input | 533 | R |  | kVA
| kVA - Circuit 38 | 38 | 6093 |  | 5133 | UINT16 | 11034 | 11035 | Analog Input | 534 | R |  | kVA
| kVA - Circuit 39 | 39 | 6094 |  | 5134 | UINT16 | 11036 | 11037 | Analog Input | 535 | R |  | kVA
| kVA - Circuit 40 | 40 | 6095 |  | 5135 | UINT16 | 11038 | 11039 | Analog Input | 536 | R |  | kVA
| kVA - Circuit 41 | 41 | 6096 |  | 5136 | UINT16 | 11040 | 11041 | Analog Input | 537 | R |  | kVA
| kVA - Circuit 42 | 42 | 6097 |  | 5137 | UINT16 | 11042 | 11043 | Analog Input | 538 | R |  | kVA
| kVA - Circuit 43 | 43 | 6098 |  | 5138 | UINT16 | 11044 | 11045 | Analog Input | 539 | R |  | kVA
| kVA - Circuit 44 | 44 | 6099 |  | 5139 | UINT16 | 11046 | 11047 | Analog Input | 540 | R |  | kVA
| kVA - Circuit 45 | 45 | 6100 |  | 5140 | UINT16 | 11048 | 11049 | Analog Input | 541 | R |  | kVA
| kVA - Circuit 46 | 46 | 6101 |  | 5141 | UINT16 | 11050 | 11051 | Analog Input | 542 | R |  | kVA
| kVA - Circuit 47 | 47 | 6102 |  | 5142 | UINT16 | 11052 | 11053 | Analog Input | 543 | R |  | kVA
| kVA - Circuit 48 | 48 | 6103 |  | 5143 | UINT16 | 11054 | 11055 | Analog Input | 544 | R |  | kVA
| kVA - Circuit 49 | 49 | 6104 |  | 5144 | UINT16 | 11056 | 11057 | Analog Input | 545 | R |  | kVA
| kVA - Circuit 50 | 50 | 6105 |  | 5145 | UINT16 | 11058 | 11059 | Analog Input | 546 | R |  | kVA
| kVA - Circuit 51 | 51 | 6106 |  | 5146 | UINT16 | 11060 | 11061 | Analog Input | 547 | R |  | kVA
| kVA - Circuit 52 | 52 | 6107 |  | 5147 | UINT16 | 11062 | 11063 | Analog Input | 548 | R |  | kVA
| kVA - Circuit 53 | 53 | 6108 |  | 5148 | UINT16 | 11064 | 11065 | Analog Input | 549 | R |  | kVA
| kVA - Circuit 54 | 54 | 6109 |  | 5149 | UINT16 | 11066 | 11067 | Analog Input | 550 | R |  | kVA
| kVA - Circuit 55 | 55 | 6110 |  | 5150 | UINT16 | 11068 | 11069 | Analog Input | 551 | R |  | kVA
| kVA - Circuit 56 | 56 | 6111 |  | 5151 | UINT16 | 11070 | 11071 | Analog Input | 552 | R |  | kVA
| kVA - Circuit 57 | 57 | 6112 |  | 5152 | UINT16 | 11072 | 11073 | Analog Input | 553 | R |  | kVA
| kVA - Circuit 58 | 58 | 6113 |  | 5153 | UINT16 | 11074 | 11075 | Analog Input | 554 | R |  | kVA
| kVA - Circuit 59 | 59 | 6114 |  | 5154 | UINT16 | 11076 | 11077 | Analog Input | 555 | R |  | kVA
| kVA - Circuit 60 | 60 | 6115 |  | 5155 | UINT16 | 11078 | 11079 | Analog Input | 556 | R |  | kVA
| kVA - Circuit 61 | 61 | 6116 |  | 5156 | UINT16 | 11080 | 11081 | Analog Input | 557 | R |  | kVA
| kVA - Circuit 62 | 62 | 6117 |  | 5157 | UINT16 | 11082 | 11083 | Analog Input | 558 | R |  | kVA
| kVA - Circuit 63 | 63 | 6118 |  | 5158 | UINT16 | 11084 | 11085 | Analog Input | 559 | R |  | kVA
| kVA - Circuit 64 | 64 | 6119 |  | 5159 | UINT16 | 11086 | 11087 | Analog Input | 560 | R |  | kVA
| kVA - Circuit 65 | 65 | 6120 |  | 5160 | UINT16 | 11088 | 11089 | Analog Input | 561 | R |  | kVA
| kVA - Circuit 66 | 66 | 6121 |  | 5161 | UINT16 | 11090 | 11091 | Analog Input | 562 | R |  | kVA
| kVA - Circuit 67 | 67 | 6122 |  | 5162 | UINT16 | 11092 | 11093 | Analog Input | 563 | R |  | kVA
| kVA - Circuit 68 | 68 | 6123 |  | 5163 | UINT16 | 11094 | 11095 | Analog Input | 564 | R |  | kVA
| kVA - Circuit 69 | 69 | 6124 |  | 5164 | UINT16 | 11096 | 11097 | Analog Input | 565 | R |  | kVA
| kVA - Circuit 70 | 70 | 6125 |  | 5165 | UINT16 | 11098 | 11099 | Analog Input | 566 | R |  | kVA
| kVA - Circuit 71 | 71 | 6126 |  | 5166 | UINT16 | 11100 | 11101 | Analog Input | 567 | R |  | kVA
| kVA - Circuit 72 | 72 | 6127 |  | 5167 | UINT16 | 11102 | 11103 | Analog Input | 568 | R |  | kVA
| kVA - Circuit 73 | 73 | 6128 |  | 5168 | UINT16 | 11104 | 11105 | Analog Input | 569 | R |  | kVA
| kVA - Circuit 74 | 74 | 6129 |  | 5169 | UINT16 | 11106 | 11107 | Analog Input | 570 | R |  | kVA
| kVA - Circuit 75 | 75 | 6130 |  | 5170 | UINT16 | 11108 | 11109 | Analog Input | 571 | R |  | kVA
| kVA - Circuit 76 | 76 | 6131 |  | 5171 | UINT16 | 11110 | 11111 | Analog Input | 572 | R |  | kVA
| kVA - Circuit 77 | 77 | 6132 |  | 5172 | UINT16 | 11112 | 11113 | Analog Input | 573 | R |  | kVA
| kVA - Circuit 78 | 78 | 6133 |  | 5173 | UINT16 | 11114 | 11115 | Analog Input | 574 | R |  | kVA
| kVA - Circuit 79 | 79 | 6134 |  | 5174 | UINT16 | 11116 | 11117 | Analog Input | 575 | R |  | kVA
| kVA - Circuit 80 | 80 | 6135 |  | 5175 | UINT16 | 11118 | 11119 | Analog Input | 576 | R |  | kVA
| kVA - Circuit 81 | 81 | 6136 |  | 5176 | UINT16 | 11120 | 11121 | Analog Input | 577 | R |  | kVA
| kVA - Circuit 82 | 82 | 6137 |  | 5177 | UINT16 | 11122 | 11123 | Analog Input | 578 | R |  | kVA
| kVA - Circuit 83 | 83 | 6138 |  | 5178 | UINT16 | 11124 | 11125 | Analog Input | 579 | R |  | kVA
| kVA - Circuit 84 | 84 | 6139 |  | 5179 | UINT16 | 11126 | 11127 | Analog Input | 580 | R |  | kVA
| kVA - Circuit 85 | 85 | 6140 |  | 5180 | UINT16 | 11128 | 11129 | Analog Input | 581 | R |  | kVA
| kVA - Circuit 86 | 86 | 6141 |  | 5181 | UINT16 | 11130 | 11131 | Analog Input | 582 | R |  | kVA
| kVA - Circuit 87 | 87 | 6142 |  | 5182 | UINT16 | 11132 | 11133 | Analog Input | 583 | R |  | kVA
| kVA - Circuit 88 | 88 | 6143 |  | 5183 | UINT16 | 11134 | 11135 | Analog Input | 584 | R |  | kVA
| kVA - Circuit 89 | 89 | 6144 |  | 5184 | UINT16 | 11136 | 11137 | Analog Input | 585 | R |  | kVA
| kVA - Circuit 90 | 90 | 6145 |  | 5185 | UINT16 | 11138 | 11139 | Analog Input | 586 | R |  | kVA
| kVA - Circuit 91 | 91 | 6146 |  | 5186 | UINT16 | 11140 | 11141 | Analog Input | 587 | R |  | kVA
| kVA - Circuit 92 | 92 | 6147 |  | 5187 | UINT16 | 11142 | 11143 | Analog Input | 588 | R |  | kVA
| kVA - Circuit 93 | 93 | 6148 |  | 5188 | UINT16 | 11144 | 11145 | Analog Input | 589 | R |  | kVA
| kVA - Circuit 94 | 94 | 6149 |  | 5189 | UINT16 | 11146 | 11147 | Analog Input | 590 | R |  | kVA
| kVA - Circuit 95 | 95 | 6150 |  | 5190 | UINT16 | 11148 | 11149 | Analog Input | 591 | R |  | kVA
| kVA - Circuit 96 | 96 | 6151 |  | 5191 | UINT16 | 11150 | 11151 | Analog Input | 592 | R |  | kVA
| Current |  | 6152 | 6247 | Current | UINT16 | 11152 | 11343 | Analog Input | 593 - 688 | R |  | Amps
| Current - Circuit 1 | 1 | 6152 |  | 5192 | UINT16 | 11152 | 11153 | Analog Input | 593 | R |  | Amps
| Current - Circuit 2 | 2 | 6153 |  | 5193 | UINT16 | 11154 | 11155 | Analog Input | 594 | R |  | Amps
| Current - Circuit 3 | 3 | 6154 |  | 5194 | UINT16 | 11156 | 11157 | Analog Input | 595 | R |  | Amps
| Current - Circuit 4 | 4 | 6155 |  | 5195 | UINT16 | 11158 | 11159 | Analog Input | 596 | R |  | Amps
| Current - Circuit 5 | 5 | 6156 |  | 5196 | UINT16 | 11160 | 11161 | Analog Input | 597 | R |  | Amps
| Current - Circuit 6 | 6 | 6157 |  | 5197 | UINT16 | 11162 | 11163 | Analog Input | 598 | R |  | Amps
| Current - Circuit 7 | 7 | 6158 |  | 5198 | UINT16 | 11164 | 11165 | Analog Input | 599 | R |  | Amps
| Current - Circuit 8 | 8 | 6159 |  | 5199 | UINT16 | 11166 | 11167 | Analog Input | 600 | R |  | Amps
| Current - Circuit 9 | 9 | 6160 |  | 5200 | UINT16 | 11168 | 11169 | Analog Input | 601 | R |  | Amps
| Current - Circuit 10 | 10 | 6161 |  | 5201 | UINT16 | 11170 | 11171 | Analog Input | 602 | R |  | Amps
| Current - Circuit 11 | 11 | 6162 |  | 5202 | UINT16 | 11172 | 11173 | Analog Input | 603 | R |  | Amps
| Current - Circuit 12 | 12 | 6163 |  | 5203 | UINT16 | 11174 | 11175 | Analog Input | 604 | R |  | Amps
| Current - Circuit 13 | 13 | 6164 |  | 5204 | UINT16 | 11176 | 11177 | Analog Input | 605 | R |  | Amps
| Current - Circuit 14 | 14 | 6165 |  | 5205 | UINT16 | 11178 | 11179 | Analog Input | 606 | R |  | Amps
| Current - Circuit 15 | 15 | 6166 |  | 5206 | UINT16 | 11180 | 11181 | Analog Input | 607 | R |  | Amps
| Current - Circuit 16 | 16 | 6167 |  | 5207 | UINT16 | 11182 | 11183 | Analog Input | 608 | R |  | Amps
| Current - Circuit 17 | 17 | 6168 |  | 5208 | UINT16 | 11184 | 11185 | Analog Input | 609 | R |  | Amps
| Current - Circuit 18 | 18 | 6169 |  | 5209 | UINT16 | 11186 | 11187 | Analog Input | 610 | R |  | Amps
| Current - Circuit 19 | 19 | 6170 |  | 5210 | UINT16 | 11188 | 11189 | Analog Input | 611 | R |  | Amps
| Current - Circuit 20 | 20 | 6171 |  | 5211 | UINT16 | 11190 | 11191 | Analog Input | 612 | R |  | Amps
| Current - Circuit 21 | 21 | 6172 |  | 5212 | UINT16 | 11192 | 11193 | Analog Input | 613 | R |  | Amps
| Current - Circuit 22 | 22 | 6173 |  | 5213 | UINT16 | 11194 | 11195 | Analog Input | 614 | R |  | Amps
| Current - Circuit 23 | 23 | 6174 |  | 5214 | UINT16 | 11196 | 11197 | Analog Input | 615 | R |  | Amps
| Current - Circuit 24 | 24 | 6175 |  | 5215 | UINT16 | 11198 | 11199 | Analog Input | 616 | R |  | Amps
| Current - Circuit 25 | 25 | 6176 |  | 5216 | UINT16 | 11200 | 11201 | Analog Input | 617 | R |  | Amps
| Current - Circuit 26 | 26 | 6177 |  | 5217 | UINT16 | 11202 | 11203 | Analog Input | 618 | R |  | Amps
| Current - Circuit 27 | 27 | 6178 |  | 5218 | UINT16 | 11204 | 11205 | Analog Input | 619 | R |  | Amps
| Current - Circuit 28 | 28 | 6179 |  | 5219 | UINT16 | 11206 | 11207 | Analog Input | 620 | R |  | Amps
| Current - Circuit 29 | 29 | 6180 |  | 5220 | UINT16 | 11208 | 11209 | Analog Input | 621 | R |  | Amps
| Current - Circuit 30 | 30 | 6181 |  | 5221 | UINT16 | 11210 | 11211 | Analog Input | 622 | R |  | Amps
| Current - Circuit 31 | 31 | 6182 |  | 5222 | UINT16 | 11212 | 11213 | Analog Input | 623 | R |  | Amps
| Current - Circuit 32 | 32 | 6183 |  | 5223 | UINT16 | 11214 | 11215 | Analog Input | 624 | R |  | Amps
| Current - Circuit 33 | 33 | 6184 |  | 5224 | UINT16 | 11216 | 11217 | Analog Input | 625 | R |  | Amps
| Current - Circuit 34 | 34 | 6185 |  | 5225 | UINT16 | 11218 | 11219 | Analog Input | 626 | R |  | Amps
| Current - Circuit 35 | 35 | 6186 |  | 5226 | UINT16 | 11220 | 11221 | Analog Input | 627 | R |  | Amps
| Current - Circuit 36 | 36 | 6187 |  | 5227 | UINT16 | 11222 | 11223 | Analog Input | 628 | R |  | Amps
| Current - Circuit 37 | 37 | 6188 |  | 5228 | UINT16 | 11224 | 11225 | Analog Input | 629 | R |  | Amps
| Current - Circuit 38 | 38 | 6189 |  | 5229 | UINT16 | 11226 | 11227 | Analog Input | 630 | R |  | Amps
| Current - Circuit 39 | 39 | 6190 |  | 5230 | UINT16 | 11228 | 11229 | Analog Input | 631 | R |  | Amps
| Current - Circuit 40 | 40 | 6191 |  | 5231 | UINT16 | 11230 | 11231 | Analog Input | 632 | R |  | Amps
| Current - Circuit 41 | 41 | 6192 |  | 5232 | UINT16 | 11232 | 11233 | Analog Input | 633 | R |  | Amps
| Current - Circuit 42 | 42 | 6193 |  | 5233 | UINT16 | 11234 | 11235 | Analog Input | 634 | R |  | Amps
| Current - Circuit 43 | 43 | 6194 |  | 5234 | UINT16 | 11236 | 11237 | Analog Input | 635 | R |  | Amps
| Current - Circuit 44 | 44 | 6195 |  | 5235 | UINT16 | 11238 | 11239 | Analog Input | 636 | R |  | Amps
| Current - Circuit 45 | 45 | 6196 |  | 5236 | UINT16 | 11240 | 11241 | Analog Input | 637 | R |  | Amps
| Current - Circuit 46 | 46 | 6197 |  | 5237 | UINT16 | 11242 | 11243 | Analog Input | 638 | R |  | Amps
| Current - Circuit 47 | 47 | 6198 |  | 5238 | UINT16 | 11244 | 11245 | Analog Input | 639 | R |  | Amps
| Current - Circuit 48 | 48 | 6199 |  | 5239 | UINT16 | 11246 | 11247 | Analog Input | 640 | R |  | Amps
| Current - Circuit 49 | 49 | 6200 |  | 5240 | UINT16 | 11248 | 11249 | Analog Input | 641 | R |  | Amps
| Current - Circuit 50 | 50 | 6201 |  | 5241 | UINT16 | 11250 | 11251 | Analog Input | 642 | R |  | Amps
| Current - Circuit 51 | 51 | 6202 |  | 5242 | UINT16 | 11252 | 11253 | Analog Input | 643 | R |  | Amps
| Current - Circuit 52 | 52 | 6203 |  | 5243 | UINT16 | 11254 | 11255 | Analog Input | 644 | R |  | Amps
| Current - Circuit 53 | 53 | 6204 |  | 5244 | UINT16 | 11256 | 11257 | Analog Input | 645 | R |  | Amps
| Current - Circuit 54 | 54 | 6205 |  | 5245 | UINT16 | 11258 | 11259 | Analog Input | 646 | R |  | Amps
| Current - Circuit 55 | 55 | 6206 |  | 5246 | UINT16 | 11260 | 11261 | Analog Input | 647 | R |  | Amps
| Current - Circuit 56 | 56 | 6207 |  | 5247 | UINT16 | 11262 | 11263 | Analog Input | 648 | R |  | Amps
| Current - Circuit 57 | 57 | 6208 |  | 5248 | UINT16 | 11264 | 11265 | Analog Input | 649 | R |  | Amps
| Current - Circuit 58 | 58 | 6209 |  | 5249 | UINT16 | 11266 | 11267 | Analog Input | 650 | R |  | Amps
| Current - Circuit 59 | 59 | 6210 |  | 5250 | UINT16 | 11268 | 11269 | Analog Input | 651 | R |  | Amps
| Current - Circuit 60 | 60 | 6211 |  | 5251 | UINT16 | 11270 | 11271 | Analog Input | 652 | R |  | Amps
| Current - Circuit 61 | 61 | 6212 |  | 5252 | UINT16 | 11272 | 11273 | Analog Input | 653 | R |  | Amps
| Current - Circuit 62 | 62 | 6213 |  | 5253 | UINT16 | 11274 | 11275 | Analog Input | 654 | R |  | Amps
| Current - Circuit 63 | 63 | 6214 |  | 5254 | UINT16 | 11276 | 11277 | Analog Input | 655 | R |  | Amps
| Current - Circuit 64 | 64 | 6215 |  | 5255 | UINT16 | 11278 | 11279 | Analog Input | 656 | R |  | Amps
| Current - Circuit 65 | 65 | 6216 |  | 5256 | UINT16 | 11280 | 11281 | Analog Input | 657 | R |  | Amps
| Current - Circuit 66 | 66 | 6217 |  | 5257 | UINT16 | 11282 | 11283 | Analog Input | 658 | R |  | Amps
| Current - Circuit 67 | 67 | 6218 |  | 5258 | UINT16 | 11284 | 11285 | Analog Input | 659 | R |  | Amps
| Current - Circuit 68 | 68 | 6219 |  | 5259 | UINT16 | 11286 | 11287 | Analog Input | 660 | R |  | Amps
| Current - Circuit 69 | 69 | 6220 |  | 5260 | UINT16 | 11288 | 11289 | Analog Input | 661 | R |  | Amps
| Current - Circuit 70 | 70 | 6221 |  | 5261 | UINT16 | 11290 | 11291 | Analog Input | 662 | R |  | Amps
| Current - Circuit 71 | 71 | 6222 |  | 5262 | UINT16 | 11292 | 11293 | Analog Input | 663 | R |  | Amps
| Current - Circuit 72 | 72 | 6223 |  | 5263 | UINT16 | 11294 | 11295 | Analog Input | 664 | R |  | Amps
| Current - Circuit 73 | 73 | 6224 |  | 5264 | UINT16 | 11296 | 11297 | Analog Input | 665 | R |  | Amps
| Current - Circuit 74 | 74 | 6225 |  | 5265 | UINT16 | 11298 | 11299 | Analog Input | 666 | R |  | Amps
| Current - Circuit 75 | 75 | 6226 |  | 5266 | UINT16 | 11300 | 11301 | Analog Input | 667 | R |  | Amps
| Current - Circuit 76 | 76 | 6227 |  | 5267 | UINT16 | 11302 | 11303 | Analog Input | 668 | R |  | Amps
| Current - Circuit 77 | 77 | 6228 |  | 5268 | UINT16 | 11304 | 11305 | Analog Input | 669 | R |  | Amps
| Current - Circuit 78 | 78 | 6229 |  | 5269 | UINT16 | 11306 | 11307 | Analog Input | 670 | R |  | Amps
| Current - Circuit 79 | 79 | 6230 |  | 5270 | UINT16 | 11308 | 11309 | Analog Input | 671 | R |  | Amps
| Current - Circuit 80 | 80 | 6231 |  | 5271 | UINT16 | 11310 | 11311 | Analog Input | 672 | R |  | Amps
| Current - Circuit 81 | 81 | 6232 |  | 5272 | UINT16 | 11312 | 11313 | Analog Input | 673 | R |  | Amps
| Current - Circuit 82 | 82 | 6233 |  | 5273 | UINT16 | 11314 | 11315 | Analog Input | 674 | R |  | Amps
| Current - Circuit 83 | 83 | 6234 |  | 5274 | UINT16 | 11316 | 11317 | Analog Input | 675 | R |  | Amps
| Current - Circuit 84 | 84 | 6235 |  | 5275 | UINT16 | 11318 | 11319 | Analog Input | 676 | R |  | Amps
| Current - Circuit 85 | 85 | 6236 |  | 5276 | UINT16 | 11320 | 11321 | Analog Input | 677 | R |  | Amps
| Current - Circuit 86 | 86 | 6237 |  | 5277 | UINT16 | 11322 | 11323 | Analog Input | 678 | R |  | Amps
| Current - Circuit 87 | 87 | 6238 |  | 5278 | UINT16 | 11324 | 11325 | Analog Input | 679 | R |  | Amps
| Current - Circuit 88 | 88 | 6239 |  | 5279 | UINT16 | 11326 | 11327 | Analog Input | 680 | R |  | Amps
| Current - Circuit 89 | 89 | 6240 |  | 5280 | UINT16 | 11328 | 11329 | Analog Input | 681 | R |  | Amps
| Current - Circuit 90 | 90 | 6241 |  | 5281 | UINT16 | 11330 | 11331 | Analog Input | 682 | R |  | Amps
| Current - Circuit 91 | 91 | 6242 |  | 5282 | UINT16 | 11332 | 11333 | Analog Input | 683 | R |  | Amps
| Current - Circuit 92 | 92 | 6243 |  | 5283 | UINT16 | 11334 | 11335 | Analog Input | 684 | R |  | Amps
| Current - Circuit 93 | 93 | 6244 |  | 5284 | UINT16 | 11336 | 11337 | Analog Input | 685 | R |  | Amps
| Current - Circuit 94 | 94 | 6245 |  | 5285 | UINT16 | 11338 | 11339 | Analog Input | 686 | R |  | Amps
| Current - Circuit 95 | 95 | 6246 |  | 5286 | UINT16 | 11340 | 11341 | Analog Input | 687 | R |  | Amps
| Current - Circuit 96 | 96 | 6247 |  | 5287 | UINT16 | 11342 | 11343 | Analog Input | 688 | R |  | Amps
| Power Factor |  | 6248 | 6343 | -3 | INT16 | 11344 | 11535 | Analog Input | 689 - 784 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 1 | 1 | 6248 |  | -3 | INT16 | 11344 | 11345 | Analog Input | 689 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 2 | 2 | 6249 |  | -3 | INT16 | 11346 | 11347 | Analog Input | 690 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 3 | 3 | 6250 |  | -3 | INT16 | 11348 | 11349 | Analog Input | 691 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 4 | 4 | 6251 |  | -3 | INT16 | 11350 | 11351 | Analog Input | 692 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 5 | 5 | 6252 |  | -3 | INT16 | 11352 | 11353 | Analog Input | 693 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 6 | 6 | 6253 |  | -3 | INT16 | 11354 | 11355 | Analog Input | 694 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 7 | 7 | 6254 |  | -3 | INT16 | 11356 | 11357 | Analog Input | 695 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 8 | 8 | 6255 |  | -3 | INT16 | 11358 | 11359 | Analog Input | 696 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 9 | 9 | 6256 |  | -3 | INT16 | 11360 | 11361 | Analog Input | 697 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 10 | 10 | 6257 |  | -3 | INT16 | 11362 | 11363 | Analog Input | 698 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 11 | 11 | 6258 |  | -3 | INT16 | 11364 | 11365 | Analog Input | 699 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 12 | 12 | 6259 |  | -3 | INT16 | 11366 | 11367 | Analog Input | 700 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 13 | 13 | 6260 |  | -3 | INT16 | 11368 | 11369 | Analog Input | 701 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 14 | 14 | 6261 |  | -3 | INT16 | 11370 | 11371 | Analog Input | 702 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 15 | 15 | 6262 |  | -3 | INT16 | 11372 | 11373 | Analog Input | 703 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 16 | 16 | 6263 |  | -3 | INT16 | 11374 | 11375 | Analog Input | 704 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 17 | 17 | 6264 |  | -3 | INT16 | 11376 | 11377 | Analog Input | 705 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 18 | 18 | 6265 |  | -3 | INT16 | 11378 | 11379 | Analog Input | 706 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 19 | 19 | 6266 |  | -3 | INT16 | 11380 | 11381 | Analog Input | 707 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 20 | 20 | 6267 |  | -3 | INT16 | 11382 | 11383 | Analog Input | 708 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 21 | 21 | 6268 |  | -3 | INT16 | 11384 | 11385 | Analog Input | 709 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 22 | 22 | 6269 |  | -3 | INT16 | 11386 | 11387 | Analog Input | 710 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 23 | 23 | 6270 |  | -3 | INT16 | 11388 | 11389 | Analog Input | 711 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 24 | 24 | 6271 |  | -3 | INT16 | 11390 | 11391 | Analog Input | 712 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 25 | 25 | 6272 |  | -3 | INT16 | 11392 | 11393 | Analog Input | 713 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 26 | 26 | 6273 |  | -3 | INT16 | 11394 | 11395 | Analog Input | 714 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 27 | 27 | 6274 |  | -3 | INT16 | 11396 | 11397 | Analog Input | 715 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 28 | 28 | 6275 |  | -3 | INT16 | 11398 | 11399 | Analog Input | 716 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 29 | 29 | 6276 |  | -3 | INT16 | 11400 | 11401 | Analog Input | 717 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 30 | 30 | 6277 |  | -3 | INT16 | 11402 | 11403 | Analog Input | 718 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 31 | 31 | 6278 |  | -3 | INT16 | 11404 | 11405 | Analog Input | 719 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 32 | 32 | 6279 |  | -3 | INT16 | 11406 | 11407 | Analog Input | 720 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 33 | 33 | 6280 |  | -3 | INT16 | 11408 | 11409 | Analog Input | 721 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 34 | 34 | 6281 |  | -3 | INT16 | 11410 | 11411 | Analog Input | 722 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 35 | 35 | 6282 |  | -3 | INT16 | 11412 | 11413 | Analog Input | 723 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 36 | 36 | 6283 |  | -3 | INT16 | 11414 | 11415 | Analog Input | 724 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 37 | 37 | 6284 |  | -3 | INT16 | 11416 | 11417 | Analog Input | 725 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 38 | 38 | 6285 |  | -3 | INT16 | 11418 | 11419 | Analog Input | 726 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 39 | 39 | 6286 |  | -3 | INT16 | 11420 | 11421 | Analog Input | 727 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 40 | 40 | 6287 |  | -3 | INT16 | 11422 | 11423 | Analog Input | 728 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 41 | 41 | 6288 |  | -3 | INT16 | 11424 | 11425 | Analog Input | 729 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 42 | 42 | 6289 |  | -3 | INT16 | 11426 | 11427 | Analog Input | 730 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 43 | 43 | 6290 |  | -3 | INT16 | 11428 | 11429 | Analog Input | 731 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 44 | 44 | 6291 |  | -3 | INT16 | 11430 | 11431 | Analog Input | 732 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 45 | 45 | 6292 |  | -3 | INT16 | 11432 | 11433 | Analog Input | 733 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 46 | 46 | 6293 |  | -3 | INT16 | 11434 | 11435 | Analog Input | 734 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 47 | 47 | 6294 |  | -3 | INT16 | 11436 | 11437 | Analog Input | 735 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 48 | 48 | 6295 |  | -3 | INT16 | 11438 | 11439 | Analog Input | 736 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 49 | 49 | 6296 |  | -3 | INT16 | 11440 | 11441 | Analog Input | 737 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 50 | 50 | 6297 |  | -3 | INT16 | 11442 | 11443 | Analog Input | 738 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 51 | 51 | 6298 |  | -3 | INT16 | 11444 | 11445 | Analog Input | 739 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 52 | 52 | 6299 |  | -3 | INT16 | 11446 | 11447 | Analog Input | 740 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 53 | 53 | 6300 |  | -3 | INT16 | 11448 | 11449 | Analog Input | 741 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 54 | 54 | 6301 |  | -3 | INT16 | 11450 | 11451 | Analog Input | 742 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 55 | 55 | 6302 |  | -3 | INT16 | 11452 | 11453 | Analog Input | 743 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 56 | 56 | 6303 |  | -3 | INT16 | 11454 | 11455 | Analog Input | 744 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 57 | 57 | 6304 |  | -3 | INT16 | 11456 | 11457 | Analog Input | 745 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 58 | 58 | 6305 |  | -3 | INT16 | 11458 | 11459 | Analog Input | 746 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 59 | 59 | 6306 |  | -3 | INT16 | 11460 | 11461 | Analog Input | 747 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 60 | 60 | 6307 |  | -3 | INT16 | 11462 | 11463 | Analog Input | 748 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 61 | 61 | 6308 |  | -3 | INT16 | 11464 | 11465 | Analog Input | 749 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 62 | 62 | 6309 |  | -3 | INT16 | 11466 | 11467 | Analog Input | 750 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 63 | 63 | 6310 |  | -3 | INT16 | 11468 | 11469 | Analog Input | 751 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 64 | 64 | 6311 |  | -3 | INT16 | 11470 | 11471 | Analog Input | 752 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 65 | 65 | 6312 |  | -3 | INT16 | 11472 | 11473 | Analog Input | 753 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 66 | 66 | 6313 |  | -3 | INT16 | 11474 | 11475 | Analog Input | 754 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 67 | 67 | 6314 |  | -3 | INT16 | 11476 | 11477 | Analog Input | 755 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 68 | 68 | 6315 |  | -3 | INT16 | 11478 | 11479 | Analog Input | 756 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 69 | 69 | 6316 |  | -3 | INT16 | 11480 | 11481 | Analog Input | 757 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 70 | 70 | 6317 |  | -3 | INT16 | 11482 | 11483 | Analog Input | 758 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 71 | 71 | 6318 |  | -3 | INT16 | 11484 | 11485 | Analog Input | 759 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 72 | 72 | 6319 |  | -3 | INT16 | 11486 | 11487 | Analog Input | 760 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 73 | 73 | 6320 |  | -3 | INT16 | 11488 | 11489 | Analog Input | 761 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 74 | 74 | 6321 |  | -3 | INT16 | 11490 | 11491 | Analog Input | 762 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 75 | 75 | 6322 |  | -3 | INT16 | 11492 | 11493 | Analog Input | 763 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 76 | 76 | 6323 |  | -3 | INT16 | 11494 | 11495 | Analog Input | 764 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 77 | 77 | 6324 |  | -3 | INT16 | 11496 | 11497 | Analog Input | 765 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 78 | 78 | 6325 |  | -3 | INT16 | 11498 | 11499 | Analog Input | 766 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 79 | 79 | 6326 |  | -3 | INT16 | 11500 | 11501 | Analog Input | 767 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 80 | 80 | 6327 |  | -3 | INT16 | 11502 | 11503 | Analog Input | 768 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 81 | 81 | 6328 |  | -3 | INT16 | 11504 | 11505 | Analog Input | 769 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 82 | 82 | 6329 |  | -3 | INT16 | 11506 | 11507 | Analog Input | 770 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 83 | 83 | 6330 |  | -3 | INT16 | 11508 | 11509 | Analog Input | 771 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 84 | 84 | 6331 |  | -3 | INT16 | 11510 | 11511 | Analog Input | 772 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 85 | 85 | 6332 |  | -3 | INT16 | 11512 | 11513 | Analog Input | 773 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 86 | 86 | 6333 |  | -3 | INT16 | 11514 | 11515 | Analog Input | 774 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 87 | 87 | 6334 |  | -3 | INT16 | 11516 | 11517 | Analog Input | 775 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 88 | 88 | 6335 |  | -3 | INT16 | 11518 | 11519 | Analog Input | 776 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 89 | 89 | 6336 |  | -3 | INT16 | 11520 | 11521 | Analog Input | 777 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 90 | 90 | 6337 |  | -3 | INT16 | 11522 | 11523 | Analog Input | 778 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 91 | 91 | 6338 |  | -3 | INT16 | 11524 | 11525 | Analog Input | 779 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 92 | 92 | 6339 |  | -3 | INT16 | 11526 | 11527 | Analog Input | 780 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 93 | 93 | 6340 |  | -3 | INT16 | 11528 | 11529 | Analog Input | 781 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 94 | 94 | 6341 |  | -3 | INT16 | 11530 | 11531 | Analog Input | 782 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 95 | 95 | 6342 |  | -3 | INT16 | 11532 | 11533 | Analog Input | 783 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Power Factor - Circuit 96 | 96 | 6343 |  | -3 | INT16 | 11534 | 11535 | Analog Input | 784 | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Current Angle |  | 6344 | 6439 | -1 | INT16 | 11536 | 11727 | Analog Input | 785 - 880 | R |  | Degrees | -180° - 180° | Referenced to Assigned Voltage Phase
| Current Angle- Circuit 1 | 1 | 6344 |  | -1 | INT16 | 11536 | 11537 | Analog Input | 785 | R |  | Degrees
| Current Angle- Circuit 2 | 2 | 6345 |  | -1 | INT16 | 11538 | 11539 | Analog Input | 786 | R |  | Degrees
| Current Angle- Circuit 3 | 3 | 6346 |  | -1 | INT16 | 11540 | 11541 | Analog Input | 787 | R |  | Degrees
| Current Angle- Circuit 4 | 4 | 6347 |  | -1 | INT16 | 11542 | 11543 | Analog Input | 788 | R |  | Degrees
| Current Angle- Circuit 5 | 5 | 6348 |  | -1 | INT16 | 11544 | 11545 | Analog Input | 789 | R |  | Degrees
| Current Angle- Circuit 6 | 6 | 6349 |  | -1 | INT16 | 11546 | 11547 | Analog Input | 790 | R |  | Degrees
| Current Angle- Circuit 7 | 7 | 6350 |  | -1 | INT16 | 11548 | 11549 | Analog Input | 791 | R |  | Degrees
| Current Angle- Circuit 8 | 8 | 6351 |  | -1 | INT16 | 11550 | 11551 | Analog Input | 792 | R |  | Degrees
| Current Angle- Circuit 9 | 9 | 6352 |  | -1 | INT16 | 11552 | 11553 | Analog Input | 793 | R |  | Degrees
| Current Angle- Circuit 10 | 10 | 6353 |  | -1 | INT16 | 11554 | 11555 | Analog Input | 794 | R |  | Degrees
| Current Angle- Circuit 11 | 11 | 6354 |  | -1 | INT16 | 11556 | 11557 | Analog Input | 795 | R |  | Degrees
| Current Angle- Circuit 12 | 12 | 6355 |  | -1 | INT16 | 11558 | 11559 | Analog Input | 796 | R |  | Degrees
| Current Angle- Circuit 13 | 13 | 6356 |  | -1 | INT16 | 11560 | 11561 | Analog Input | 797 | R |  | Degrees
| Current Angle- Circuit 14 | 14 | 6357 |  | -1 | INT16 | 11562 | 11563 | Analog Input | 798 | R |  | Degrees
| Current Angle- Circuit 15 | 15 | 6358 |  | -1 | INT16 | 11564 | 11565 | Analog Input | 799 | R |  | Degrees
| Current Angle- Circuit 16 | 16 | 6359 |  | -1 | INT16 | 11566 | 11567 | Analog Input | 800 | R |  | Degrees
| Current Angle- Circuit 17 | 17 | 6360 |  | -1 | INT16 | 11568 | 11569 | Analog Input | 801 | R |  | Degrees
| Current Angle- Circuit 18 | 18 | 6361 |  | -1 | INT16 | 11570 | 11571 | Analog Input | 802 | R |  | Degrees
| Current Angle- Circuit 19 | 19 | 6362 |  | -1 | INT16 | 11572 | 11573 | Analog Input | 803 | R |  | Degrees
| Current Angle- Circuit 20 | 20 | 6363 |  | -1 | INT16 | 11574 | 11575 | Analog Input | 804 | R |  | Degrees
| Current Angle- Circuit 21 | 21 | 6364 |  | -1 | INT16 | 11576 | 11577 | Analog Input | 805 | R |  | Degrees
| Current Angle- Circuit 22 | 22 | 6365 |  | -1 | INT16 | 11578 | 11579 | Analog Input | 806 | R |  | Degrees
| Current Angle- Circuit 23 | 23 | 6366 |  | -1 | INT16 | 11580 | 11581 | Analog Input | 807 | R |  | Degrees
| Current Angle- Circuit 24 | 24 | 6367 |  | -1 | INT16 | 11582 | 11583 | Analog Input | 808 | R |  | Degrees
| Current Angle- Circuit 25 | 25 | 6368 |  | -1 | INT16 | 11584 | 11585 | Analog Input | 809 | R |  | Degrees
| Current Angle- Circuit 26 | 26 | 6369 |  | -1 | INT16 | 11586 | 11587 | Analog Input | 810 | R |  | Degrees
| Current Angle- Circuit 27 | 27 | 6370 |  | -1 | INT16 | 11588 | 11589 | Analog Input | 811 | R |  | Degrees
| Current Angle- Circuit 28 | 28 | 6371 |  | -1 | INT16 | 11590 | 11591 | Analog Input | 812 | R |  | Degrees
| Current Angle- Circuit 29 | 29 | 6372 |  | -1 | INT16 | 11592 | 11593 | Analog Input | 813 | R |  | Degrees
| Current Angle- Circuit 30 | 30 | 6373 |  | -1 | INT16 | 11594 | 11595 | Analog Input | 814 | R |  | Degrees
| Current Angle- Circuit 31 | 31 | 6374 |  | -1 | INT16 | 11596 | 11597 | Analog Input | 815 | R |  | Degrees
| Current Angle- Circuit 32 | 32 | 6375 |  | -1 | INT16 | 11598 | 11599 | Analog Input | 816 | R |  | Degrees
| Current Angle- Circuit 33 | 33 | 6376 |  | -1 | INT16 | 11600 | 11601 | Analog Input | 817 | R |  | Degrees
| Current Angle- Circuit 34 | 34 | 6377 |  | -1 | INT16 | 11602 | 11603 | Analog Input | 818 | R |  | Degrees
| Current Angle- Circuit 35 | 35 | 6378 |  | -1 | INT16 | 11604 | 11605 | Analog Input | 819 | R |  | Degrees
| Current Angle- Circuit 36 | 36 | 6379 |  | -1 | INT16 | 11606 | 11607 | Analog Input | 820 | R |  | Degrees
| Current Angle- Circuit 37 | 37 | 6380 |  | -1 | INT16 | 11608 | 11609 | Analog Input | 821 | R |  | Degrees
| Current Angle- Circuit 38 | 38 | 6381 |  | -1 | INT16 | 11610 | 11611 | Analog Input | 822 | R |  | Degrees
| Current Angle- Circuit 39 | 39 | 6382 |  | -1 | INT16 | 11612 | 11613 | Analog Input | 823 | R |  | Degrees
| Current Angle- Circuit 40 | 40 | 6383 |  | -1 | INT16 | 11614 | 11615 | Analog Input | 824 | R |  | Degrees
| Current Angle- Circuit 41 | 41 | 6384 |  | -1 | INT16 | 11616 | 11617 | Analog Input | 825 | R |  | Degrees
| Current Angle- Circuit 42 | 42 | 6385 |  | -1 | INT16 | 11618 | 11619 | Analog Input | 826 | R |  | Degrees
| Current Angle- Circuit 43 | 43 | 6386 |  | -1 | INT16 | 11620 | 11621 | Analog Input | 827 | R |  | Degrees
| Current Angle- Circuit 44 | 44 | 6387 |  | -1 | INT16 | 11622 | 11623 | Analog Input | 828 | R |  | Degrees
| Current Angle- Circuit 45 | 45 | 6388 |  | -1 | INT16 | 11624 | 11625 | Analog Input | 829 | R |  | Degrees
| Current Angle- Circuit 46 | 46 | 6389 |  | -1 | INT16 | 11626 | 11627 | Analog Input | 830 | R |  | Degrees
| Current Angle- Circuit 47 | 47 | 6390 |  | -1 | INT16 | 11628 | 11629 | Analog Input | 831 | R |  | Degrees
| Current Angle- Circuit 48 | 48 | 6391 |  | -1 | INT16 | 11630 | 11631 | Analog Input | 832 | R |  | Degrees
| Current Angle- Circuit 49 | 49 | 6392 |  | -1 | INT16 | 11632 | 11633 | Analog Input | 833 | R |  | Degrees
| Current Angle- Circuit 50 | 50 | 6393 |  | -1 | INT16 | 11634 | 11635 | Analog Input | 834 | R |  | Degrees
| Current Angle- Circuit 51 | 51 | 6394 |  | -1 | INT16 | 11636 | 11637 | Analog Input | 835 | R |  | Degrees
| Current Angle- Circuit 52 | 52 | 6395 |  | -1 | INT16 | 11638 | 11639 | Analog Input | 836 | R |  | Degrees
| Current Angle- Circuit 53 | 53 | 6396 |  | -1 | INT16 | 11640 | 11641 | Analog Input | 837 | R |  | Degrees
| Current Angle- Circuit 54 | 54 | 6397 |  | -1 | INT16 | 11642 | 11643 | Analog Input | 838 | R |  | Degrees
| Current Angle- Circuit 55 | 55 | 6398 |  | -1 | INT16 | 11644 | 11645 | Analog Input | 839 | R |  | Degrees
| Current Angle- Circuit 56 | 56 | 6399 |  | -1 | INT16 | 11646 | 11647 | Analog Input | 840 | R |  | Degrees
| Current Angle- Circuit 57 | 57 | 6400 |  | -1 | INT16 | 11648 | 11649 | Analog Input | 841 | R |  | Degrees
| Current Angle- Circuit 58 | 58 | 6401 |  | -1 | INT16 | 11650 | 11651 | Analog Input | 842 | R |  | Degrees
| Current Angle- Circuit 59 | 59 | 6402 |  | -1 | INT16 | 11652 | 11653 | Analog Input | 843 | R |  | Degrees
| Current Angle- Circuit 60 | 60 | 6403 |  | -1 | INT16 | 11654 | 11655 | Analog Input | 844 | R |  | Degrees
| Current Angle- Circuit 61 | 61 | 6404 |  | -1 | INT16 | 11656 | 11657 | Analog Input | 845 | R |  | Degrees
| Current Angle- Circuit 62 | 62 | 6405 |  | -1 | INT16 | 11658 | 11659 | Analog Input | 846 | R |  | Degrees
| Current Angle- Circuit 63 | 63 | 6406 |  | -1 | INT16 | 11660 | 11661 | Analog Input | 847 | R |  | Degrees
| Current Angle- Circuit 64 | 64 | 6407 |  | -1 | INT16 | 11662 | 11663 | Analog Input | 848 | R |  | Degrees
| Current Angle- Circuit 65 | 65 | 6408 |  | -1 | INT16 | 11664 | 11665 | Analog Input | 849 | R |  | Degrees
| Current Angle- Circuit 66 | 66 | 6409 |  | -1 | INT16 | 11666 | 11667 | Analog Input | 850 | R |  | Degrees
| Current Angle- Circuit 67 | 67 | 6410 |  | -1 | INT16 | 11668 | 11669 | Analog Input | 851 | R |  | Degrees
| Current Angle- Circuit 68 | 68 | 6411 |  | -1 | INT16 | 11670 | 11671 | Analog Input | 852 | R |  | Degrees
| Current Angle- Circuit 69 | 69 | 6412 |  | -1 | INT16 | 11672 | 11673 | Analog Input | 853 | R |  | Degrees
| Current Angle- Circuit 70 | 70 | 6413 |  | -1 | INT16 | 11674 | 11675 | Analog Input | 854 | R |  | Degrees
| Current Angle- Circuit 71 | 71 | 6414 |  | -1 | INT16 | 11676 | 11677 | Analog Input | 855 | R |  | Degrees
| Current Angle- Circuit 72 | 72 | 6415 |  | -1 | INT16 | 11678 | 11679 | Analog Input | 856 | R |  | Degrees
| Current Angle- Circuit 73 | 73 | 6416 |  | -1 | INT16 | 11680 | 11681 | Analog Input | 857 | R |  | Degrees
| Current Angle- Circuit 74 | 74 | 6417 |  | -1 | INT16 | 11682 | 11683 | Analog Input | 858 | R |  | Degrees
| Current Angle- Circuit 75 | 75 | 6418 |  | -1 | INT16 | 11684 | 11685 | Analog Input | 859 | R |  | Degrees
| Current Angle- Circuit 76 | 76 | 6419 |  | -1 | INT16 | 11686 | 11687 | Analog Input | 860 | R |  | Degrees
| Current Angle- Circuit 77 | 77 | 6420 |  | -1 | INT16 | 11688 | 11689 | Analog Input | 861 | R |  | Degrees
| Current Angle- Circuit 78 | 78 | 6421 |  | -1 | INT16 | 11690 | 11691 | Analog Input | 862 | R |  | Degrees
| Current Angle- Circuit 79 | 79 | 6422 |  | -1 | INT16 | 11692 | 11693 | Analog Input | 863 | R |  | Degrees
| Current Angle- Circuit 80 | 80 | 6423 |  | -1 | INT16 | 11694 | 11695 | Analog Input | 864 | R |  | Degrees
| Current Angle- Circuit 81 | 81 | 6424 |  | -1 | INT16 | 11696 | 11697 | Analog Input | 865 | R |  | Degrees
| Current Angle- Circuit 82 | 82 | 6425 |  | -1 | INT16 | 11698 | 11699 | Analog Input | 866 | R |  | Degrees
| Current Angle- Circuit 83 | 83 | 6426 |  | -1 | INT16 | 11700 | 11701 | Analog Input | 867 | R |  | Degrees
| Current Angle- Circuit 84 | 84 | 6427 |  | -1 | INT16 | 11702 | 11703 | Analog Input | 868 | R |  | Degrees
| Current Angle- Circuit 85 | 85 | 6428 |  | -1 | INT16 | 11704 | 11705 | Analog Input | 869 | R |  | Degrees
| Current Angle- Circuit 86 | 86 | 6429 |  | -1 | INT16 | 11706 | 11707 | Analog Input | 870 | R |  | Degrees
| Current Angle- Circuit 87 | 87 | 6430 |  | -1 | INT16 | 11708 | 11709 | Analog Input | 871 | R |  | Degrees
| Current Angle- Circuit 88 | 88 | 6431 |  | -1 | INT16 | 11710 | 11711 | Analog Input | 872 | R |  | Degrees
| Current Angle- Circuit 89 | 89 | 6432 |  | -1 | INT16 | 11712 | 11713 | Analog Input | 873 | R |  | Degrees
| Current Angle- Circuit 90 | 90 | 6433 |  | -1 | INT16 | 11714 | 11715 | Analog Input | 874 | R |  | Degrees
| Current Angle- Circuit 91 | 91 | 6434 |  | -1 | INT16 | 11716 | 11717 | Analog Input | 875 | R |  | Degrees
| Current Angle- Circuit 92 | 92 | 6435 |  | -1 | INT16 | 11718 | 11719 | Analog Input | 876 | R |  | Degrees
| Current Angle- Circuit 93 | 93 | 6436 |  | -1 | INT16 | 11720 | 11721 | Analog Input | 877 | R |  | Degrees
| Current Angle- Circuit 94 | 94 | 6437 |  | -1 | INT16 | 11722 | 11723 | Analog Input | 878 | R |  | Degrees
| Current Angle- Circuit 95 | 95 | 6438 |  | -1 | INT16 | 11724 | 11725 | Analog Input | 879 | R |  | Degrees
| Current Angle- Circuit 96 | 96 | 6439 |  | -1 | INT16 | 11726 | 11727 | Analog Input | 880 | R |  | Degrees
| Percent THD |  | 6440 | 6535 | -1 | UINT16 | 11728 | 11919 | Analog Input | 681 - 976 | R |  | Percent
| Percent THD - Circuit 1 | 1 | 6440 |  | -1 | UINT16 | 11728 | 11729 | Analog Input | 881 | R |  | Percent
| Percent THD - Circuit 2 | 2 | 6441 |  | -1 | UINT16 | 11730 | 11731 | Analog Input | 882 | R |  | Percent
| Percent THD - Circuit 3 | 3 | 6442 |  | -1 | UINT16 | 11732 | 11733 | Analog Input | 883 | R |  | Percent
| Percent THD - Circuit 4 | 4 | 6443 |  | -1 | UINT16 | 11734 | 11735 | Analog Input | 884 | R |  | Percent
| Percent THD - Circuit 5 | 5 | 6444 |  | -1 | UINT16 | 11736 | 11737 | Analog Input | 885 | R |  | Percent
| Percent THD - Circuit 6 | 6 | 6445 |  | -1 | UINT16 | 11738 | 11739 | Analog Input | 886 | R |  | Percent
| Percent THD - Circuit 7 | 7 | 6446 |  | -1 | UINT16 | 11740 | 11741 | Analog Input | 887 | R |  | Percent
| Percent THD - Circuit 8 | 8 | 6447 |  | -1 | UINT16 | 11742 | 11743 | Analog Input | 888 | R |  | Percent
| Percent THD - Circuit 9 | 9 | 6448 |  | -1 | UINT16 | 11744 | 11745 | Analog Input | 889 | R |  | Percent
| Percent THD - Circuit 10 | 10 | 6449 |  | -1 | UINT16 | 11746 | 11747 | Analog Input | 890 | R |  | Percent
| Percent THD - Circuit 11 | 11 | 6450 |  | -1 | UINT16 | 11748 | 11749 | Analog Input | 891 | R |  | Percent
| Percent THD - Circuit 12 | 12 | 6451 |  | -1 | UINT16 | 11750 | 11751 | Analog Input | 892 | R |  | Percent
| Percent THD - Circuit 13 | 13 | 6452 |  | -1 | UINT16 | 11752 | 11753 | Analog Input | 893 | R |  | Percent
| Percent THD - Circuit 14 | 14 | 6453 |  | -1 | UINT16 | 11754 | 11755 | Analog Input | 894 | R |  | Percent
| Percent THD - Circuit 15 | 15 | 6454 |  | -1 | UINT16 | 11756 | 11757 | Analog Input | 895 | R |  | Percent
| Percent THD - Circuit 16 | 16 | 6455 |  | -1 | UINT16 | 11758 | 11759 | Analog Input | 896 | R |  | Percent
| Percent THD - Circuit 17 | 17 | 6456 |  | -1 | UINT16 | 11760 | 11761 | Analog Input | 897 | R |  | Percent
| Percent THD - Circuit 18 | 18 | 6457 |  | -1 | UINT16 | 11762 | 11763 | Analog Input | 898 | R |  | Percent
| Percent THD - Circuit 19 | 19 | 6458 |  | -1 | UINT16 | 11764 | 11765 | Analog Input | 899 | R |  | Percent
| Percent THD - Circuit 20 | 20 | 6459 |  | -1 | UINT16 | 11766 | 11767 | Analog Input | 900 | R |  | Percent
| Percent THD - Circuit 21 | 21 | 6460 |  | -1 | UINT16 | 11768 | 11769 | Analog Input | 901 | R |  | Percent
| Percent THD - Circuit 22 | 22 | 6461 |  | -1 | UINT16 | 11770 | 11771 | Analog Input | 902 | R |  | Percent
| Percent THD - Circuit 23 | 23 | 6462 |  | -1 | UINT16 | 11772 | 11773 | Analog Input | 903 | R |  | Percent
| Percent THD - Circuit 24 | 24 | 6463 |  | -1 | UINT16 | 11774 | 11775 | Analog Input | 904 | R |  | Percent
| Percent THD - Circuit 25 | 25 | 6464 |  | -1 | UINT16 | 11776 | 11777 | Analog Input | 905 | R |  | Percent
| Percent THD - Circuit 26 | 26 | 6465 |  | -1 | UINT16 | 11778 | 11779 | Analog Input | 906 | R |  | Percent
| Percent THD - Circuit 27 | 27 | 6466 |  | -1 | UINT16 | 11780 | 11781 | Analog Input | 907 | R |  | Percent
| Percent THD - Circuit 28 | 28 | 6467 |  | -1 | UINT16 | 11782 | 11783 | Analog Input | 908 | R |  | Percent
| Percent THD - Circuit 29 | 29 | 6468 |  | -1 | UINT16 | 11784 | 11785 | Analog Input | 909 | R |  | Percent
| Percent THD - Circuit 30 | 30 | 6469 |  | -1 | UINT16 | 11786 | 11787 | Analog Input | 910 | R |  | Percent
| Percent THD - Circuit 31 | 31 | 6470 |  | -1 | UINT16 | 11788 | 11789 | Analog Input | 911 | R |  | Percent
| Percent THD - Circuit 32 | 32 | 6471 |  | -1 | UINT16 | 11790 | 11791 | Analog Input | 912 | R |  | Percent
| Percent THD - Circuit 33 | 33 | 6472 |  | -1 | UINT16 | 11792 | 11793 | Analog Input | 913 | R |  | Percent
| Percent THD - Circuit 34 | 34 | 6473 |  | -1 | UINT16 | 11794 | 11795 | Analog Input | 914 | R |  | Percent
| Percent THD - Circuit 35 | 35 | 6474 |  | -1 | UINT16 | 11796 | 11797 | Analog Input | 915 | R |  | Percent
| Percent THD - Circuit 36 | 36 | 6475 |  | -1 | UINT16 | 11798 | 11799 | Analog Input | 916 | R |  | Percent
| Percent THD - Circuit 37 | 37 | 6476 |  | -1 | UINT16 | 11800 | 11801 | Analog Input | 917 | R |  | Percent
| Percent THD - Circuit 38 | 38 | 6477 |  | -1 | UINT16 | 11802 | 11803 | Analog Input | 918 | R |  | Percent
| Percent THD - Circuit 39 | 39 | 6478 |  | -1 | UINT16 | 11804 | 11805 | Analog Input | 919 | R |  | Percent
| Percent THD - Circuit 40 | 40 | 6479 |  | -1 | UINT16 | 11806 | 11807 | Analog Input | 920 | R |  | Percent
| Percent THD - Circuit 41 | 41 | 6480 |  | -1 | UINT16 | 11808 | 11809 | Analog Input | 921 | R |  | Percent
| Percent THD - Circuit 42 | 42 | 6481 |  | -1 | UINT16 | 11810 | 11811 | Analog Input | 922 | R |  | Percent
| Percent THD - Circuit 43 | 43 | 6482 |  | -1 | UINT16 | 11812 | 11813 | Analog Input | 923 | R |  | Percent
| Percent THD - Circuit 44 | 44 | 6483 |  | -1 | UINT16 | 11814 | 11815 | Analog Input | 924 | R |  | Percent
| Percent THD - Circuit 45 | 45 | 6484 |  | -1 | UINT16 | 11816 | 11817 | Analog Input | 925 | R |  | Percent
| Percent THD - Circuit 46 | 46 | 6485 |  | -1 | UINT16 | 11818 | 11819 | Analog Input | 926 | R |  | Percent
| Percent THD - Circuit 47 | 47 | 6486 |  | -1 | UINT16 | 11820 | 11821 | Analog Input | 927 | R |  | Percent
| Percent THD - Circuit 48 | 48 | 6487 |  | -1 | UINT16 | 11822 | 11823 | Analog Input | 928 | R |  | Percent
| Percent THD - Circuit 49 | 49 | 6488 |  | -1 | UINT16 | 11824 | 11825 | Analog Input | 929 | R |  | Percent
| Percent THD - Circuit 50 | 50 | 6489 |  | -1 | UINT16 | 11826 | 11827 | Analog Input | 930 | R |  | Percent
| Percent THD - Circuit 51 | 51 | 6490 |  | -1 | UINT16 | 11828 | 11829 | Analog Input | 931 | R |  | Percent
| Percent THD - Circuit 52 | 52 | 6491 |  | -1 | UINT16 | 11830 | 11831 | Analog Input | 932 | R |  | Percent
| Percent THD - Circuit 53 | 53 | 6492 |  | -1 | UINT16 | 11832 | 11833 | Analog Input | 933 | R |  | Percent
| Percent THD - Circuit 54 | 54 | 6493 |  | -1 | UINT16 | 11834 | 11835 | Analog Input | 934 | R |  | Percent
| Percent THD - Circuit 55 | 55 | 6494 |  | -1 | UINT16 | 11836 | 11837 | Analog Input | 935 | R |  | Percent
| Percent THD - Circuit 56 | 56 | 6495 |  | -1 | UINT16 | 11838 | 11839 | Analog Input | 936 | R |  | Percent
| Percent THD - Circuit 57 | 57 | 6496 |  | -1 | UINT16 | 11840 | 11841 | Analog Input | 937 | R |  | Percent
| Percent THD - Circuit 58 | 58 | 6497 |  | -1 | UINT16 | 11842 | 11843 | Analog Input | 938 | R |  | Percent
| Percent THD - Circuit 59 | 59 | 6498 |  | -1 | UINT16 | 11844 | 11845 | Analog Input | 939 | R |  | Percent
| Percent THD - Circuit 60 | 60 | 6499 |  | -1 | UINT16 | 11846 | 11847 | Analog Input | 940 | R |  | Percent
| Percent THD - Circuit 61 | 61 | 6500 |  | -1 | UINT16 | 11848 | 11849 | Analog Input | 941 | R |  | Percent
| Percent THD - Circuit 62 | 62 | 6501 |  | -1 | UINT16 | 11850 | 11851 | Analog Input | 942 | R |  | Percent
| Percent THD - Circuit 63 | 63 | 6502 |  | -1 | UINT16 | 11852 | 11853 | Analog Input | 943 | R |  | Percent
| Percent THD - Circuit 64 | 64 | 6503 |  | -1 | UINT16 | 11854 | 11855 | Analog Input | 944 | R |  | Percent
| Percent THD - Circuit 65 | 65 | 6504 |  | -1 | UINT16 | 11856 | 11857 | Analog Input | 945 | R |  | Percent
| Percent THD - Circuit 66 | 66 | 6505 |  | -1 | UINT16 | 11858 | 11859 | Analog Input | 946 | R |  | Percent
| Percent THD - Circuit 67 | 67 | 6506 |  | -1 | UINT16 | 11860 | 11861 | Analog Input | 947 | R |  | Percent
| Percent THD - Circuit 68 | 68 | 6507 |  | -1 | UINT16 | 11862 | 11863 | Analog Input | 948 | R |  | Percent
| Percent THD - Circuit 69 | 69 | 6508 |  | -1 | UINT16 | 11864 | 11865 | Analog Input | 949 | R |  | Percent
| Percent THD - Circuit 70 | 70 | 6509 |  | -1 | UINT16 | 11866 | 11867 | Analog Input | 950 | R |  | Percent
| Percent THD - Circuit 71 | 71 | 6510 |  | -1 | UINT16 | 11868 | 11869 | Analog Input | 951 | R |  | Percent
| Percent THD - Circuit 72 | 72 | 6511 |  | -1 | UINT16 | 11870 | 11871 | Analog Input | 952 | R |  | Percent
| Percent THD - Circuit 73 | 73 | 6512 |  | -1 | UINT16 | 11872 | 11873 | Analog Input | 953 | R |  | Percent
| Percent THD - Circuit 74 | 74 | 6513 |  | -1 | UINT16 | 11874 | 11875 | Analog Input | 954 | R |  | Percent
| Percent THD - Circuit 75 | 75 | 6514 |  | -1 | UINT16 | 11876 | 11877 | Analog Input | 955 | R |  | Percent
| Percent THD - Circuit 76 | 76 | 6515 |  | -1 | UINT16 | 11878 | 11879 | Analog Input | 956 | R |  | Percent
| Percent THD - Circuit 77 | 77 | 6516 |  | -1 | UINT16 | 11880 | 11881 | Analog Input | 957 | R |  | Percent
| Percent THD - Circuit 78 | 78 | 6517 |  | -1 | UINT16 | 11882 | 11883 | Analog Input | 958 | R |  | Percent
| Percent THD - Circuit 79 | 79 | 6518 |  | -1 | UINT16 | 11884 | 11885 | Analog Input | 959 | R |  | Percent
| Percent THD - Circuit 80 | 80 | 6519 |  | -1 | UINT16 | 11886 | 11887 | Analog Input | 960 | R |  | Percent
| Percent THD - Circuit 81 | 81 | 6520 |  | -1 | UINT16 | 11888 | 11889 | Analog Input | 961 | R |  | Percent
| Percent THD - Circuit 82 | 82 | 6521 |  | -1 | UINT16 | 11890 | 11891 | Analog Input | 962 | R |  | Percent
| Percent THD - Circuit 83 | 83 | 6522 |  | -1 | UINT16 | 11892 | 11893 | Analog Input | 963 | R |  | Percent
| Percent THD - Circuit 84 | 84 | 6523 |  | -1 | UINT16 | 11894 | 11895 | Analog Input | 964 | R |  | Percent
| Percent THD - Circuit 85 | 85 | 6524 |  | -1 | UINT16 | 11896 | 11897 | Analog Input | 965 | R |  | Percent
| Percent THD - Circuit 86 | 86 | 6525 |  | -1 | UINT16 | 11898 | 11899 | Analog Input | 966 | R |  | Percent
| Percent THD - Circuit 87 | 87 | 6526 |  | -1 | UINT16 | 11900 | 11901 | Analog Input | 967 | R |  | Percent
| Percent THD - Circuit 88 | 88 | 6527 |  | -1 | UINT16 | 11902 | 11903 | Analog Input | 968 | R |  | Percent
| Percent THD - Circuit 89 | 89 | 6528 |  | -1 | UINT16 | 11904 | 11905 | Analog Input | 969 | R |  | Percent
| Percent THD - Circuit 90 | 90 | 6529 |  | -1 | UINT16 | 11906 | 11907 | Analog Input | 970 | R |  | Percent
| Percent THD - Circuit 91 | 91 | 6530 |  | -1 | UINT16 | 11908 | 11909 | Analog Input | 971 | R |  | Percent
| Percent THD - Circuit 92 | 92 | 6531 |  | -1 | UINT16 | 11910 | 11911 | Analog Input | 972 | R |  | Percent
| Percent THD - Circuit 93 | 93 | 6532 |  | -1 | UINT16 | 11912 | 11913 | Analog Input | 973 | R |  | Percent
| Percent THD - Circuit 94 | 94 | 6533 |  | -1 | UINT16 | 11914 | 11915 | Analog Input | 974 | R |  | Percent
| Percent THD - Circuit 95 | 95 | 6534 |  | -1 | UINT16 | 11916 | 11917 | Analog Input | 975 | R |  | Percent
| Percent THD - Circuit 96 | 96 | 6535 |  | -1 | UINT16 | 11918 | 11919 | Analog Input | 976 | R |  | Percent
| Max Current |  | 6536 | 6631 | Current | UINT16 | 11920 | 12111 | Analog Input | 977 - 1072 | R | NV | Amps
| Max Current- Circuit 1 | 1 | 6536 |  | 5192 | UINT16 | 11920 | 11921 | Analog Input | 977 | R | NV | Amps
| Max Current- Circuit 2 | 2 | 6537 |  | 5193 | UINT16 | 11922 | 11923 | Analog Input | 978 | R | NV | Amps
| Max Current- Circuit 3 | 3 | 6538 |  | 5194 | UINT16 | 11924 | 11925 | Analog Input | 979 | R | NV | Amps
| Max Current- Circuit 4 | 4 | 6539 |  | 5195 | UINT16 | 11926 | 11927 | Analog Input | 980 | R | NV | Amps
| Max Current- Circuit 5 | 5 | 6540 |  | 5196 | UINT16 | 11928 | 11929 | Analog Input | 981 | R | NV | Amps
| Max Current- Circuit 6 | 6 | 6541 |  | 5197 | UINT16 | 11930 | 11931 | Analog Input | 982 | R | NV | Amps
| Max Current- Circuit 7 | 7 | 6542 |  | 5198 | UINT16 | 11932 | 11933 | Analog Input | 983 | R | NV | Amps
| Max Current- Circuit 8 | 8 | 6543 |  | 5199 | UINT16 | 11934 | 11935 | Analog Input | 984 | R | NV | Amps
| Max Current- Circuit 9 | 9 | 6544 |  | 5200 | UINT16 | 11936 | 11937 | Analog Input | 985 | R | NV | Amps
| Max Current- Circuit 10 | 10 | 6545 |  | 5201 | UINT16 | 11938 | 11939 | Analog Input | 986 | R | NV | Amps
| Max Current- Circuit 11 | 11 | 6546 |  | 5202 | UINT16 | 11940 | 11941 | Analog Input | 987 | R | NV | Amps
| Max Current- Circuit 12 | 12 | 6547 |  | 5203 | UINT16 | 11942 | 11943 | Analog Input | 988 | R | NV | Amps
| Max Current- Circuit 13 | 13 | 6548 |  | 5204 | UINT16 | 11944 | 11945 | Analog Input | 989 | R | NV | Amps
| Max Current- Circuit 14 | 14 | 6549 |  | 5205 | UINT16 | 11946 | 11947 | Analog Input | 990 | R | NV | Amps
| Max Current- Circuit 15 | 15 | 6550 |  | 5206 | UINT16 | 11948 | 11949 | Analog Input | 991 | R | NV | Amps
| Max Current- Circuit 16 | 16 | 6551 |  | 5207 | UINT16 | 11950 | 11951 | Analog Input | 992 | R | NV | Amps
| Max Current- Circuit 17 | 17 | 6552 |  | 5208 | UINT16 | 11952 | 11953 | Analog Input | 993 | R | NV | Amps
| Max Current- Circuit 18 | 18 | 6553 |  | 5209 | UINT16 | 11954 | 11955 | Analog Input | 994 | R | NV | Amps
| Max Current- Circuit 19 | 19 | 6554 |  | 5210 | UINT16 | 11956 | 11957 | Analog Input | 995 | R | NV | Amps
| Max Current- Circuit 20 | 20 | 6555 |  | 5211 | UINT16 | 11958 | 11959 | Analog Input | 996 | R | NV | Amps
| Max Current- Circuit 21 | 21 | 6556 |  | 5212 | UINT16 | 11960 | 11961 | Analog Input | 997 | R | NV | Amps
| Max Current- Circuit 22 | 22 | 6557 |  | 5213 | UINT16 | 11962 | 11963 | Analog Input | 998 | R | NV | Amps
| Max Current- Circuit 23 | 23 | 6558 |  | 5214 | UINT16 | 11964 | 11965 | Analog Input | 999 | R | NV | Amps
| Max Current- Circuit 24 | 24 | 6559 |  | 5215 | UINT16 | 11966 | 11967 | Analog Input | 1000 | R | NV | Amps
| Max Current- Circuit 25 | 25 | 6560 |  | 5216 | UINT16 | 11968 | 11969 | Analog Input | 1001 | R | NV | Amps
| Max Current- Circuit 26 | 26 | 6561 |  | 5217 | UINT16 | 11970 | 11971 | Analog Input | 1002 | R | NV | Amps
| Max Current- Circuit 27 | 27 | 6562 |  | 5218 | UINT16 | 11972 | 11973 | Analog Input | 1003 | R | NV | Amps
| Max Current- Circuit 28 | 28 | 6563 |  | 5219 | UINT16 | 11974 | 11975 | Analog Input | 1004 | R | NV | Amps
| Max Current- Circuit 29 | 29 | 6564 |  | 5220 | UINT16 | 11976 | 11977 | Analog Input | 1005 | R | NV | Amps
| Max Current- Circuit 30 | 30 | 6565 |  | 5221 | UINT16 | 11978 | 11979 | Analog Input | 1006 | R | NV | Amps
| Max Current- Circuit 31 | 31 | 6566 |  | 5222 | UINT16 | 11980 | 11981 | Analog Input | 1007 | R | NV | Amps
| Max Current- Circuit 32 | 32 | 6567 |  | 5223 | UINT16 | 11982 | 11983 | Analog Input | 1008 | R | NV | Amps
| Max Current- Circuit 33 | 33 | 6568 |  | 5224 | UINT16 | 11984 | 11985 | Analog Input | 1009 | R | NV | Amps
| Max Current- Circuit 34 | 34 | 6569 |  | 5225 | UINT16 | 11986 | 11987 | Analog Input | 1010 | R | NV | Amps
| Max Current- Circuit 35 | 35 | 6570 |  | 5226 | UINT16 | 11988 | 11989 | Analog Input | 1011 | R | NV | Amps
| Max Current- Circuit 36 | 36 | 6571 |  | 5227 | UINT16 | 11990 | 11991 | Analog Input | 1012 | R | NV | Amps
| Max Current- Circuit 37 | 37 | 6572 |  | 5228 | UINT16 | 11992 | 11993 | Analog Input | 1013 | R | NV | Amps
| Max Current- Circuit 38 | 38 | 6573 |  | 5229 | UINT16 | 11994 | 11995 | Analog Input | 1014 | R | NV | Amps
| Max Current- Circuit 39 | 39 | 6574 |  | 5230 | UINT16 | 11996 | 11997 | Analog Input | 1015 | R | NV | Amps
| Max Current- Circuit 40 | 40 | 6575 |  | 5231 | UINT16 | 11998 | 11999 | Analog Input | 1016 | R | NV | Amps
| Max Current- Circuit 41 | 41 | 6576 |  | 5232 | UINT16 | 12000 | 12001 | Analog Input | 1017 | R | NV | Amps
| Max Current- Circuit 42 | 42 | 6577 |  | 5233 | UINT16 | 12002 | 12003 | Analog Input | 1018 | R | NV | Amps
| Max Current- Circuit 43 | 43 | 6578 |  | 5234 | UINT16 | 12004 | 12005 | Analog Input | 1019 | R | NV | Amps
| Max Current- Circuit 44 | 44 | 6579 |  | 5235 | UINT16 | 12006 | 12007 | Analog Input | 1020 | R | NV | Amps
| Max Current- Circuit 45 | 45 | 6580 |  | 5236 | UINT16 | 12008 | 12009 | Analog Input | 1021 | R | NV | Amps
| Max Current- Circuit 46 | 46 | 6581 |  | 5237 | UINT16 | 12010 | 12011 | Analog Input | 1022 | R | NV | Amps
| Max Current- Circuit 47 | 47 | 6582 |  | 5238 | UINT16 | 12012 | 12013 | Analog Input | 1023 | R | NV | Amps
| Max Current- Circuit 48 | 48 | 6583 |  | 5239 | UINT16 | 12014 | 12015 | Analog Input | 1024 | R | NV | Amps
| Max Current- Circuit 49 | 49 | 6584 |  | 5240 | UINT16 | 12016 | 12017 | Analog Input | 1025 | R | NV | Amps
| Max Current- Circuit 50 | 50 | 6585 |  | 5241 | UINT16 | 12018 | 12019 | Analog Input | 1026 | R | NV | Amps
| Max Current- Circuit 51 | 51 | 6586 |  | 5242 | UINT16 | 12020 | 12021 | Analog Input | 1027 | R | NV | Amps
| Max Current- Circuit 52 | 52 | 6587 |  | 5243 | UINT16 | 12022 | 12023 | Analog Input | 1028 | R | NV | Amps
| Max Current- Circuit 53 | 53 | 6588 |  | 5244 | UINT16 | 12024 | 12025 | Analog Input | 1029 | R | NV | Amps
| Max Current- Circuit 54 | 54 | 6589 |  | 5245 | UINT16 | 12026 | 12027 | Analog Input | 1030 | R | NV | Amps
| Max Current- Circuit 55 | 55 | 6590 |  | 5246 | UINT16 | 12028 | 12029 | Analog Input | 1031 | R | NV | Amps
| Max Current- Circuit 56 | 56 | 6591 |  | 5247 | UINT16 | 12030 | 12031 | Analog Input | 1032 | R | NV | Amps
| Max Current- Circuit 57 | 57 | 6592 |  | 5248 | UINT16 | 12032 | 12033 | Analog Input | 1033 | R | NV | Amps
| Max Current- Circuit 58 | 58 | 6593 |  | 5249 | UINT16 | 12034 | 12035 | Analog Input | 1034 | R | NV | Amps
| Max Current- Circuit 59 | 59 | 6594 |  | 5250 | UINT16 | 12036 | 12037 | Analog Input | 1035 | R | NV | Amps
| Max Current- Circuit 60 | 60 | 6595 |  | 5251 | UINT16 | 12038 | 12039 | Analog Input | 1036 | R | NV | Amps
| Max Current- Circuit 61 | 61 | 6596 |  | 5252 | UINT16 | 12040 | 12041 | Analog Input | 1037 | R | NV | Amps
| Max Current- Circuit 62 | 62 | 6597 |  | 5253 | UINT16 | 12042 | 12043 | Analog Input | 1038 | R | NV | Amps
| Max Current- Circuit 63 | 63 | 6598 |  | 5254 | UINT16 | 12044 | 12045 | Analog Input | 1039 | R | NV | Amps
| Max Current- Circuit 64 | 64 | 6599 |  | 5255 | UINT16 | 12046 | 12047 | Analog Input | 1040 | R | NV | Amps
| Max Current- Circuit 65 | 65 | 6600 |  | 5256 | UINT16 | 12048 | 12049 | Analog Input | 1041 | R | NV | Amps
| Max Current- Circuit 66 | 66 | 6601 |  | 5257 | UINT16 | 12050 | 12051 | Analog Input | 1042 | R | NV | Amps
| Max Current- Circuit 67 | 67 | 6602 |  | 5258 | UINT16 | 12052 | 12053 | Analog Input | 1043 | R | NV | Amps
| Max Current- Circuit 68 | 68 | 6603 |  | 5259 | UINT16 | 12054 | 12055 | Analog Input | 1044 | R | NV | Amps
| Max Current- Circuit 69 | 69 | 6604 |  | 5260 | UINT16 | 12056 | 12057 | Analog Input | 1045 | R | NV | Amps
| Max Current- Circuit 70 | 70 | 6605 |  | 5261 | UINT16 | 12058 | 12059 | Analog Input | 1046 | R | NV | Amps
| Max Current- Circuit 71 | 71 | 6606 |  | 5262 | UINT16 | 12060 | 12061 | Analog Input | 1047 | R | NV | Amps
| Max Current- Circuit 72 | 72 | 6607 |  | 5263 | UINT16 | 12062 | 12063 | Analog Input | 1048 | R | NV | Amps
| Max Current- Circuit 73 | 73 | 6608 |  | 5264 | UINT16 | 12064 | 12065 | Analog Input | 1049 | R | NV | Amps
| Max Current- Circuit 74 | 74 | 6609 |  | 5265 | UINT16 | 12066 | 12067 | Analog Input | 1050 | R | NV | Amps
| Max Current- Circuit 75 | 75 | 6610 |  | 5266 | UINT16 | 12068 | 12069 | Analog Input | 1051 | R | NV | Amps
| Max Current- Circuit 76 | 76 | 6611 |  | 5267 | UINT16 | 12070 | 12071 | Analog Input | 1052 | R | NV | Amps
| Max Current- Circuit 77 | 77 | 6612 |  | 5268 | UINT16 | 12072 | 12073 | Analog Input | 1053 | R | NV | Amps
| Max Current- Circuit 78 | 78 | 6613 |  | 5269 | UINT16 | 12074 | 12075 | Analog Input | 1054 | R | NV | Amps
| Max Current- Circuit 79 | 79 | 6614 |  | 5270 | UINT16 | 12076 | 12077 | Analog Input | 1055 | R | NV | Amps
| Max Current- Circuit 80 | 80 | 6615 |  | 5271 | UINT16 | 12078 | 12079 | Analog Input | 1056 | R | NV | Amps
| Max Current- Circuit 81 | 81 | 6616 |  | 5272 | UINT16 | 12080 | 12081 | Analog Input | 1057 | R | NV | Amps
| Max Current- Circuit 82 | 82 | 6617 |  | 5273 | UINT16 | 12082 | 12083 | Analog Input | 1058 | R | NV | Amps
| Max Current- Circuit 83 | 83 | 6618 |  | 5274 | UINT16 | 12084 | 12085 | Analog Input | 1059 | R | NV | Amps
| Max Current- Circuit 84 | 84 | 6619 |  | 5275 | UINT16 | 12086 | 12087 | Analog Input | 1060 | R | NV | Amps
| Max Current- Circuit 85 | 85 | 6620 |  | 5276 | UINT16 | 12088 | 12089 | Analog Input | 1061 | R | NV | Amps
| Max Current- Circuit 86 | 86 | 6621 |  | 5277 | UINT16 | 12090 | 12091 | Analog Input | 1062 | R | NV | Amps
| Max Current- Circuit 87 | 87 | 6622 |  | 5278 | UINT16 | 12092 | 12093 | Analog Input | 1063 | R | NV | Amps
| Max Current- Circuit 88 | 88 | 6623 |  | 5279 | UINT16 | 12094 | 12095 | Analog Input | 1064 | R | NV | Amps
| Max Current- Circuit 89 | 89 | 6624 |  | 5280 | UINT16 | 12096 | 12097 | Analog Input | 1065 | R | NV | Amps
| Max Current- Circuit 90 | 90 | 6625 |  | 5281 | UINT16 | 12098 | 12099 | Analog Input | 1066 | R | NV | Amps
| Max Current- Circuit 91 | 91 | 6626 |  | 5282 | UINT16 | 12100 | 12101 | Analog Input | 1067 | R | NV | Amps
| Max Current- Circuit 92 | 92 | 6627 |  | 5283 | UINT16 | 12102 | 12103 | Analog Input | 1068 | R | NV | Amps
| Max Current- Circuit 93 | 93 | 6628 |  | 5284 | UINT16 | 12104 | 12105 | Analog Input | 1069 | R | NV | Amps
| Max Current- Circuit 94 | 94 | 6629 |  | 5285 | UINT16 | 12106 | 12107 | Analog Input | 1070 | R | NV | Amps
| Max Current- Circuit 95 | 95 | 6630 |  | 5286 | UINT16 | 12108 | 12109 | Analog Input | 1071 | R | NV | Amps
| Max Current- Circuit 96 | 96 | 6631 |  | 5287 | UINT16 | 12110 | 12111 | Analog Input | 1072 | R | NV | Amps
| Max kW |  | 6632 | 6727 | Power | UINT16 | 12112 | 12303 | Analog Input | 1073 - 1068 | R | NV | kW
| Max kW- Circuit 1 | 1 | 6632 |  | 5096 | UINT16 | 12112 | 12113 | Analog Input | 1073 | R | NV | kW
| Max kW- Circuit 2 | 2 | 6633 |  | 5097 | UINT16 | 12114 | 12115 | Analog Input | 1074 | R | NV | kW
| Max kW- Circuit 3 | 3 | 6634 |  | 5098 | UINT16 | 12116 | 12117 | Analog Input | 1075 | R | NV | kW
| Max kW- Circuit 4 | 4 | 6635 |  | 5099 | UINT16 | 12118 | 12119 | Analog Input | 1076 | R | NV | kW
| Max kW- Circuit 5 | 5 | 6636 |  | 5100 | UINT16 | 12120 | 12121 | Analog Input | 1077 | R | NV | kW
| Max kW- Circuit 6 | 6 | 6637 |  | 5101 | UINT16 | 12122 | 12123 | Analog Input | 1078 | R | NV | kW
| Max kW- Circuit 7 | 7 | 6638 |  | 5102 | UINT16 | 12124 | 12125 | Analog Input | 1079 | R | NV | kW
| Max kW- Circuit 8 | 8 | 6639 |  | 5103 | UINT16 | 12126 | 12127 | Analog Input | 1080 | R | NV | kW
| Max kW- Circuit 9 | 9 | 6640 |  | 5104 | UINT16 | 12128 | 12129 | Analog Input | 1081 | R | NV | kW
| Max kW- Circuit 10 | 10 | 6641 |  | 5105 | UINT16 | 12130 | 12131 | Analog Input | 1082 | R | NV | kW
| Max kW- Circuit 11 | 11 | 6642 |  | 5106 | UINT16 | 12132 | 12133 | Analog Input | 1083 | R | NV | kW
| Max kW- Circuit 12 | 12 | 6643 |  | 5107 | UINT16 | 12134 | 12135 | Analog Input | 1084 | R | NV | kW
| Max kW- Circuit 13 | 13 | 6644 |  | 5108 | UINT16 | 12136 | 12137 | Analog Input | 1085 | R | NV | kW
| Max kW- Circuit 14 | 14 | 6645 |  | 5109 | UINT16 | 12138 | 12139 | Analog Input | 1086 | R | NV | kW
| Max kW- Circuit 15 | 15 | 6646 |  | 5110 | UINT16 | 12140 | 12141 | Analog Input | 1087 | R | NV | kW
| Max kW- Circuit 16 | 16 | 6647 |  | 5111 | UINT16 | 12142 | 12143 | Analog Input | 1088 | R | NV | kW
| Max kW- Circuit 17 | 17 | 6648 |  | 5112 | UINT16 | 12144 | 12145 | Analog Input | 1089 | R | NV | kW
| Max kW- Circuit 18 | 18 | 6649 |  | 5113 | UINT16 | 12146 | 12147 | Analog Input | 1090 | R | NV | kW
| Max kW- Circuit 19 | 19 | 6650 |  | 5114 | UINT16 | 12148 | 12149 | Analog Input | 1091 | R | NV | kW
| Max kW- Circuit 20 | 20 | 6651 |  | 5115 | UINT16 | 12150 | 12151 | Analog Input | 1092 | R | NV | kW
| Max kW- Circuit 21 | 21 | 6652 |  | 5116 | UINT16 | 12152 | 12153 | Analog Input | 1093 | R | NV | kW
| Max kW- Circuit 22 | 22 | 6653 |  | 5117 | UINT16 | 12154 | 12155 | Analog Input | 1094 | R | NV | kW
| Max kW- Circuit 23 | 23 | 6654 |  | 5118 | UINT16 | 12156 | 12157 | Analog Input | 1095 | R | NV | kW
| Max kW- Circuit 24 | 24 | 6655 |  | 5119 | UINT16 | 12158 | 12159 | Analog Input | 1096 | R | NV | kW
| Max kW- Circuit 25 | 25 | 6656 |  | 5120 | UINT16 | 12160 | 12161 | Analog Input | 1097 | R | NV | kW
| Max kW- Circuit 26 | 26 | 6657 |  | 5121 | UINT16 | 12162 | 12163 | Analog Input | 1098 | R | NV | kW
| Max kW- Circuit 27 | 27 | 6658 |  | 5122 | UINT16 | 12164 | 12165 | Analog Input | 1099 | R | NV | kW
| Max kW- Circuit 28 | 28 | 6659 |  | 5123 | UINT16 | 12166 | 12167 | Analog Input | 1100 | R | NV | kW
| Max kW- Circuit 29 | 29 | 6660 |  | 5124 | UINT16 | 12168 | 12169 | Analog Input | 1101 | R | NV | kW
| Max kW- Circuit 30 | 30 | 6661 |  | 5125 | UINT16 | 12170 | 12171 | Analog Input | 1102 | R | NV | kW
| Max kW- Circuit 31 | 31 | 6662 |  | 5126 | UINT16 | 12172 | 12173 | Analog Input | 1103 | R | NV | kW
| Max kW- Circuit 32 | 32 | 6663 |  | 5127 | UINT16 | 12174 | 12175 | Analog Input | 1104 | R | NV | kW
| Max kW- Circuit 33 | 33 | 6664 |  | 5128 | UINT16 | 12176 | 12177 | Analog Input | 1105 | R | NV | kW
| Max kW- Circuit 34 | 34 | 6665 |  | 5129 | UINT16 | 12178 | 12179 | Analog Input | 1106 | R | NV | kW
| Max kW- Circuit 35 | 35 | 6666 |  | 5130 | UINT16 | 12180 | 12181 | Analog Input | 1107 | R | NV | kW
| Max kW- Circuit 36 | 36 | 6667 |  | 5131 | UINT16 | 12182 | 12183 | Analog Input | 1108 | R | NV | kW
| Max kW- Circuit 37 | 37 | 6668 |  | 5132 | UINT16 | 12184 | 12185 | Analog Input | 1109 | R | NV | kW
| Max kW- Circuit 38 | 38 | 6669 |  | 5133 | UINT16 | 12186 | 12187 | Analog Input | 1110 | R | NV | kW
| Max kW- Circuit 39 | 39 | 6670 |  | 5134 | UINT16 | 12188 | 12189 | Analog Input | 1111 | R | NV | kW
| Max kW- Circuit 40 | 40 | 6671 |  | 5135 | UINT16 | 12190 | 12191 | Analog Input | 1112 | R | NV | kW
| Max kW- Circuit 41 | 41 | 6672 |  | 5136 | UINT16 | 12192 | 12193 | Analog Input | 1113 | R | NV | kW
| Max kW- Circuit 42 | 42 | 6673 |  | 5137 | UINT16 | 12194 | 12195 | Analog Input | 1114 | R | NV | kW
| Max kW- Circuit 43 | 43 | 6674 |  | 5138 | UINT16 | 12196 | 12197 | Analog Input | 1115 | R | NV | kW
| Max kW- Circuit 44 | 44 | 6675 |  | 5139 | UINT16 | 12198 | 12199 | Analog Input | 1116 | R | NV | kW
| Max kW- Circuit 45 | 45 | 6676 |  | 5140 | UINT16 | 12200 | 12201 | Analog Input | 1117 | R | NV | kW
| Max kW- Circuit 46 | 46 | 6677 |  | 5141 | UINT16 | 12202 | 12203 | Analog Input | 1118 | R | NV | kW
| Max kW- Circuit 47 | 47 | 6678 |  | 5142 | UINT16 | 12204 | 12205 | Analog Input | 1119 | R | NV | kW
| Max kW- Circuit 48 | 48 | 6679 |  | 5143 | UINT16 | 12206 | 12207 | Analog Input | 1120 | R | NV | kW
| Max kW- Circuit 49 | 49 | 6680 |  | 5144 | UINT16 | 12208 | 12209 | Analog Input | 1121 | R | NV | kW
| Max kW- Circuit 50 | 50 | 6681 |  | 5145 | UINT16 | 12210 | 12211 | Analog Input | 1122 | R | NV | kW
| Max kW- Circuit 51 | 51 | 6682 |  | 5146 | UINT16 | 12212 | 12213 | Analog Input | 1123 | R | NV | kW
| Max kW- Circuit 52 | 52 | 6683 |  | 5147 | UINT16 | 12214 | 12215 | Analog Input | 1124 | R | NV | kW
| Max kW- Circuit 53 | 53 | 6684 |  | 5148 | UINT16 | 12216 | 12217 | Analog Input | 1125 | R | NV | kW
| Max kW- Circuit 54 | 54 | 6685 |  | 5149 | UINT16 | 12218 | 12219 | Analog Input | 1126 | R | NV | kW
| Max kW- Circuit 55 | 55 | 6686 |  | 5150 | UINT16 | 12220 | 12221 | Analog Input | 1127 | R | NV | kW
| Max kW- Circuit 56 | 56 | 6687 |  | 5151 | UINT16 | 12222 | 12223 | Analog Input | 1128 | R | NV | kW
| Max kW- Circuit 57 | 57 | 6688 |  | 5152 | UINT16 | 12224 | 12225 | Analog Input | 1129 | R | NV | kW
| Max kW- Circuit 58 | 58 | 6689 |  | 5153 | UINT16 | 12226 | 12227 | Analog Input | 1130 | R | NV | kW
| Max kW- Circuit 59 | 59 | 6690 |  | 5154 | UINT16 | 12228 | 12229 | Analog Input | 1131 | R | NV | kW
| Max kW- Circuit 60 | 60 | 6691 |  | 5155 | UINT16 | 12230 | 12231 | Analog Input | 1132 | R | NV | kW
| Max kW- Circuit 61 | 61 | 6692 |  | 5156 | UINT16 | 12232 | 12233 | Analog Input | 1133 | R | NV | kW
| Max kW- Circuit 62 | 62 | 6693 |  | 5157 | UINT16 | 12234 | 12235 | Analog Input | 1134 | R | NV | kW
| Max kW- Circuit 63 | 63 | 6694 |  | 5158 | UINT16 | 12236 | 12237 | Analog Input | 1135 | R | NV | kW
| Max kW- Circuit 64 | 64 | 6695 |  | 5159 | UINT16 | 12238 | 12239 | Analog Input | 1136 | R | NV | kW
| Max kW- Circuit 65 | 65 | 6696 |  | 5160 | UINT16 | 12240 | 12241 | Analog Input | 1137 | R | NV | kW
| Max kW- Circuit 66 | 66 | 6697 |  | 5161 | UINT16 | 12242 | 12243 | Analog Input | 1138 | R | NV | kW
| Max kW- Circuit 67 | 67 | 6698 |  | 5162 | UINT16 | 12244 | 12245 | Analog Input | 1139 | R | NV | kW
| Max kW- Circuit 68 | 68 | 6699 |  | 5163 | UINT16 | 12246 | 12247 | Analog Input | 1140 | R | NV | kW
| Max kW- Circuit 69 | 69 | 6700 |  | 5164 | UINT16 | 12248 | 12249 | Analog Input | 1141 | R | NV | kW
| Max kW- Circuit 70 | 70 | 6701 |  | 5165 | UINT16 | 12250 | 12251 | Analog Input | 1142 | R | NV | kW
| Max kW- Circuit 71 | 71 | 6702 |  | 5166 | UINT16 | 12252 | 12253 | Analog Input | 1143 | R | NV | kW
| Max kW- Circuit 72 | 72 | 6703 |  | 5167 | UINT16 | 12254 | 12255 | Analog Input | 1144 | R | NV | kW
| Max kW- Circuit 73 | 73 | 6704 |  | 5168 | UINT16 | 12256 | 12257 | Analog Input | 1145 | R | NV | kW
| Max kW- Circuit 74 | 74 | 6705 |  | 5169 | UINT16 | 12258 | 12259 | Analog Input | 1146 | R | NV | kW
| Max kW- Circuit 75 | 75 | 6706 |  | 5170 | UINT16 | 12260 | 12261 | Analog Input | 1147 | R | NV | kW
| Max kW- Circuit 76 | 76 | 6707 |  | 5171 | UINT16 | 12262 | 12263 | Analog Input | 1148 | R | NV | kW
| Max kW- Circuit 77 | 77 | 6708 |  | 5172 | UINT16 | 12264 | 12265 | Analog Input | 1149 | R | NV | kW
| Max kW- Circuit 78 | 78 | 6709 |  | 5173 | UINT16 | 12266 | 12267 | Analog Input | 1150 | R | NV | kW
| Max kW- Circuit 79 | 79 | 6710 |  | 5174 | UINT16 | 12268 | 12269 | Analog Input | 1151 | R | NV | kW
| Max kW- Circuit 80 | 80 | 6711 |  | 5175 | UINT16 | 12270 | 12271 | Analog Input | 1152 | R | NV | kW
| Max kW- Circuit 81 | 81 | 6712 |  | 5176 | UINT16 | 12272 | 12273 | Analog Input | 1153 | R | NV | kW
| Max kW- Circuit 82 | 82 | 6713 |  | 5177 | UINT16 | 12274 | 12275 | Analog Input | 1154 | R | NV | kW
| Max kW- Circuit 83 | 83 | 6714 |  | 5178 | UINT16 | 12276 | 12277 | Analog Input | 1155 | R | NV | kW
| Max kW- Circuit 84 | 84 | 6715 |  | 5179 | UINT16 | 12278 | 12279 | Analog Input | 1156 | R | NV | kW
| Max kW- Circuit 85 | 85 | 6716 |  | 5180 | UINT16 | 12280 | 12281 | Analog Input | 1157 | R | NV | kW
| Max kW- Circuit 86 | 86 | 6717 |  | 5181 | UINT16 | 12282 | 12283 | Analog Input | 1158 | R | NV | kW
| Max kW- Circuit 87 | 87 | 6718 |  | 5182 | UINT16 | 12284 | 12285 | Analog Input | 1159 | R | NV | kW
| Max kW- Circuit 88 | 88 | 6719 |  | 5183 | UINT16 | 12286 | 12287 | Analog Input | 1160 | R | NV | kW
| Max kW- Circuit 89 | 89 | 6720 |  | 5184 | UINT16 | 12288 | 12289 | Analog Input | 1161 | R | NV | kW
| Max kW- Circuit 90 | 90 | 6721 |  | 5185 | UINT16 | 12290 | 12291 | Analog Input | 1162 | R | NV | kW
| Max kW- Circuit 91 | 91 | 6722 |  | 5186 | UINT16 | 12292 | 12293 | Analog Input | 1163 | R | NV | kW
| Max kW- Circuit 92 | 92 | 6723 |  | 5187 | UINT16 | 12294 | 12295 | Analog Input | 1164 | R | NV | kW
| Max kW- Circuit 93 | 93 | 6724 |  | 5188 | UINT16 | 12296 | 12297 | Analog Input | 1165 | R | NV | kW
| Max kW- Circuit 94 | 94 | 6725 |  | 5189 | UINT16 | 12298 | 12299 | Analog Input | 1166 | R | NV | kW
| Max kW- Circuit 95 | 95 | 6726 |  | 5190 | UINT16 | 12300 | 12301 | Analog Input | 1167 | R | NV | kW
| Max kW- Circuit 96 | 96 | 6727 |  | 5191 | UINT16 | 12302 | 12303 | Analog Input | 1168 | R | NV | kW
| Current Demand |  | 6728 | 6823 | Current | UINT16 | 12304 | 12495 | Analog Input | 1169 - 1264 | R |  | Amps
| Current Demand- Circuit 1 | 1 | 6728 |  | 5192 | UINT16 | 12304 | 12305 | Analog Input | 1169 | R |  | Amps
| Current Demand- Circuit 2 | 2 | 6729 |  | 5193 | UINT16 | 12306 | 12307 | Analog Input | 1170 | R |  | Amps
| Current Demand- Circuit 3 | 3 | 6730 |  | 5194 | UINT16 | 12308 | 12309 | Analog Input | 1171 | R |  | Amps
| Current Demand- Circuit 4 | 4 | 6731 |  | 5195 | UINT16 | 12310 | 12311 | Analog Input | 1172 | R |  | Amps
| Current Demand- Circuit 5 | 5 | 6732 |  | 5196 | UINT16 | 12312 | 12313 | Analog Input | 1173 | R |  | Amps
| Current Demand- Circuit 6 | 6 | 6733 |  | 5197 | UINT16 | 12314 | 12315 | Analog Input | 1174 | R |  | Amps
| Current Demand- Circuit 7 | 7 | 6734 |  | 5198 | UINT16 | 12316 | 12317 | Analog Input | 1175 | R |  | Amps
| Current Demand- Circuit 8 | 8 | 6735 |  | 5199 | UINT16 | 12318 | 12319 | Analog Input | 1176 | R |  | Amps
| Current Demand- Circuit 9 | 9 | 6736 |  | 5200 | UINT16 | 12320 | 12321 | Analog Input | 1177 | R |  | Amps
| Current Demand- Circuit 10 | 10 | 6737 |  | 5201 | UINT16 | 12322 | 12323 | Analog Input | 1178 | R |  | Amps
| Current Demand- Circuit 11 | 11 | 6738 |  | 5202 | UINT16 | 12324 | 12325 | Analog Input | 1179 | R |  | Amps
| Current Demand- Circuit 12 | 12 | 6739 |  | 5203 | UINT16 | 12326 | 12327 | Analog Input | 1180 | R |  | Amps
| Current Demand- Circuit 13 | 13 | 6740 |  | 5204 | UINT16 | 12328 | 12329 | Analog Input | 1181 | R |  | Amps
| Current Demand- Circuit 14 | 14 | 6741 |  | 5205 | UINT16 | 12330 | 12331 | Analog Input | 1182 | R |  | Amps
| Current Demand- Circuit 15 | 15 | 6742 |  | 5206 | UINT16 | 12332 | 12333 | Analog Input | 1183 | R |  | Amps
| Current Demand- Circuit 16 | 16 | 6743 |  | 5207 | UINT16 | 12334 | 12335 | Analog Input | 1184 | R |  | Amps
| Current Demand- Circuit 17 | 17 | 6744 |  | 5208 | UINT16 | 12336 | 12337 | Analog Input | 1185 | R |  | Amps
| Current Demand- Circuit 18 | 18 | 6745 |  | 5209 | UINT16 | 12338 | 12339 | Analog Input | 1186 | R |  | Amps
| Current Demand- Circuit 19 | 19 | 6746 |  | 5210 | UINT16 | 12340 | 12341 | Analog Input | 1187 | R |  | Amps
| Current Demand- Circuit 20 | 20 | 6747 |  | 5211 | UINT16 | 12342 | 12343 | Analog Input | 1188 | R |  | Amps
| Current Demand- Circuit 21 | 21 | 6748 |  | 5212 | UINT16 | 12344 | 12345 | Analog Input | 1189 | R |  | Amps
| Current Demand- Circuit 22 | 22 | 6749 |  | 5213 | UINT16 | 12346 | 12347 | Analog Input | 1190 | R |  | Amps
| Current Demand- Circuit 23 | 23 | 6750 |  | 5214 | UINT16 | 12348 | 12349 | Analog Input | 1191 | R |  | Amps
| Current Demand- Circuit 24 | 24 | 6751 |  | 5215 | UINT16 | 12350 | 12351 | Analog Input | 1192 | R |  | Amps
| Current Demand- Circuit 25 | 25 | 6752 |  | 5216 | UINT16 | 12352 | 12353 | Analog Input | 1193 | R |  | Amps
| Current Demand- Circuit 26 | 26 | 6753 |  | 5217 | UINT16 | 12354 | 12355 | Analog Input | 1194 | R |  | Amps
| Current Demand- Circuit 27 | 27 | 6754 |  | 5218 | UINT16 | 12356 | 12357 | Analog Input | 1195 | R |  | Amps
| Current Demand- Circuit 28 | 28 | 6755 |  | 5219 | UINT16 | 12358 | 12359 | Analog Input | 1196 | R |  | Amps
| Current Demand- Circuit 29 | 29 | 6756 |  | 5220 | UINT16 | 12360 | 12361 | Analog Input | 1197 | R |  | Amps
| Current Demand- Circuit 30 | 30 | 6757 |  | 5221 | UINT16 | 12362 | 12363 | Analog Input | 1198 | R |  | Amps
| Current Demand- Circuit 31 | 31 | 6758 |  | 5222 | UINT16 | 12364 | 12365 | Analog Input | 1199 | R |  | Amps
| Current Demand- Circuit 32 | 32 | 6759 |  | 5223 | UINT16 | 12366 | 12367 | Analog Input | 1200 | R |  | Amps
| Current Demand- Circuit 33 | 33 | 6760 |  | 5224 | UINT16 | 12368 | 12369 | Analog Input | 1201 | R |  | Amps
| Current Demand- Circuit 34 | 34 | 6761 |  | 5225 | UINT16 | 12370 | 12371 | Analog Input | 1202 | R |  | Amps
| Current Demand- Circuit 35 | 35 | 6762 |  | 5226 | UINT16 | 12372 | 12373 | Analog Input | 1203 | R |  | Amps
| Current Demand- Circuit 36 | 36 | 6763 |  | 5227 | UINT16 | 12374 | 12375 | Analog Input | 1204 | R |  | Amps
| Current Demand- Circuit 37 | 37 | 6764 |  | 5228 | UINT16 | 12376 | 12377 | Analog Input | 1205 | R |  | Amps
| Current Demand- Circuit 38 | 38 | 6765 |  | 5229 | UINT16 | 12378 | 12379 | Analog Input | 1206 | R |  | Amps
| Current Demand- Circuit 39 | 39 | 6766 |  | 5230 | UINT16 | 12380 | 12381 | Analog Input | 1207 | R |  | Amps
| Current Demand- Circuit 40 | 40 | 6767 |  | 5231 | UINT16 | 12382 | 12383 | Analog Input | 1208 | R |  | Amps
| Current Demand- Circuit 41 | 41 | 6768 |  | 5232 | UINT16 | 12384 | 12385 | Analog Input | 1209 | R |  | Amps
| Current Demand- Circuit 42 | 42 | 6769 |  | 5233 | UINT16 | 12386 | 12387 | Analog Input | 1210 | R |  | Amps
| Current Demand- Circuit 43 | 43 | 6770 |  | 5234 | UINT16 | 12388 | 12389 | Analog Input | 1211 | R |  | Amps
| Current Demand- Circuit 44 | 44 | 6771 |  | 5235 | UINT16 | 12390 | 12391 | Analog Input | 1212 | R |  | Amps
| Current Demand- Circuit 45 | 45 | 6772 |  | 5236 | UINT16 | 12392 | 12393 | Analog Input | 1213 | R |  | Amps
| Current Demand- Circuit 46 | 46 | 6773 |  | 5237 | UINT16 | 12394 | 12395 | Analog Input | 1214 | R |  | Amps
| Current Demand- Circuit 47 | 47 | 6774 |  | 5238 | UINT16 | 12396 | 12397 | Analog Input | 1215 | R |  | Amps
| Current Demand- Circuit 48 | 48 | 6775 |  | 5239 | UINT16 | 12398 | 12399 | Analog Input | 1216 | R |  | Amps
| Current Demand- Circuit 49 | 49 | 6776 |  | 5240 | UINT16 | 12400 | 12401 | Analog Input | 1217 | R |  | Amps
| Current Demand- Circuit 50 | 50 | 6777 |  | 5241 | UINT16 | 12402 | 12403 | Analog Input | 1218 | R |  | Amps
| Current Demand- Circuit 51 | 51 | 6778 |  | 5242 | UINT16 | 12404 | 12405 | Analog Input | 1219 | R |  | Amps
| Current Demand- Circuit 52 | 52 | 6779 |  | 5243 | UINT16 | 12406 | 12407 | Analog Input | 1220 | R |  | Amps
| Current Demand- Circuit 53 | 53 | 6780 |  | 5244 | UINT16 | 12408 | 12409 | Analog Input | 1221 | R |  | Amps
| Current Demand- Circuit 54 | 54 | 6781 |  | 5245 | UINT16 | 12410 | 12411 | Analog Input | 1222 | R |  | Amps
| Current Demand- Circuit 55 | 55 | 6782 |  | 5246 | UINT16 | 12412 | 12413 | Analog Input | 1223 | R |  | Amps
| Current Demand- Circuit 56 | 56 | 6783 |  | 5247 | UINT16 | 12414 | 12415 | Analog Input | 1224 | R |  | Amps
| Current Demand- Circuit 57 | 57 | 6784 |  | 5248 | UINT16 | 12416 | 12417 | Analog Input | 1225 | R |  | Amps
| Current Demand- Circuit 58 | 58 | 6785 |  | 5249 | UINT16 | 12418 | 12419 | Analog Input | 1226 | R |  | Amps
| Current Demand- Circuit 59 | 59 | 6786 |  | 5250 | UINT16 | 12420 | 12421 | Analog Input | 1227 | R |  | Amps
| Current Demand- Circuit 60 | 60 | 6787 |  | 5251 | UINT16 | 12422 | 12423 | Analog Input | 1228 | R |  | Amps
| Current Demand- Circuit 61 | 61 | 6788 |  | 5252 | UINT16 | 12424 | 12425 | Analog Input | 1229 | R |  | Amps
| Current Demand- Circuit 62 | 62 | 6789 |  | 5253 | UINT16 | 12426 | 12427 | Analog Input | 1230 | R |  | Amps
| Current Demand- Circuit 63 | 63 | 6790 |  | 5254 | UINT16 | 12428 | 12429 | Analog Input | 1231 | R |  | Amps
| Current Demand- Circuit 64 | 64 | 6791 |  | 5255 | UINT16 | 12430 | 12431 | Analog Input | 1232 | R |  | Amps
| Current Demand- Circuit 65 | 65 | 6792 |  | 5256 | UINT16 | 12432 | 12433 | Analog Input | 1233 | R |  | Amps
| Current Demand- Circuit 66 | 66 | 6793 |  | 5257 | UINT16 | 12434 | 12435 | Analog Input | 1234 | R |  | Amps
| Current Demand- Circuit 67 | 67 | 6794 |  | 5258 | UINT16 | 12436 | 12437 | Analog Input | 1235 | R |  | Amps
| Current Demand- Circuit 68 | 68 | 6795 |  | 5259 | UINT16 | 12438 | 12439 | Analog Input | 1236 | R |  | Amps
| Current Demand- Circuit 69 | 69 | 6796 |  | 5260 | UINT16 | 12440 | 12441 | Analog Input | 1237 | R |  | Amps
| Current Demand- Circuit 70 | 70 | 6797 |  | 5261 | UINT16 | 12442 | 12443 | Analog Input | 1238 | R |  | Amps
| Current Demand- Circuit 71 | 71 | 6798 |  | 5262 | UINT16 | 12444 | 12445 | Analog Input | 1239 | R |  | Amps
| Current Demand- Circuit 72 | 72 | 6799 |  | 5263 | UINT16 | 12446 | 12447 | Analog Input | 1240 | R |  | Amps
| Current Demand- Circuit 73 | 73 | 6800 |  | 5264 | UINT16 | 12448 | 12449 | Analog Input | 1241 | R |  | Amps
| Current Demand- Circuit 74 | 74 | 6801 |  | 5265 | UINT16 | 12450 | 12451 | Analog Input | 1242 | R |  | Amps
| Current Demand- Circuit 75 | 75 | 6802 |  | 5266 | UINT16 | 12452 | 12453 | Analog Input | 1243 | R |  | Amps
| Current Demand- Circuit 76 | 76 | 6803 |  | 5267 | UINT16 | 12454 | 12455 | Analog Input | 1244 | R |  | Amps
| Current Demand- Circuit 77 | 77 | 6804 |  | 5268 | UINT16 | 12456 | 12457 | Analog Input | 1245 | R |  | Amps
| Current Demand- Circuit 78 | 78 | 6805 |  | 5269 | UINT16 | 12458 | 12459 | Analog Input | 1246 | R |  | Amps
| Current Demand- Circuit 79 | 79 | 6806 |  | 5270 | UINT16 | 12460 | 12461 | Analog Input | 1247 | R |  | Amps
| Current Demand- Circuit 80 | 80 | 6807 |  | 5271 | UINT16 | 12462 | 12463 | Analog Input | 1248 | R |  | Amps
| Current Demand- Circuit 81 | 81 | 6808 |  | 5272 | UINT16 | 12464 | 12465 | Analog Input | 1249 | R |  | Amps
| Current Demand- Circuit 82 | 82 | 6809 |  | 5273 | UINT16 | 12466 | 12467 | Analog Input | 1250 | R |  | Amps
| Current Demand- Circuit 83 | 83 | 6810 |  | 5274 | UINT16 | 12468 | 12469 | Analog Input | 1251 | R |  | Amps
| Current Demand- Circuit 84 | 84 | 6811 |  | 5275 | UINT16 | 12470 | 12471 | Analog Input | 1252 | R |  | Amps
| Current Demand- Circuit 85 | 85 | 6812 |  | 5276 | UINT16 | 12472 | 12473 | Analog Input | 1253 | R |  | Amps
| Current Demand- Circuit 86 | 86 | 6813 |  | 5277 | UINT16 | 12474 | 12475 | Analog Input | 1254 | R |  | Amps
| Current Demand- Circuit 87 | 87 | 6814 |  | 5278 | UINT16 | 12476 | 12477 | Analog Input | 1255 | R |  | Amps
| Current Demand- Circuit 88 | 88 | 6815 |  | 5279 | UINT16 | 12478 | 12479 | Analog Input | 1256 | R |  | Amps
| Current Demand- Circuit 89 | 89 | 6816 |  | 5280 | UINT16 | 12480 | 12481 | Analog Input | 1257 | R |  | Amps
| Current Demand- Circuit 90 | 90 | 6817 |  | 5281 | UINT16 | 12482 | 12483 | Analog Input | 1258 | R |  | Amps
| Current Demand- Circuit 91 | 91 | 6818 |  | 5282 | UINT16 | 12484 | 12485 | Analog Input | 1259 | R |  | Amps
| Current Demand- Circuit 92 | 92 | 6819 |  | 5283 | UINT16 | 12486 | 12487 | Analog Input | 1260 | R |  | Amps
| Current Demand- Circuit 93 | 93 | 6820 |  | 5284 | UINT16 | 12488 | 12489 | Analog Input | 1261 | R |  | Amps
| Current Demand- Circuit 94 | 94 | 6821 |  | 5285 | UINT16 | 12490 | 12491 | Analog Input | 1262 | R |  | Amps
| Current Demand- Circuit 95 | 95 | 6822 |  | 5286 | UINT16 | 12492 | 12493 | Analog Input | 1263 | R |  | Amps
| Current Demand- Circuit 96 | 96 | 6823 |  | 5287 | UINT16 | 12494 | 12495 | Analog Input | 1264 | R |  | Amps
| kW Demand |  | 6824 | 6919 | Power | UINT16 | 12496 | 12687 | Analog Input | 1265 - 1360 | R |  | kW
| kW Demand- Circuit 1 | 1 | 6824 |  | 5096 | UINT16 | 12496 | 12497 | Analog Input | 1265 | R |  | kW
| kW Demand- Circuit 2 | 2 | 6825 |  | 5097 | UINT16 | 12498 | 12499 | Analog Input | 1266 | R |  | kW
| kW Demand- Circuit 3 | 3 | 6826 |  | 5098 | UINT16 | 12500 | 12501 | Analog Input | 1267 | R |  | kW
| kW Demand- Circuit 4 | 4 | 6827 |  | 5099 | UINT16 | 12502 | 12503 | Analog Input | 1268 | R |  | kW
| kW Demand- Circuit 5 | 5 | 6828 |  | 5100 | UINT16 | 12504 | 12505 | Analog Input | 1269 | R |  | kW
| kW Demand- Circuit 6 | 6 | 6829 |  | 5101 | UINT16 | 12506 | 12507 | Analog Input | 1270 | R |  | kW
| kW Demand- Circuit 7 | 7 | 6830 |  | 5102 | UINT16 | 12508 | 12509 | Analog Input | 1271 | R |  | kW
| kW Demand- Circuit 8 | 8 | 6831 |  | 5103 | UINT16 | 12510 | 12511 | Analog Input | 1272 | R |  | kW
| kW Demand- Circuit 9 | 9 | 6832 |  | 5104 | UINT16 | 12512 | 12513 | Analog Input | 1273 | R |  | kW
| kW Demand- Circuit 10 | 10 | 6833 |  | 5105 | UINT16 | 12514 | 12515 | Analog Input | 1274 | R |  | kW
| kW Demand- Circuit 11 | 11 | 6834 |  | 5106 | UINT16 | 12516 | 12517 | Analog Input | 1275 | R |  | kW
| kW Demand- Circuit 12 | 12 | 6835 |  | 5107 | UINT16 | 12518 | 12519 | Analog Input | 1276 | R |  | kW
| kW Demand- Circuit 13 | 13 | 6836 |  | 5108 | UINT16 | 12520 | 12521 | Analog Input | 1277 | R |  | kW
| kW Demand- Circuit 14 | 14 | 6837 |  | 5109 | UINT16 | 12522 | 12523 | Analog Input | 1278 | R |  | kW
| kW Demand- Circuit 15 | 15 | 6838 |  | 5110 | UINT16 | 12524 | 12525 | Analog Input | 1279 | R |  | kW
| kW Demand- Circuit 16 | 16 | 6839 |  | 5111 | UINT16 | 12526 | 12527 | Analog Input | 1280 | R |  | kW
| kW Demand- Circuit 17 | 17 | 6840 |  | 5112 | UINT16 | 12528 | 12529 | Analog Input | 1281 | R |  | kW
| kW Demand- Circuit 18 | 18 | 6841 |  | 5113 | UINT16 | 12530 | 12531 | Analog Input | 1282 | R |  | kW
| kW Demand- Circuit 19 | 19 | 6842 |  | 5114 | UINT16 | 12532 | 12533 | Analog Input | 1283 | R |  | kW
| kW Demand- Circuit 20 | 20 | 6843 |  | 5115 | UINT16 | 12534 | 12535 | Analog Input | 1284 | R |  | kW
| kW Demand- Circuit 21 | 21 | 6844 |  | 5116 | UINT16 | 12536 | 12537 | Analog Input | 1285 | R |  | kW
| kW Demand- Circuit 22 | 22 | 6845 |  | 5117 | UINT16 | 12538 | 12539 | Analog Input | 1286 | R |  | kW
| kW Demand- Circuit 23 | 23 | 6846 |  | 5118 | UINT16 | 12540 | 12541 | Analog Input | 1287 | R |  | kW
| kW Demand- Circuit 24 | 24 | 6847 |  | 5119 | UINT16 | 12542 | 12543 | Analog Input | 1288 | R |  | kW
| kW Demand- Circuit 25 | 25 | 6848 |  | 5120 | UINT16 | 12544 | 12545 | Analog Input | 1289 | R |  | kW
| kW Demand- Circuit 26 | 26 | 6849 |  | 5121 | UINT16 | 12546 | 12547 | Analog Input | 1290 | R |  | kW
| kW Demand- Circuit 27 | 27 | 6850 |  | 5122 | UINT16 | 12548 | 12549 | Analog Input | 1291 | R |  | kW
| kW Demand- Circuit 28 | 28 | 6851 |  | 5123 | UINT16 | 12550 | 12551 | Analog Input | 1292 | R |  | kW
| kW Demand- Circuit 29 | 29 | 6852 |  | 5124 | UINT16 | 12552 | 12553 | Analog Input | 1293 | R |  | kW
| kW Demand- Circuit 30 | 30 | 6853 |  | 5125 | UINT16 | 12554 | 12555 | Analog Input | 1294 | R |  | kW
| kW Demand- Circuit 31 | 31 | 6854 |  | 5126 | UINT16 | 12556 | 12557 | Analog Input | 1295 | R |  | kW
| kW Demand- Circuit 32 | 32 | 6855 |  | 5127 | UINT16 | 12558 | 12559 | Analog Input | 1296 | R |  | kW
| kW Demand- Circuit 33 | 33 | 6856 |  | 5128 | UINT16 | 12560 | 12561 | Analog Input | 1297 | R |  | kW
| kW Demand- Circuit 34 | 34 | 6857 |  | 5129 | UINT16 | 12562 | 12563 | Analog Input | 1298 | R |  | kW
| kW Demand- Circuit 35 | 35 | 6858 |  | 5130 | UINT16 | 12564 | 12565 | Analog Input | 1299 | R |  | kW
| kW Demand- Circuit 36 | 36 | 6859 |  | 5131 | UINT16 | 12566 | 12567 | Analog Input | 1300 | R |  | kW
| kW Demand- Circuit 37 | 37 | 6860 |  | 5132 | UINT16 | 12568 | 12569 | Analog Input | 1301 | R |  | kW
| kW Demand- Circuit 38 | 38 | 6861 |  | 5133 | UINT16 | 12570 | 12571 | Analog Input | 1302 | R |  | kW
| kW Demand- Circuit 39 | 39 | 6862 |  | 5134 | UINT16 | 12572 | 12573 | Analog Input | 1303 | R |  | kW
| kW Demand- Circuit 40 | 40 | 6863 |  | 5135 | UINT16 | 12574 | 12575 | Analog Input | 1304 | R |  | kW
| kW Demand- Circuit 41 | 41 | 6864 |  | 5136 | UINT16 | 12576 | 12577 | Analog Input | 1305 | R |  | kW
| kW Demand- Circuit 42 | 42 | 6865 |  | 5137 | UINT16 | 12578 | 12579 | Analog Input | 1306 | R |  | kW
| kW Demand- Circuit 43 | 43 | 6866 |  | 5138 | UINT16 | 12580 | 12581 | Analog Input | 1307 | R |  | kW
| kW Demand- Circuit 44 | 44 | 6867 |  | 5139 | UINT16 | 12582 | 12583 | Analog Input | 1308 | R |  | kW
| kW Demand- Circuit 45 | 45 | 6868 |  | 5140 | UINT16 | 12584 | 12585 | Analog Input | 1309 | R |  | kW
| kW Demand- Circuit 46 | 46 | 6869 |  | 5141 | UINT16 | 12586 | 12587 | Analog Input | 1310 | R |  | kW
| kW Demand- Circuit 47 | 47 | 6870 |  | 5142 | UINT16 | 12588 | 12589 | Analog Input | 1311 | R |  | kW
| kW Demand- Circuit 48 | 48 | 6871 |  | 5143 | UINT16 | 12590 | 12591 | Analog Input | 1312 | R |  | kW
| kW Demand- Circuit 49 | 49 | 6872 |  | 5144 | UINT16 | 12592 | 12593 | Analog Input | 1313 | R |  | kW
| kW Demand- Circuit 50 | 50 | 6873 |  | 5145 | UINT16 | 12594 | 12595 | Analog Input | 1314 | R |  | kW
| kW Demand- Circuit 51 | 51 | 6874 |  | 5146 | UINT16 | 12596 | 12597 | Analog Input | 1315 | R |  | kW
| kW Demand- Circuit 52 | 52 | 6875 |  | 5147 | UINT16 | 12598 | 12599 | Analog Input | 1316 | R |  | kW
| kW Demand- Circuit 53 | 53 | 6876 |  | 5148 | UINT16 | 12600 | 12601 | Analog Input | 1317 | R |  | kW
| kW Demand- Circuit 54 | 54 | 6877 |  | 5149 | UINT16 | 12602 | 12603 | Analog Input | 1318 | R |  | kW
| kW Demand- Circuit 55 | 55 | 6878 |  | 5150 | UINT16 | 12604 | 12605 | Analog Input | 1319 | R |  | kW
| kW Demand- Circuit 56 | 56 | 6879 |  | 5151 | UINT16 | 12606 | 12607 | Analog Input | 1320 | R |  | kW
| kW Demand- Circuit 57 | 57 | 6880 |  | 5152 | UINT16 | 12608 | 12609 | Analog Input | 1321 | R |  | kW
| kW Demand- Circuit 58 | 58 | 6881 |  | 5153 | UINT16 | 12610 | 12611 | Analog Input | 1322 | R |  | kW
| kW Demand- Circuit 59 | 59 | 6882 |  | 5154 | UINT16 | 12612 | 12613 | Analog Input | 1323 | R |  | kW
| kW Demand- Circuit 60 | 60 | 6883 |  | 5155 | UINT16 | 12614 | 12615 | Analog Input | 1324 | R |  | kW
| kW Demand- Circuit 61 | 61 | 6884 |  | 5156 | UINT16 | 12616 | 12617 | Analog Input | 1325 | R |  | kW
| kW Demand- Circuit 62 | 62 | 6885 |  | 5157 | UINT16 | 12618 | 12619 | Analog Input | 1326 | R |  | kW
| kW Demand- Circuit 63 | 63 | 6886 |  | 5158 | UINT16 | 12620 | 12621 | Analog Input | 1327 | R |  | kW
| kW Demand- Circuit 64 | 64 | 6887 |  | 5159 | UINT16 | 12622 | 12623 | Analog Input | 1328 | R |  | kW
| kW Demand- Circuit 65 | 65 | 6888 |  | 5160 | UINT16 | 12624 | 12625 | Analog Input | 1329 | R |  | kW
| kW Demand- Circuit 66 | 66 | 6889 |  | 5161 | UINT16 | 12626 | 12627 | Analog Input | 1330 | R |  | kW
| kW Demand- Circuit 67 | 67 | 6890 |  | 5162 | UINT16 | 12628 | 12629 | Analog Input | 1331 | R |  | kW
| kW Demand- Circuit 68 | 68 | 6891 |  | 5163 | UINT16 | 12630 | 12631 | Analog Input | 1332 | R |  | kW
| kW Demand- Circuit 69 | 69 | 6892 |  | 5164 | UINT16 | 12632 | 12633 | Analog Input | 1333 | R |  | kW
| kW Demand- Circuit 70 | 70 | 6893 |  | 5165 | UINT16 | 12634 | 12635 | Analog Input | 1334 | R |  | kW
| kW Demand- Circuit 71 | 71 | 6894 |  | 5166 | UINT16 | 12636 | 12637 | Analog Input | 1335 | R |  | kW
| kW Demand- Circuit 72 | 72 | 6895 |  | 5167 | UINT16 | 12638 | 12639 | Analog Input | 1336 | R |  | kW
| kW Demand- Circuit 73 | 73 | 6896 |  | 5168 | UINT16 | 12640 | 12641 | Analog Input | 1337 | R |  | kW
| kW Demand- Circuit 74 | 74 | 6897 |  | 5169 | UINT16 | 12642 | 12643 | Analog Input | 1338 | R |  | kW
| kW Demand- Circuit 75 | 75 | 6898 |  | 5170 | UINT16 | 12644 | 12645 | Analog Input | 1339 | R |  | kW
| kW Demand- Circuit 76 | 76 | 6899 |  | 5171 | UINT16 | 12646 | 12647 | Analog Input | 1340 | R |  | kW
| kW Demand- Circuit 77 | 77 | 6900 |  | 5172 | UINT16 | 12648 | 12649 | Analog Input | 1341 | R |  | kW
| kW Demand- Circuit 78 | 78 | 6901 |  | 5173 | UINT16 | 12650 | 12651 | Analog Input | 1342 | R |  | kW
| kW Demand- Circuit 79 | 79 | 6902 |  | 5174 | UINT16 | 12652 | 12653 | Analog Input | 1343 | R |  | kW
| kW Demand- Circuit 80 | 80 | 6903 |  | 5175 | UINT16 | 12654 | 12655 | Analog Input | 1344 | R |  | kW
| kW Demand- Circuit 81 | 81 | 6904 |  | 5176 | UINT16 | 12656 | 12657 | Analog Input | 1345 | R |  | kW
| kW Demand- Circuit 82 | 82 | 6905 |  | 5177 | UINT16 | 12658 | 12659 | Analog Input | 1346 | R |  | kW
| kW Demand- Circuit 83 | 83 | 6906 |  | 5178 | UINT16 | 12660 | 12661 | Analog Input | 1347 | R |  | kW
| kW Demand- Circuit 84 | 84 | 6907 |  | 5179 | UINT16 | 12662 | 12663 | Analog Input | 1348 | R |  | kW
| kW Demand- Circuit 85 | 85 | 6908 |  | 5180 | UINT16 | 12664 | 12665 | Analog Input | 1349 | R |  | kW
| kW Demand- Circuit 86 | 86 | 6909 |  | 5181 | UINT16 | 12666 | 12667 | Analog Input | 1350 | R |  | kW
| kW Demand- Circuit 87 | 87 | 6910 |  | 5182 | UINT16 | 12668 | 12669 | Analog Input | 1351 | R |  | kW
| kW Demand- Circuit 88 | 88 | 6911 |  | 5183 | UINT16 | 12670 | 12671 | Analog Input | 1352 | R |  | kW
| kW Demand- Circuit 89 | 89 | 6912 |  | 5184 | UINT16 | 12672 | 12673 | Analog Input | 1353 | R |  | kW
| kW Demand- Circuit 90 | 90 | 6913 |  | 5185 | UINT16 | 12674 | 12675 | Analog Input | 1354 | R |  | kW
| kW Demand- Circuit 91 | 91 | 6914 |  | 5186 | UINT16 | 12676 | 12677 | Analog Input | 1355 | R |  | kW
| kW Demand- Circuit 92 | 92 | 6915 |  | 5187 | UINT16 | 12678 | 12679 | Analog Input | 1356 | R |  | kW
| kW Demand- Circuit 93 | 93 | 6916 |  | 5188 | UINT16 | 12680 | 12681 | Analog Input | 1357 | R |  | kW
| kW Demand- Circuit 94 | 94 | 6917 |  | 5189 | UINT16 | 12682 | 12683 | Analog Input | 1358 | R |  | kW
| kW Demand- Circuit 95 | 95 | 6918 |  | 5190 | UINT16 | 12684 | 12685 | Analog Input | 1359 | R |  | kW
| kW Demand- Circuit 96 | 96 | 6919 |  | 5191 | UINT16 | 12686 | 12687 | Analog Input | 1360 | R |  | kW
| Max Current Demand |  | 6920 | 7015 | Current | UINT16 | 12688 | 12879 | Analog Input | 1361 - 1456 | R | NV | Amps
| Max Current Demand - Circuit 1 | 1 | 6920 |  | 5192 | UINT16 | 12688 | 12689 | Analog Input | 1361 | R | NV | Amps
| Max Current Demand - Circuit 2 | 2 | 6921 |  | 5193 | UINT16 | 12690 | 12691 | Analog Input | 1362 | R | NV | Amps
| Max Current Demand - Circuit 3 | 3 | 6922 |  | 5194 | UINT16 | 12692 | 12693 | Analog Input | 1363 | R | NV | Amps
| Max Current Demand - Circuit 4 | 4 | 6923 |  | 5195 | UINT16 | 12694 | 12695 | Analog Input | 1364 | R | NV | Amps
| Max Current Demand - Circuit 5 | 5 | 6924 |  | 5196 | UINT16 | 12696 | 12697 | Analog Input | 1365 | R | NV | Amps
| Max Current Demand - Circuit 6 | 6 | 6925 |  | 5197 | UINT16 | 12698 | 12699 | Analog Input | 1366 | R | NV | Amps
| Max Current Demand - Circuit 7 | 7 | 6926 |  | 5198 | UINT16 | 12700 | 12701 | Analog Input | 1367 | R | NV | Amps
| Max Current Demand - Circuit 8 | 8 | 6927 |  | 5199 | UINT16 | 12702 | 12703 | Analog Input | 1368 | R | NV | Amps
| Max Current Demand - Circuit 9 | 9 | 6928 |  | 5200 | UINT16 | 12704 | 12705 | Analog Input | 1369 | R | NV | Amps
| Max Current Demand - Circuit 10 | 10 | 6929 |  | 5201 | UINT16 | 12706 | 12707 | Analog Input | 1370 | R | NV | Amps
| Max Current Demand - Circuit 11 | 11 | 6930 |  | 5202 | UINT16 | 12708 | 12709 | Analog Input | 1371 | R | NV | Amps
| Max Current Demand - Circuit 12 | 12 | 6931 |  | 5203 | UINT16 | 12710 | 12711 | Analog Input | 1372 | R | NV | Amps
| Max Current Demand - Circuit 13 | 13 | 6932 |  | 5204 | UINT16 | 12712 | 12713 | Analog Input | 1373 | R | NV | Amps
| Max Current Demand - Circuit 14 | 14 | 6933 |  | 5205 | UINT16 | 12714 | 12715 | Analog Input | 1374 | R | NV | Amps
| Max Current Demand - Circuit 15 | 15 | 6934 |  | 5206 | UINT16 | 12716 | 12717 | Analog Input | 1375 | R | NV | Amps
| Max Current Demand - Circuit 16 | 16 | 6935 |  | 5207 | UINT16 | 12718 | 12719 | Analog Input | 1376 | R | NV | Amps
| Max Current Demand - Circuit 17 | 17 | 6936 |  | 5208 | UINT16 | 12720 | 12721 | Analog Input | 1377 | R | NV | Amps
| Max Current Demand - Circuit 18 | 18 | 6937 |  | 5209 | UINT16 | 12722 | 12723 | Analog Input | 1378 | R | NV | Amps
| Max Current Demand - Circuit 19 | 19 | 6938 |  | 5210 | UINT16 | 12724 | 12725 | Analog Input | 1379 | R | NV | Amps
| Max Current Demand - Circuit 20 | 20 | 6939 |  | 5211 | UINT16 | 12726 | 12727 | Analog Input | 1380 | R | NV | Amps
| Max Current Demand - Circuit 21 | 21 | 6940 |  | 5212 | UINT16 | 12728 | 12729 | Analog Input | 1381 | R | NV | Amps
| Max Current Demand - Circuit 22 | 22 | 6941 |  | 5213 | UINT16 | 12730 | 12731 | Analog Input | 1382 | R | NV | Amps
| Max Current Demand - Circuit 23 | 23 | 6942 |  | 5214 | UINT16 | 12732 | 12733 | Analog Input | 1383 | R | NV | Amps
| Max Current Demand - Circuit 24 | 24 | 6943 |  | 5215 | UINT16 | 12734 | 12735 | Analog Input | 1384 | R | NV | Amps
| Max Current Demand - Circuit 25 | 25 | 6944 |  | 5216 | UINT16 | 12736 | 12737 | Analog Input | 1385 | R | NV | Amps
| Max Current Demand - Circuit 26 | 26 | 6945 |  | 5217 | UINT16 | 12738 | 12739 | Analog Input | 1386 | R | NV | Amps
| Max Current Demand - Circuit 27 | 27 | 6946 |  | 5218 | UINT16 | 12740 | 12741 | Analog Input | 1387 | R | NV | Amps
| Max Current Demand - Circuit 28 | 28 | 6947 |  | 5219 | UINT16 | 12742 | 12743 | Analog Input | 1388 | R | NV | Amps
| Max Current Demand - Circuit 29 | 29 | 6948 |  | 5220 | UINT16 | 12744 | 12745 | Analog Input | 1389 | R | NV | Amps
| Max Current Demand - Circuit 30 | 30 | 6949 |  | 5221 | UINT16 | 12746 | 12747 | Analog Input | 1390 | R | NV | Amps
| Max Current Demand - Circuit 31 | 31 | 6950 |  | 5222 | UINT16 | 12748 | 12749 | Analog Input | 1391 | R | NV | Amps
| Max Current Demand - Circuit 32 | 32 | 6951 |  | 5223 | UINT16 | 12750 | 12751 | Analog Input | 1392 | R | NV | Amps
| Max Current Demand - Circuit 33 | 33 | 6952 |  | 5224 | UINT16 | 12752 | 12753 | Analog Input | 1393 | R | NV | Amps
| Max Current Demand - Circuit 34 | 34 | 6953 |  | 5225 | UINT16 | 12754 | 12755 | Analog Input | 1394 | R | NV | Amps
| Max Current Demand - Circuit 35 | 35 | 6954 |  | 5226 | UINT16 | 12756 | 12757 | Analog Input | 1395 | R | NV | Amps
| Max Current Demand - Circuit 36 | 36 | 6955 |  | 5227 | UINT16 | 12758 | 12759 | Analog Input | 1396 | R | NV | Amps
| Max Current Demand - Circuit 37 | 37 | 6956 |  | 5228 | UINT16 | 12760 | 12761 | Analog Input | 1397 | R | NV | Amps
| Max Current Demand - Circuit 38 | 38 | 6957 |  | 5229 | UINT16 | 12762 | 12763 | Analog Input | 1398 | R | NV | Amps
| Max Current Demand - Circuit 39 | 39 | 6958 |  | 5230 | UINT16 | 12764 | 12765 | Analog Input | 1399 | R | NV | Amps
| Max Current Demand - Circuit 40 | 40 | 6959 |  | 5231 | UINT16 | 12766 | 12767 | Analog Input | 1400 | R | NV | Amps
| Max Current Demand - Circuit 41 | 41 | 6960 |  | 5232 | UINT16 | 12768 | 12769 | Analog Input | 1401 | R | NV | Amps
| Max Current Demand - Circuit 42 | 42 | 6961 |  | 5233 | UINT16 | 12770 | 12771 | Analog Input | 1402 | R | NV | Amps
| Max Current Demand - Circuit 43 | 43 | 6962 |  | 5234 | UINT16 | 12772 | 12773 | Analog Input | 1403 | R | NV | Amps
| Max Current Demand - Circuit 44 | 44 | 6963 |  | 5235 | UINT16 | 12774 | 12775 | Analog Input | 1404 | R | NV | Amps
| Max Current Demand - Circuit 45 | 45 | 6964 |  | 5236 | UINT16 | 12776 | 12777 | Analog Input | 1405 | R | NV | Amps
| Max Current Demand - Circuit 46 | 46 | 6965 |  | 5237 | UINT16 | 12778 | 12779 | Analog Input | 1406 | R | NV | Amps
| Max Current Demand - Circuit 47 | 47 | 6966 |  | 5238 | UINT16 | 12780 | 12781 | Analog Input | 1407 | R | NV | Amps
| Max Current Demand - Circuit 48 | 48 | 6967 |  | 5239 | UINT16 | 12782 | 12783 | Analog Input | 1408 | R | NV | Amps
| Max Current Demand - Circuit 49 | 49 | 6968 |  | 5240 | UINT16 | 12784 | 12785 | Analog Input | 1409 | R | NV | Amps
| Max Current Demand - Circuit 50 | 50 | 6969 |  | 5241 | UINT16 | 12786 | 12787 | Analog Input | 1410 | R | NV | Amps
| Max Current Demand - Circuit 51 | 51 | 6970 |  | 5242 | UINT16 | 12788 | 12789 | Analog Input | 1411 | R | NV | Amps
| Max Current Demand - Circuit 52 | 52 | 6971 |  | 5243 | UINT16 | 12790 | 12791 | Analog Input | 1412 | R | NV | Amps
| Max Current Demand - Circuit 53 | 53 | 6972 |  | 5244 | UINT16 | 12792 | 12793 | Analog Input | 1413 | R | NV | Amps
| Max Current Demand - Circuit 54 | 54 | 6973 |  | 5245 | UINT16 | 12794 | 12795 | Analog Input | 1414 | R | NV | Amps
| Max Current Demand - Circuit 55 | 55 | 6974 |  | 5246 | UINT16 | 12796 | 12797 | Analog Input | 1415 | R | NV | Amps
| Max Current Demand - Circuit 56 | 56 | 6975 |  | 5247 | UINT16 | 12798 | 12799 | Analog Input | 1416 | R | NV | Amps
| Max Current Demand - Circuit 57 | 57 | 6976 |  | 5248 | UINT16 | 12800 | 12801 | Analog Input | 1417 | R | NV | Amps
| Max Current Demand - Circuit 58 | 58 | 6977 |  | 5249 | UINT16 | 12802 | 12803 | Analog Input | 1418 | R | NV | Amps
| Max Current Demand - Circuit 59 | 59 | 6978 |  | 5250 | UINT16 | 12804 | 12805 | Analog Input | 1419 | R | NV | Amps
| Max Current Demand - Circuit 60 | 60 | 6979 |  | 5251 | UINT16 | 12806 | 12807 | Analog Input | 1420 | R | NV | Amps
| Max Current Demand - Circuit 61 | 61 | 6980 |  | 5252 | UINT16 | 12808 | 12809 | Analog Input | 1421 | R | NV | Amps
| Max Current Demand - Circuit 62 | 62 | 6981 |  | 5253 | UINT16 | 12810 | 12811 | Analog Input | 1422 | R | NV | Amps
| Max Current Demand - Circuit 63 | 63 | 6982 |  | 5254 | UINT16 | 12812 | 12813 | Analog Input | 1423 | R | NV | Amps
| Max Current Demand - Circuit 64 | 64 | 6983 |  | 5255 | UINT16 | 12814 | 12815 | Analog Input | 1424 | R | NV | Amps
| Max Current Demand - Circuit 65 | 65 | 6984 |  | 5256 | UINT16 | 12816 | 12817 | Analog Input | 1425 | R | NV | Amps
| Max Current Demand - Circuit 66 | 66 | 6985 |  | 5257 | UINT16 | 12818 | 12819 | Analog Input | 1426 | R | NV | Amps
| Max Current Demand - Circuit 67 | 67 | 6986 |  | 5258 | UINT16 | 12820 | 12821 | Analog Input | 1427 | R | NV | Amps
| Max Current Demand - Circuit 68 | 68 | 6987 |  | 5259 | UINT16 | 12822 | 12823 | Analog Input | 1428 | R | NV | Amps
| Max Current Demand - Circuit 69 | 69 | 6988 |  | 5260 | UINT16 | 12824 | 12825 | Analog Input | 1429 | R | NV | Amps
| Max Current Demand - Circuit 70 | 70 | 6989 |  | 5261 | UINT16 | 12826 | 12827 | Analog Input | 1430 | R | NV | Amps
| Max Current Demand - Circuit 71 | 71 | 6990 |  | 5262 | UINT16 | 12828 | 12829 | Analog Input | 1431 | R | NV | Amps
| Max Current Demand - Circuit 72 | 72 | 6991 |  | 5263 | UINT16 | 12830 | 12831 | Analog Input | 1432 | R | NV | Amps
| Max Current Demand - Circuit 73 | 73 | 6992 |  | 5264 | UINT16 | 12832 | 12833 | Analog Input | 1433 | R | NV | Amps
| Max Current Demand - Circuit 74 | 74 | 6993 |  | 5265 | UINT16 | 12834 | 12835 | Analog Input | 1434 | R | NV | Amps
| Max Current Demand - Circuit 75 | 75 | 6994 |  | 5266 | UINT16 | 12836 | 12837 | Analog Input | 1435 | R | NV | Amps
| Max Current Demand - Circuit 76 | 76 | 6995 |  | 5267 | UINT16 | 12838 | 12839 | Analog Input | 1436 | R | NV | Amps
| Max Current Demand - Circuit 77 | 77 | 6996 |  | 5268 | UINT16 | 12840 | 12841 | Analog Input | 1437 | R | NV | Amps
| Max Current Demand - Circuit 78 | 78 | 6997 |  | 5269 | UINT16 | 12842 | 12843 | Analog Input | 1438 | R | NV | Amps
| Max Current Demand - Circuit 79 | 79 | 6998 |  | 5270 | UINT16 | 12844 | 12845 | Analog Input | 1439 | R | NV | Amps
| Max Current Demand - Circuit 80 | 80 | 6999 |  | 5271 | UINT16 | 12846 | 12847 | Analog Input | 1440 | R | NV | Amps
| Max Current Demand - Circuit 81 | 81 | 7000 |  | 5272 | UINT16 | 12848 | 12849 | Analog Input | 1441 | R | NV | Amps
| Max Current Demand - Circuit 82 | 82 | 7001 |  | 5273 | UINT16 | 12850 | 12851 | Analog Input | 1442 | R | NV | Amps
| Max Current Demand - Circuit 83 | 83 | 7002 |  | 5274 | UINT16 | 12852 | 12853 | Analog Input | 1443 | R | NV | Amps
| Max Current Demand - Circuit 84 | 84 | 7003 |  | 5275 | UINT16 | 12854 | 12855 | Analog Input | 1444 | R | NV | Amps
| Max Current Demand - Circuit 85 | 85 | 7004 |  | 5276 | UINT16 | 12856 | 12857 | Analog Input | 1445 | R | NV | Amps
| Max Current Demand - Circuit 86 | 86 | 7005 |  | 5277 | UINT16 | 12858 | 12859 | Analog Input | 1446 | R | NV | Amps
| Max Current Demand - Circuit 87 | 87 | 7006 |  | 5278 | UINT16 | 12860 | 12861 | Analog Input | 1447 | R | NV | Amps
| Max Current Demand - Circuit 88 | 88 | 7007 |  | 5279 | UINT16 | 12862 | 12863 | Analog Input | 1448 | R | NV | Amps
| Max Current Demand - Circuit 89 | 89 | 7008 |  | 5280 | UINT16 | 12864 | 12865 | Analog Input | 1449 | R | NV | Amps
| Max Current Demand - Circuit 90 | 90 | 7009 |  | 5281 | UINT16 | 12866 | 12867 | Analog Input | 1450 | R | NV | Amps
| Max Current Demand - Circuit 91 | 91 | 7010 |  | 5282 | UINT16 | 12868 | 12869 | Analog Input | 1451 | R | NV | Amps
| Max Current Demand - Circuit 92 | 92 | 7011 |  | 5283 | UINT16 | 12870 | 12871 | Analog Input | 1452 | R | NV | Amps
| Max Current Demand - Circuit 93 | 93 | 7012 |  | 5284 | UINT16 | 12872 | 12873 | Analog Input | 1453 | R | NV | Amps
| Max Current Demand - Circuit 94 | 94 | 7013 |  | 5285 | UINT16 | 12874 | 12875 | Analog Input | 1454 | R | NV | Amps
| Max Current Demand - Circuit 95 | 95 | 7014 |  | 5286 | UINT16 | 12876 | 12877 | Analog Input | 1455 | R | NV | Amps
| Max Current Demand - Circuit 96 | 96 | 7015 |  | 5287 | UINT16 | 12878 | 12879 | Analog Input | 1456 | R | NV | Amps
| Max kW Demand |  | 7016 | 7111 | Power | UINT16 | 12880 | 13071 | Analog Input | 1457 - 1552 | R | NV | kW
| Max kW Demand - Circuit 1 | 1 | 7016 |  | 5096 | UINT16 | 12880 | 12881 | Analog Input | 1457 | R | NV | kW
| Max kW Demand - Circuit 2 | 2 | 7017 |  | 5097 | UINT16 | 12882 | 12883 | Analog Input | 1458 | R | NV | kW
| Max kW Demand - Circuit 3 | 3 | 7018 |  | 5098 | UINT16 | 12884 | 12885 | Analog Input | 1459 | R | NV | kW
| Max kW Demand - Circuit 4 | 4 | 7019 |  | 5099 | UINT16 | 12886 | 12887 | Analog Input | 1460 | R | NV | kW
| Max kW Demand - Circuit 5 | 5 | 7020 |  | 5100 | UINT16 | 12888 | 12889 | Analog Input | 1461 | R | NV | kW
| Max kW Demand - Circuit 6 | 6 | 7021 |  | 5101 | UINT16 | 12890 | 12891 | Analog Input | 1462 | R | NV | kW
| Max kW Demand - Circuit 7 | 7 | 7022 |  | 5102 | UINT16 | 12892 | 12893 | Analog Input | 1463 | R | NV | kW
| Max kW Demand - Circuit 8 | 8 | 7023 |  | 5103 | UINT16 | 12894 | 12895 | Analog Input | 1464 | R | NV | kW
| Max kW Demand - Circuit 9 | 9 | 7024 |  | 5104 | UINT16 | 12896 | 12897 | Analog Input | 1465 | R | NV | kW
| Max kW Demand - Circuit 10 | 10 | 7025 |  | 5105 | UINT16 | 12898 | 12899 | Analog Input | 1466 | R | NV | kW
| Max kW Demand - Circuit 11 | 11 | 7026 |  | 5106 | UINT16 | 12900 | 12901 | Analog Input | 1467 | R | NV | kW
| Max kW Demand - Circuit 12 | 12 | 7027 |  | 5107 | UINT16 | 12902 | 12903 | Analog Input | 1468 | R | NV | kW
| Max kW Demand - Circuit 13 | 13 | 7028 |  | 5108 | UINT16 | 12904 | 12905 | Analog Input | 1469 | R | NV | kW
| Max kW Demand - Circuit 14 | 14 | 7029 |  | 5109 | UINT16 | 12906 | 12907 | Analog Input | 1470 | R | NV | kW
| Max kW Demand - Circuit 15 | 15 | 7030 |  | 5110 | UINT16 | 12908 | 12909 | Analog Input | 1471 | R | NV | kW
| Max kW Demand - Circuit 16 | 16 | 7031 |  | 5111 | UINT16 | 12910 | 12911 | Analog Input | 1472 | R | NV | kW
| Max kW Demand - Circuit 17 | 17 | 7032 |  | 5112 | UINT16 | 12912 | 12913 | Analog Input | 1473 | R | NV | kW
| Max kW Demand - Circuit 18 | 18 | 7033 |  | 5113 | UINT16 | 12914 | 12915 | Analog Input | 1474 | R | NV | kW
| Max kW Demand - Circuit 19 | 19 | 7034 |  | 5114 | UINT16 | 12916 | 12917 | Analog Input | 1475 | R | NV | kW
| Max kW Demand - Circuit 20 | 20 | 7035 |  | 5115 | UINT16 | 12918 | 12919 | Analog Input | 1476 | R | NV | kW
| Max kW Demand - Circuit 21 | 21 | 7036 |  | 5116 | UINT16 | 12920 | 12921 | Analog Input | 1477 | R | NV | kW
| Max kW Demand - Circuit 22 | 22 | 7037 |  | 5117 | UINT16 | 12922 | 12923 | Analog Input | 1478 | R | NV | kW
| Max kW Demand - Circuit 23 | 23 | 7038 |  | 5118 | UINT16 | 12924 | 12925 | Analog Input | 1479 | R | NV | kW
| Max kW Demand - Circuit 24 | 24 | 7039 |  | 5119 | UINT16 | 12926 | 12927 | Analog Input | 1480 | R | NV | kW
| Max kW Demand - Circuit 25 | 25 | 7040 |  | 5120 | UINT16 | 12928 | 12929 | Analog Input | 1481 | R | NV | kW
| Max kW Demand - Circuit 26 | 26 | 7041 |  | 5121 | UINT16 | 12930 | 12931 | Analog Input | 1482 | R | NV | kW
| Max kW Demand - Circuit 27 | 27 | 7042 |  | 5122 | UINT16 | 12932 | 12933 | Analog Input | 1483 | R | NV | kW
| Max kW Demand - Circuit 28 | 28 | 7043 |  | 5123 | UINT16 | 12934 | 12935 | Analog Input | 1484 | R | NV | kW
| Max kW Demand - Circuit 29 | 29 | 7044 |  | 5124 | UINT16 | 12936 | 12937 | Analog Input | 1485 | R | NV | kW
| Max kW Demand - Circuit 30 | 30 | 7045 |  | 5125 | UINT16 | 12938 | 12939 | Analog Input | 1486 | R | NV | kW
| Max kW Demand - Circuit 31 | 31 | 7046 |  | 5126 | UINT16 | 12940 | 12941 | Analog Input | 1487 | R | NV | kW
| Max kW Demand - Circuit 32 | 32 | 7047 |  | 5127 | UINT16 | 12942 | 12943 | Analog Input | 1488 | R | NV | kW
| Max kW Demand - Circuit 33 | 33 | 7048 |  | 5128 | UINT16 | 12944 | 12945 | Analog Input | 1489 | R | NV | kW
| Max kW Demand - Circuit 34 | 34 | 7049 |  | 5129 | UINT16 | 12946 | 12947 | Analog Input | 1490 | R | NV | kW
| Max kW Demand - Circuit 35 | 35 | 7050 |  | 5130 | UINT16 | 12948 | 12949 | Analog Input | 1491 | R | NV | kW
| Max kW Demand - Circuit 36 | 36 | 7051 |  | 5131 | UINT16 | 12950 | 12951 | Analog Input | 1492 | R | NV | kW
| Max kW Demand - Circuit 37 | 37 | 7052 |  | 5132 | UINT16 | 12952 | 12953 | Analog Input | 1493 | R | NV | kW
| Max kW Demand - Circuit 38 | 38 | 7053 |  | 5133 | UINT16 | 12954 | 12955 | Analog Input | 1494 | R | NV | kW
| Max kW Demand - Circuit 39 | 39 | 7054 |  | 5134 | UINT16 | 12956 | 12957 | Analog Input | 1495 | R | NV | kW
| Max kW Demand - Circuit 40 | 40 | 7055 |  | 5135 | UINT16 | 12958 | 12959 | Analog Input | 1496 | R | NV | kW
| Max kW Demand - Circuit 41 | 41 | 7056 |  | 5136 | UINT16 | 12960 | 12961 | Analog Input | 1497 | R | NV | kW
| Max kW Demand - Circuit 42 | 42 | 7057 |  | 5137 | UINT16 | 12962 | 12963 | Analog Input | 1498 | R | NV | kW
| Max kW Demand - Circuit 43 | 43 | 7058 |  | 5138 | UINT16 | 12964 | 12965 | Analog Input | 1499 | R | NV | kW
| Max kW Demand - Circuit 44 | 44 | 7059 |  | 5139 | UINT16 | 12966 | 12967 | Analog Input | 1500 | R | NV | kW
| Max kW Demand - Circuit 45 | 45 | 7060 |  | 5140 | UINT16 | 12968 | 12969 | Analog Input | 1501 | R | NV | kW
| Max kW Demand - Circuit 46 | 46 | 7061 |  | 5141 | UINT16 | 12970 | 12971 | Analog Input | 1502 | R | NV | kW
| Max kW Demand - Circuit 47 | 47 | 7062 |  | 5142 | UINT16 | 12972 | 12973 | Analog Input | 1503 | R | NV | kW
| Max kW Demand - Circuit 48 | 48 | 7063 |  | 5143 | UINT16 | 12974 | 12975 | Analog Input | 1504 | R | NV | kW
| Max kW Demand - Circuit 49 | 49 | 7064 |  | 5144 | UINT16 | 12976 | 12977 | Analog Input | 1505 | R | NV | kW
| Max kW Demand - Circuit 50 | 50 | 7065 |  | 5145 | UINT16 | 12978 | 12979 | Analog Input | 1506 | R | NV | kW
| Max kW Demand - Circuit 51 | 51 | 7066 |  | 5146 | UINT16 | 12980 | 12981 | Analog Input | 1507 | R | NV | kW
| Max kW Demand - Circuit 52 | 52 | 7067 |  | 5147 | UINT16 | 12982 | 12983 | Analog Input | 1508 | R | NV | kW
| Max kW Demand - Circuit 53 | 53 | 7068 |  | 5148 | UINT16 | 12984 | 12985 | Analog Input | 1509 | R | NV | kW
| Max kW Demand - Circuit 54 | 54 | 7069 |  | 5149 | UINT16 | 12986 | 12987 | Analog Input | 1510 | R | NV | kW
| Max kW Demand - Circuit 55 | 55 | 7070 |  | 5150 | UINT16 | 12988 | 12989 | Analog Input | 1511 | R | NV | kW
| Max kW Demand - Circuit 56 | 56 | 7071 |  | 5151 | UINT16 | 12990 | 12991 | Analog Input | 1512 | R | NV | kW
| Max kW Demand - Circuit 57 | 57 | 7072 |  | 5152 | UINT16 | 12992 | 12993 | Analog Input | 1513 | R | NV | kW
| Max kW Demand - Circuit 58 | 58 | 7073 |  | 5153 | UINT16 | 12994 | 12995 | Analog Input | 1514 | R | NV | kW
| Max kW Demand - Circuit 59 | 59 | 7074 |  | 5154 | UINT16 | 12996 | 12997 | Analog Input | 1515 | R | NV | kW
| Max kW Demand - Circuit 60 | 60 | 7075 |  | 5155 | UINT16 | 12998 | 12999 | Analog Input | 1516 | R | NV | kW
| Max kW Demand - Circuit 61 | 61 | 7076 |  | 5156 | UINT16 | 13000 | 13001 | Analog Input | 1517 | R | NV | kW
| Max kW Demand - Circuit 62 | 62 | 7077 |  | 5157 | UINT16 | 13002 | 13003 | Analog Input | 1518 | R | NV | kW
| Max kW Demand - Circuit 63 | 63 | 7078 |  | 5158 | UINT16 | 13004 | 13005 | Analog Input | 1519 | R | NV | kW
| Max kW Demand - Circuit 64 | 64 | 7079 |  | 5159 | UINT16 | 13006 | 13007 | Analog Input | 1520 | R | NV | kW
| Max kW Demand - Circuit 65 | 65 | 7080 |  | 5160 | UINT16 | 13008 | 13009 | Analog Input | 1521 | R | NV | kW
| Max kW Demand - Circuit 66 | 66 | 7081 |  | 5161 | UINT16 | 13010 | 13011 | Analog Input | 1522 | R | NV | kW
| Max kW Demand - Circuit 67 | 67 | 7082 |  | 5162 | UINT16 | 13012 | 13013 | Analog Input | 1523 | R | NV | kW
| Max kW Demand - Circuit 68 | 68 | 7083 |  | 5163 | UINT16 | 13014 | 13015 | Analog Input | 1524 | R | NV | kW
| Max kW Demand - Circuit 69 | 69 | 7084 |  | 5164 | UINT16 | 13016 | 13017 | Analog Input | 1525 | R | NV | kW
| Max kW Demand - Circuit 70 | 70 | 7085 |  | 5165 | UINT16 | 13018 | 13019 | Analog Input | 1526 | R | NV | kW
| Max kW Demand - Circuit 71 | 71 | 7086 |  | 5166 | UINT16 | 13020 | 13021 | Analog Input | 1527 | R | NV | kW
| Max kW Demand - Circuit 72 | 72 | 7087 |  | 5167 | UINT16 | 13022 | 13023 | Analog Input | 1528 | R | NV | kW
| Max kW Demand - Circuit 73 | 73 | 7088 |  | 5168 | UINT16 | 13024 | 13025 | Analog Input | 1529 | R | NV | kW
| Max kW Demand - Circuit 74 | 74 | 7089 |  | 5169 | UINT16 | 13026 | 13027 | Analog Input | 1530 | R | NV | kW
| Max kW Demand - Circuit 75 | 75 | 7090 |  | 5170 | UINT16 | 13028 | 13029 | Analog Input | 1531 | R | NV | kW
| Max kW Demand - Circuit 76 | 76 | 7091 |  | 5171 | UINT16 | 13030 | 13031 | Analog Input | 1532 | R | NV | kW
| Max kW Demand - Circuit 77 | 77 | 7092 |  | 5172 | UINT16 | 13032 | 13033 | Analog Input | 1533 | R | NV | kW
| Max kW Demand - Circuit 78 | 78 | 7093 |  | 5173 | UINT16 | 13034 | 13035 | Analog Input | 1534 | R | NV | kW
| Max kW Demand - Circuit 79 | 79 | 7094 |  | 5174 | UINT16 | 13036 | 13037 | Analog Input | 1535 | R | NV | kW
| Max kW Demand - Circuit 80 | 80 | 7095 |  | 5175 | UINT16 | 13038 | 13039 | Analog Input | 1536 | R | NV | kW
| Max kW Demand - Circuit 81 | 81 | 7096 |  | 5176 | UINT16 | 13040 | 13041 | Analog Input | 1537 | R | NV | kW
| Max kW Demand - Circuit 82 | 82 | 7097 |  | 5177 | UINT16 | 13042 | 13043 | Analog Input | 1538 | R | NV | kW
| Max kW Demand - Circuit 83 | 83 | 7098 |  | 5178 | UINT16 | 13044 | 13045 | Analog Input | 1539 | R | NV | kW
| Max kW Demand - Circuit 84 | 84 | 7099 |  | 5179 | UINT16 | 13046 | 13047 | Analog Input | 1540 | R | NV | kW
| Max kW Demand - Circuit 85 | 85 | 7100 |  | 5180 | UINT16 | 13048 | 13049 | Analog Input | 1541 | R | NV | kW
| Max kW Demand - Circuit 86 | 86 | 7101 |  | 5181 | UINT16 | 13050 | 13051 | Analog Input | 1542 | R | NV | kW
| Max kW Demand - Circuit 87 | 87 | 7102 |  | 5182 | UINT16 | 13052 | 13053 | Analog Input | 1543 | R | NV | kW
| Max kW Demand - Circuit 88 | 88 | 7103 |  | 5183 | UINT16 | 13054 | 13055 | Analog Input | 1544 | R | NV | kW
| Max kW Demand - Circuit 89 | 89 | 7104 |  | 5184 | UINT16 | 13056 | 13057 | Analog Input | 1545 | R | NV | kW
| Max kW Demand - Circuit 90 | 90 | 7105 |  | 5185 | UINT16 | 13058 | 13059 | Analog Input | 1546 | R | NV | kW
| Max kW Demand - Circuit 91 | 91 | 7106 |  | 5186 | UINT16 | 13060 | 13061 | Analog Input | 1547 | R | NV | kW
| Max kW Demand - Circuit 92 | 92 | 7107 |  | 5187 | UINT16 | 13062 | 13063 | Analog Input | 1548 | R | NV | kW
| Max kW Demand - Circuit 93 | 93 | 7108 |  | 5188 | UINT16 | 13064 | 13065 | Analog Input | 1549 | R | NV | kW
| Max kW Demand - Circuit 94 | 94 | 7109 |  | 5189 | UINT16 | 13066 | 13067 | Analog Input | 1550 | R | NV | kW
| Max kW Demand - Circuit 95 | 95 | 7110 |  | 5190 | UINT16 | 13068 | 13069 | Analog Input | 1551 | R | NV | kW
| Max kW Demand - Circuit 96 | 96 | 7111 |  | 5191 | UINT16 | 13070 | 13071 | Analog Input | 1552 | R | NV | kW
| KWH Snapshot |  | 7112 | 7303 | Energy | UINT32 | 13072 | 13263 | Analog Input | 1553 - 1648 | R |  | kWh
| KWH Snapshot - Circuit 1 | 1 | 7112 | 7113 | 5000 |  | 13072 | 13073 | Analog Input | 1553 | R |  | kWh
| KWH Snapshot - Circuit 2 | 2 | 7114 | 7115 | 5001 |  | 13074 | 13075 | Analog Input | 1554 | R |  | kWh
| KWH Snapshot - Circuit 3 | 3 | 7116 | 7117 | 5002 |  | 13076 | 13077 | Analog Input | 1555 | R |  | kWh
| KWH Snapshot - Circuit 4 | 4 | 7118 | 7119 | 5003 |  | 13078 | 13079 | Analog Input | 1556 | R |  | kWh
| KWH Snapshot - Circuit 5 | 5 | 7120 | 7121 | 5004 |  | 13080 | 13081 | Analog Input | 1557 | R |  | kWh
| KWH Snapshot - Circuit 6 | 6 | 7122 | 7123 | 5005 |  | 13082 | 13083 | Analog Input | 1558 | R |  | kWh
| KWH Snapshot - Circuit 7 | 7 | 7124 | 7125 | 5006 |  | 13084 | 13085 | Analog Input | 1559 | R |  | kWh
| KWH Snapshot - Circuit 8 | 8 | 7126 | 7127 | 5007 |  | 13086 | 13087 | Analog Input | 1560 | R |  | kWh
| KWH Snapshot - Circuit 9 | 9 | 7128 | 7129 | 5008 |  | 13088 | 13089 | Analog Input | 1561 | R |  | kWh
| KWH Snapshot - Circuit 10 | 10 | 7130 | 7131 | 5009 |  | 13090 | 13091 | Analog Input | 1562 | R |  | kWh
| KWH Snapshot - Circuit 11 | 11 | 7132 | 7133 | 5010 |  | 13092 | 13093 | Analog Input | 1563 | R |  | kWh
| KWH Snapshot - Circuit 12 | 12 | 7134 | 7135 | 5011 |  | 13094 | 13095 | Analog Input | 1564 | R |  | kWh
| KWH Snapshot - Circuit 13 | 13 | 7136 | 7137 | 5012 |  | 13096 | 13097 | Analog Input | 1565 | R |  | kWh
| KWH Snapshot - Circuit 14 | 14 | 7138 | 7139 | 5013 |  | 13098 | 13099 | Analog Input | 1566 | R |  | kWh
| KWH Snapshot - Circuit 15 | 15 | 7140 | 7141 | 5014 |  | 13100 | 13101 | Analog Input | 1567 | R |  | kWh
| KWH Snapshot - Circuit 16 | 16 | 7142 | 7143 | 5015 |  | 13102 | 13103 | Analog Input | 1568 | R |  | kWh
| KWH Snapshot - Circuit 17 | 17 | 7144 | 7145 | 5016 |  | 13104 | 13105 | Analog Input | 1569 | R |  | kWh
| KWH Snapshot - Circuit 18 | 18 | 7146 | 7147 | 5017 |  | 13106 | 13107 | Analog Input | 1570 | R |  | kWh
| KWH Snapshot - Circuit 19 | 19 | 7148 | 7149 | 5018 |  | 13108 | 13109 | Analog Input | 1571 | R |  | kWh
| KWH Snapshot - Circuit 20 | 20 | 7150 | 7151 | 5019 |  | 13110 | 13111 | Analog Input | 1572 | R |  | kWh
| KWH Snapshot - Circuit 21 | 21 | 7152 | 7153 | 5020 |  | 13112 | 13113 | Analog Input | 1573 | R |  | kWh
| KWH Snapshot - Circuit 22 | 22 | 7154 | 7155 | 5021 |  | 13114 | 13115 | Analog Input | 1574 | R |  | kWh
| KWH Snapshot - Circuit 23 | 23 | 7156 | 7157 | 5022 |  | 13116 | 13117 | Analog Input | 1575 | R |  | kWh
| KWH Snapshot - Circuit 24 | 24 | 7158 | 7159 | 5023 |  | 13118 | 13119 | Analog Input | 1576 | R |  | kWh
| KWH Snapshot - Circuit 25 | 25 | 7160 | 7161 | 5024 |  | 13120 | 13121 | Analog Input | 1577 | R |  | kWh
| KWH Snapshot - Circuit 26 | 26 | 7162 | 7163 | 5025 |  | 13122 | 13123 | Analog Input | 1578 | R |  | kWh
| KWH Snapshot - Circuit 27 | 27 | 7164 | 7165 | 5026 |  | 13124 | 13125 | Analog Input | 1579 | R |  | kWh
| KWH Snapshot - Circuit 28 | 28 | 7166 | 7167 | 5027 |  | 13126 | 13127 | Analog Input | 1580 | R |  | kWh
| KWH Snapshot - Circuit 29 | 29 | 7168 | 7169 | 5028 |  | 13128 | 13129 | Analog Input | 1581 | R |  | kWh
| KWH Snapshot - Circuit 30 | 30 | 7170 | 7171 | 5029 |  | 13130 | 13131 | Analog Input | 1582 | R |  | kWh
| KWH Snapshot - Circuit 31 | 31 | 7172 | 7173 | 5030 |  | 13132 | 13133 | Analog Input | 1583 | R |  | kWh
| KWH Snapshot - Circuit 32 | 32 | 7174 | 7175 | 5031 |  | 13134 | 13135 | Analog Input | 1584 | R |  | kWh
| KWH Snapshot - Circuit 33 | 33 | 7176 | 7177 | 5032 |  | 13136 | 13137 | Analog Input | 1585 | R |  | kWh
| KWH Snapshot - Circuit 34 | 34 | 7178 | 7179 | 5033 |  | 13138 | 13139 | Analog Input | 1586 | R |  | kWh
| KWH Snapshot - Circuit 35 | 35 | 7180 | 7181 | 5034 |  | 13140 | 13141 | Analog Input | 1587 | R |  | kWh
| KWH Snapshot - Circuit 36 | 36 | 7182 | 7183 | 5035 |  | 13142 | 13143 | Analog Input | 1588 | R |  | kWh
| KWH Snapshot - Circuit 37 | 37 | 7184 | 7185 | 5036 |  | 13144 | 13145 | Analog Input | 1589 | R |  | kWh
| KWH Snapshot - Circuit 38 | 38 | 7186 | 7187 | 5037 |  | 13146 | 13147 | Analog Input | 1590 | R |  | kWh
| KWH Snapshot - Circuit 39 | 39 | 7188 | 7189 | 5038 |  | 13148 | 13149 | Analog Input | 1591 | R |  | kWh
| KWH Snapshot - Circuit 40 | 40 | 7190 | 7191 | 5039 |  | 13150 | 13151 | Analog Input | 1592 | R |  | kWh
| KWH Snapshot - Circuit 41 | 41 | 7192 | 7193 | 5040 |  | 13152 | 13153 | Analog Input | 1593 | R |  | kWh
| KWH Snapshot - Circuit 42 | 42 | 7194 | 7195 | 5041 |  | 13154 | 13155 | Analog Input | 1594 | R |  | kWh
| KWH Snapshot - Circuit 43 | 43 | 7196 | 7197 | 5042 |  | 13156 | 13157 | Analog Input | 1595 | R |  | kWh
| KWH Snapshot - Circuit 44 | 44 | 7198 | 7199 | 5043 |  | 13158 | 13159 | Analog Input | 1596 | R |  | kWh
| KWH Snapshot - Circuit 45 | 45 | 7200 | 7201 | 5044 |  | 13160 | 13161 | Analog Input | 1597 | R |  | kWh
| KWH Snapshot - Circuit 46 | 46 | 7202 | 7203 | 5045 |  | 13162 | 13163 | Analog Input | 1598 | R |  | kWh
| KWH Snapshot - Circuit 47 | 47 | 7204 | 7205 | 5046 |  | 13164 | 13165 | Analog Input | 1599 | R |  | kWh
| KWH Snapshot - Circuit 48 | 48 | 7206 | 7207 | 5047 |  | 13166 | 13167 | Analog Input | 1600 | R |  | kWh
| KWH Snapshot - Circuit 49 | 49 | 7208 | 7209 | 5048 |  | 13168 | 13169 | Analog Input | 1601 | R |  | kWh
| KWH Snapshot - Circuit 50 | 50 | 7210 | 7211 | 5049 |  | 13170 | 13171 | Analog Input | 1602 | R |  | kWh
| KWH Snapshot - Circuit 51 | 51 | 7212 | 7213 | 5050 |  | 13172 | 13173 | Analog Input | 1603 | R |  | kWh
| KWH Snapshot - Circuit 52 | 52 | 7214 | 7215 | 5051 |  | 13174 | 13175 | Analog Input | 1604 | R |  | kWh
| KWH Snapshot - Circuit 53 | 53 | 7216 | 7217 | 5052 |  | 13176 | 13177 | Analog Input | 1605 | R |  | kWh
| KWH Snapshot - Circuit 54 | 54 | 7218 | 7219 | 5053 |  | 13178 | 13179 | Analog Input | 1606 | R |  | kWh
| KWH Snapshot - Circuit 55 | 55 | 7220 | 7221 | 5054 |  | 13180 | 13181 | Analog Input | 1607 | R |  | kWh
| KWH Snapshot - Circuit 56 | 56 | 7222 | 7223 | 5055 |  | 13182 | 13183 | Analog Input | 1608 | R |  | kWh
| KWH Snapshot - Circuit 57 | 57 | 7224 | 7225 | 5056 |  | 13184 | 13185 | Analog Input | 1609 | R |  | kWh
| KWH Snapshot - Circuit 58 | 58 | 7226 | 7227 | 5057 |  | 13186 | 13187 | Analog Input | 1610 | R |  | kWh
| KWH Snapshot - Circuit 59 | 59 | 7228 | 7229 | 5058 |  | 13188 | 13189 | Analog Input | 1611 | R |  | kWh
| KWH Snapshot - Circuit 60 | 60 | 7230 | 7231 | 5059 |  | 13190 | 13191 | Analog Input | 1612 | R |  | kWh
| KWH Snapshot - Circuit 61 | 61 | 7232 | 7233 | 5060 |  | 13192 | 13193 | Analog Input | 1613 | R |  | kWh
| KWH Snapshot - Circuit 62 | 62 | 7234 | 7235 | 5061 |  | 13194 | 13195 | Analog Input | 1614 | R |  | kWh
| KWH Snapshot - Circuit 63 | 63 | 7236 | 7237 | 5062 |  | 13196 | 13197 | Analog Input | 1615 | R |  | kWh
| KWH Snapshot - Circuit 64 | 64 | 7238 | 7239 | 5063 |  | 13198 | 13199 | Analog Input | 1616 | R |  | kWh
| KWH Snapshot - Circuit 65 | 65 | 7240 | 7241 | 5064 |  | 13200 | 13201 | Analog Input | 1617 | R |  | kWh
| KWH Snapshot - Circuit 66 | 66 | 7242 | 7243 | 5065 |  | 13202 | 13203 | Analog Input | 1618 | R |  | kWh
| KWH Snapshot - Circuit 67 | 67 | 7244 | 7245 | 5066 |  | 13204 | 13205 | Analog Input | 1619 | R |  | kWh
| KWH Snapshot - Circuit 68 | 68 | 7246 | 7247 | 5067 |  | 13206 | 13207 | Analog Input | 1620 | R |  | kWh
| KWH Snapshot - Circuit 69 | 69 | 7248 | 7249 | 5068 |  | 13208 | 13209 | Analog Input | 1621 | R |  | kWh
| KWH Snapshot - Circuit 70 | 70 | 7250 | 7251 | 5069 |  | 13210 | 13211 | Analog Input | 1622 | R |  | kWh
| KWH Snapshot - Circuit 71 | 71 | 7252 | 7253 | 5070 |  | 13212 | 13213 | Analog Input | 1623 | R |  | kWh
| KWH Snapshot - Circuit 72 | 72 | 7254 | 7255 | 5071 |  | 13214 | 13215 | Analog Input | 1624 | R |  | kWh
| KWH Snapshot - Circuit 73 | 73 | 7256 | 7257 | 5072 |  | 13216 | 13217 | Analog Input | 1625 | R |  | kWh
| KWH Snapshot - Circuit 74 | 74 | 7258 | 7259 | 5073 |  | 13218 | 13219 | Analog Input | 1626 | R |  | kWh
| KWH Snapshot - Circuit 75 | 75 | 7260 | 7261 | 5074 |  | 13220 | 13221 | Analog Input | 1627 | R |  | kWh
| KWH Snapshot - Circuit 76 | 76 | 7262 | 7263 | 5075 |  | 13222 | 13223 | Analog Input | 1628 | R |  | kWh
| KWH Snapshot - Circuit 77 | 77 | 7264 | 7265 | 5076 |  | 13224 | 13225 | Analog Input | 1629 | R |  | kWh
| KWH Snapshot - Circuit 78 | 78 | 7266 | 7267 | 5077 |  | 13226 | 13227 | Analog Input | 1630 | R |  | kWh
| KWH Snapshot - Circuit 79 | 79 | 7268 | 7269 | 5078 |  | 13228 | 13229 | Analog Input | 1631 | R |  | kWh
| KWH Snapshot - Circuit 80 | 80 | 7270 | 7271 | 5079 |  | 13230 | 13231 | Analog Input | 1632 | R |  | kWh
| KWH Snapshot - Circuit 81 | 81 | 7272 | 7273 | 5080 |  | 13232 | 13233 | Analog Input | 1633 | R |  | kWh
| KWH Snapshot - Circuit 82 | 82 | 7274 | 7275 | 5081 |  | 13234 | 13235 | Analog Input | 1634 | R |  | kWh
| KWH Snapshot - Circuit 83 | 83 | 7276 | 7277 | 5082 |  | 13236 | 13237 | Analog Input | 1635 | R |  | kWh
| KWH Snapshot - Circuit 84 | 84 | 7278 | 7279 | 5083 |  | 13238 | 13239 | Analog Input | 1636 | R |  | kWh
| KWH Snapshot - Circuit 85 | 85 | 7280 | 7281 | 5084 |  | 13240 | 13241 | Analog Input | 1637 | R |  | kWh
| KWH Snapshot - Circuit 86 | 86 | 7282 | 7283 | 5085 |  | 13242 | 13243 | Analog Input | 1638 | R |  | kWh
| KWH Snapshot - Circuit 87 | 87 | 7284 | 7285 | 5086 |  | 13244 | 13245 | Analog Input | 1639 | R |  | kWh
| KWH Snapshot - Circuit 88 | 88 | 7286 | 7287 | 5087 |  | 13246 | 13247 | Analog Input | 1640 | R |  | kWh
| KWH Snapshot - Circuit 89 | 89 | 7288 | 7289 | 5088 |  | 13248 | 13249 | Analog Input | 1641 | R |  | kWh
| KWH Snapshot - Circuit 90 | 90 | 7290 | 7291 | 5089 |  | 13250 | 13251 | Analog Input | 1642 | R |  | kWh
| KWH Snapshot - Circuit 91 | 91 | 7292 | 7293 | 5090 |  | 13252 | 13253 | Analog Input | 1643 | R |  | kWh
| KWH Snapshot - Circuit 92 | 92 | 7294 | 7295 | 5091 |  | 13254 | 13255 | Analog Input | 1644 | R |  | kWh
| KWH Snapshot - Circuit 93 | 93 | 7296 | 7297 | 5092 |  | 13256 | 13257 | Analog Input | 1645 | R |  | kWh
| KWH Snapshot - Circuit 94 | 94 | 7298 | 7299 | 5093 |  | 13258 | 13259 | Analog Input | 1646 | R |  | kWh
| KWH Snapshot - Circuit 95 | 95 | 7300 | 7301 | 5094 |  | 13260 | 13261 | Analog Input | 1647 | R |  | kWh
| KWH Snapshot - Circuit 96 | 96 | 7302 | 7303 | 5095 |  | 13262 | 13263 | Analog Input | 1648 | R |  | kWh
| Crest Factor |  | 7304 | 7399 | -3 | UINT16 | 13264 | 13455 | Analog Input | 1649 - 1744 | R
| Crest Factor - Circuit 1 | 1 | 7304 |  | -3 | UINT16 | 13264 | 13265 | Analog Input | 1649 | R
| Crest Factor - Circuit 2 | 2 | 7305 |  | -3 | UINT16 | 13266 | 13267 | Analog Input | 1650 | R
| Crest Factor - Circuit 3 | 3 | 7306 |  | -3 | UINT16 | 13268 | 13269 | Analog Input | 1651 | R
| Crest Factor - Circuit 4 | 4 | 7307 |  | -3 | UINT16 | 13270 | 13271 | Analog Input | 1652 | R
| Crest Factor - Circuit 5 | 5 | 7308 |  | -3 | UINT16 | 13272 | 13273 | Analog Input | 1653 | R
| Crest Factor - Circuit 6 | 6 | 7309 |  | -3 | UINT16 | 13274 | 13275 | Analog Input | 1654 | R
| Crest Factor - Circuit 7 | 7 | 7310 |  | -3 | UINT16 | 13276 | 13277 | Analog Input | 1655 | R
| Crest Factor - Circuit 8 | 8 | 7311 |  | -3 | UINT16 | 13278 | 13279 | Analog Input | 1656 | R
| Crest Factor - Circuit 9 | 9 | 7312 |  | -3 | UINT16 | 13280 | 13281 | Analog Input | 1657 | R
| Crest Factor - Circuit 10 | 10 | 7313 |  | -3 | UINT16 | 13282 | 13283 | Analog Input | 1658 | R
| Crest Factor - Circuit 11 | 11 | 7314 |  | -3 | UINT16 | 13284 | 13285 | Analog Input | 1659 | R
| Crest Factor - Circuit 12 | 12 | 7315 |  | -3 | UINT16 | 13286 | 13287 | Analog Input | 1660 | R
| Crest Factor - Circuit 13 | 13 | 7316 |  | -3 | UINT16 | 13288 | 13289 | Analog Input | 1661 | R
| Crest Factor - Circuit 14 | 14 | 7317 |  | -3 | UINT16 | 13290 | 13291 | Analog Input | 1662 | R
| Crest Factor - Circuit 15 | 15 | 7318 |  | -3 | UINT16 | 13292 | 13293 | Analog Input | 1663 | R
| Crest Factor - Circuit 16 | 16 | 7319 |  | -3 | UINT16 | 13294 | 13295 | Analog Input | 1664 | R
| Crest Factor - Circuit 17 | 17 | 7320 |  | -3 | UINT16 | 13296 | 13297 | Analog Input | 1665 | R
| Crest Factor - Circuit 18 | 18 | 7321 |  | -3 | UINT16 | 13298 | 13299 | Analog Input | 1666 | R
| Crest Factor - Circuit 19 | 19 | 7322 |  | -3 | UINT16 | 13300 | 13301 | Analog Input | 1667 | R
| Crest Factor - Circuit 20 | 20 | 7323 |  | -3 | UINT16 | 13302 | 13303 | Analog Input | 1668 | R
| Crest Factor - Circuit 21 | 21 | 7324 |  | -3 | UINT16 | 13304 | 13305 | Analog Input | 1669 | R
| Crest Factor - Circuit 22 | 22 | 7325 |  | -3 | UINT16 | 13306 | 13307 | Analog Input | 1670 | R
| Crest Factor - Circuit 23 | 23 | 7326 |  | -3 | UINT16 | 13308 | 13309 | Analog Input | 1671 | R
| Crest Factor - Circuit 24 | 24 | 7327 |  | -3 | UINT16 | 13310 | 13311 | Analog Input | 1672 | R
| Crest Factor - Circuit 25 | 25 | 7328 |  | -3 | UINT16 | 13312 | 13313 | Analog Input | 1673 | R
| Crest Factor - Circuit 26 | 26 | 7329 |  | -3 | UINT16 | 13314 | 13315 | Analog Input | 1674 | R
| Crest Factor - Circuit 27 | 27 | 7330 |  | -3 | UINT16 | 13316 | 13317 | Analog Input | 1675 | R
| Crest Factor - Circuit 28 | 28 | 7331 |  | -3 | UINT16 | 13318 | 13319 | Analog Input | 1676 | R
| Crest Factor - Circuit 29 | 29 | 7332 |  | -3 | UINT16 | 13320 | 13321 | Analog Input | 1677 | R
| Crest Factor - Circuit 30 | 30 | 7333 |  | -3 | UINT16 | 13322 | 13323 | Analog Input | 1678 | R
| Crest Factor - Circuit 31 | 31 | 7334 |  | -3 | UINT16 | 13324 | 13325 | Analog Input | 1679 | R
| Crest Factor - Circuit 32 | 32 | 7335 |  | -3 | UINT16 | 13326 | 13327 | Analog Input | 1680 | R
| Crest Factor - Circuit 33 | 33 | 7336 |  | -3 | UINT16 | 13328 | 13329 | Analog Input | 1681 | R
| Crest Factor - Circuit 34 | 34 | 7337 |  | -3 | UINT16 | 13330 | 13331 | Analog Input | 1682 | R
| Crest Factor - Circuit 35 | 35 | 7338 |  | -3 | UINT16 | 13332 | 13333 | Analog Input | 1683 | R
| Crest Factor - Circuit 36 | 36 | 7339 |  | -3 | UINT16 | 13334 | 13335 | Analog Input | 1684 | R
| Crest Factor - Circuit 37 | 37 | 7340 |  | -3 | UINT16 | 13336 | 13337 | Analog Input | 1685 | R
| Crest Factor - Circuit 38 | 38 | 7341 |  | -3 | UINT16 | 13338 | 13339 | Analog Input | 1686 | R
| Crest Factor - Circuit 39 | 39 | 7342 |  | -3 | UINT16 | 13340 | 13341 | Analog Input | 1687 | R
| Crest Factor - Circuit 40 | 40 | 7343 |  | -3 | UINT16 | 13342 | 13343 | Analog Input | 1688 | R
| Crest Factor - Circuit 41 | 41 | 7344 |  | -3 | UINT16 | 13344 | 13345 | Analog Input | 1689 | R
| Crest Factor - Circuit 42 | 42 | 7345 |  | -3 | UINT16 | 13346 | 13347 | Analog Input | 1690 | R
| Crest Factor - Circuit 43 | 43 | 7346 |  | -3 | UINT16 | 13348 | 13349 | Analog Input | 1691 | R
| Crest Factor - Circuit 44 | 44 | 7347 |  | -3 | UINT16 | 13350 | 13351 | Analog Input | 1692 | R
| Crest Factor - Circuit 45 | 45 | 7348 |  | -3 | UINT16 | 13352 | 13353 | Analog Input | 1693 | R
| Crest Factor - Circuit 46 | 46 | 7349 |  | -3 | UINT16 | 13354 | 13355 | Analog Input | 1694 | R
| Crest Factor - Circuit 47 | 47 | 7350 |  | -3 | UINT16 | 13356 | 13357 | Analog Input | 1695 | R
| Crest Factor - Circuit 48 | 48 | 7351 |  | -3 | UINT16 | 13358 | 13359 | Analog Input | 1696 | R
| Crest Factor - Circuit 49 | 49 | 7352 |  | -3 | UINT16 | 13360 | 13361 | Analog Input | 1697 | R
| Crest Factor - Circuit 50 | 50 | 7353 |  | -3 | UINT16 | 13362 | 13363 | Analog Input | 1698 | R
| Crest Factor - Circuit 51 | 51 | 7354 |  | -3 | UINT16 | 13364 | 13365 | Analog Input | 1699 | R
| Crest Factor - Circuit 52 | 52 | 7355 |  | -3 | UINT16 | 13366 | 13367 | Analog Input | 1700 | R
| Crest Factor - Circuit 53 | 53 | 7356 |  | -3 | UINT16 | 13368 | 13369 | Analog Input | 1701 | R
| Crest Factor - Circuit 54 | 54 | 7357 |  | -3 | UINT16 | 13370 | 13371 | Analog Input | 1702 | R
| Crest Factor - Circuit 55 | 55 | 7358 |  | -3 | UINT16 | 13372 | 13373 | Analog Input | 1703 | R
| Crest Factor - Circuit 56 | 56 | 7359 |  | -3 | UINT16 | 13374 | 13375 | Analog Input | 1704 | R
| Crest Factor - Circuit 57 | 57 | 7360 |  | -3 | UINT16 | 13376 | 13377 | Analog Input | 1705 | R
| Crest Factor - Circuit 58 | 58 | 7361 |  | -3 | UINT16 | 13378 | 13379 | Analog Input | 1706 | R
| Crest Factor - Circuit 59 | 59 | 7362 |  | -3 | UINT16 | 13380 | 13381 | Analog Input | 1707 | R
| Crest Factor - Circuit 60 | 60 | 7363 |  | -3 | UINT16 | 13382 | 13383 | Analog Input | 1708 | R
| Crest Factor - Circuit 61 | 61 | 7364 |  | -3 | UINT16 | 13384 | 13385 | Analog Input | 1709 | R
| Crest Factor - Circuit 62 | 62 | 7365 |  | -3 | UINT16 | 13386 | 13387 | Analog Input | 1710 | R
| Crest Factor - Circuit 63 | 63 | 7366 |  | -3 | UINT16 | 13388 | 13389 | Analog Input | 1711 | R
| Crest Factor - Circuit 64 | 64 | 7367 |  | -3 | UINT16 | 13390 | 13391 | Analog Input | 1712 | R
| Crest Factor - Circuit 65 | 65 | 7368 |  | -3 | UINT16 | 13392 | 13393 | Analog Input | 1713 | R
| Crest Factor - Circuit 66 | 66 | 7369 |  | -3 | UINT16 | 13394 | 13395 | Analog Input | 1714 | R
| Crest Factor - Circuit 67 | 67 | 7370 |  | -3 | UINT16 | 13396 | 13397 | Analog Input | 1715 | R
| Crest Factor - Circuit 68 | 68 | 7371 |  | -3 | UINT16 | 13398 | 13399 | Analog Input | 1716 | R
| Crest Factor - Circuit 69 | 69 | 7372 |  | -3 | UINT16 | 13400 | 13401 | Analog Input | 1717 | R
| Crest Factor - Circuit 70 | 70 | 7373 |  | -3 | UINT16 | 13402 | 13403 | Analog Input | 1718 | R
| Crest Factor - Circuit 71 | 71 | 7374 |  | -3 | UINT16 | 13404 | 13405 | Analog Input | 1719 | R
| Crest Factor - Circuit 72 | 72 | 7375 |  | -3 | UINT16 | 13406 | 13407 | Analog Input | 1720 | R
| Crest Factor - Circuit 73 | 73 | 7376 |  | -3 | UINT16 | 13408 | 13409 | Analog Input | 1721 | R
| Crest Factor - Circuit 74 | 74 | 7377 |  | -3 | UINT16 | 13410 | 13411 | Analog Input | 1722 | R
| Crest Factor - Circuit 75 | 75 | 7378 |  | -3 | UINT16 | 13412 | 13413 | Analog Input | 1723 | R
| Crest Factor - Circuit 76 | 76 | 7379 |  | -3 | UINT16 | 13414 | 13415 | Analog Input | 1724 | R
| Crest Factor - Circuit 77 | 77 | 7380 |  | -3 | UINT16 | 13416 | 13417 | Analog Input | 1725 | R
| Crest Factor - Circuit 78 | 78 | 7381 |  | -3 | UINT16 | 13418 | 13419 | Analog Input | 1726 | R
| Crest Factor - Circuit 79 | 79 | 7382 |  | -3 | UINT16 | 13420 | 13421 | Analog Input | 1727 | R
| Crest Factor - Circuit 80 | 80 | 7383 |  | -3 | UINT16 | 13422 | 13423 | Analog Input | 1728 | R
| Crest Factor - Circuit 81 | 81 | 7384 |  | -3 | UINT16 | 13424 | 13425 | Analog Input | 1729 | R
| Crest Factor - Circuit 82 | 82 | 7385 |  | -3 | UINT16 | 13426 | 13427 | Analog Input | 1730 | R
| Crest Factor - Circuit 83 | 83 | 7386 |  | -3 | UINT16 | 13428 | 13429 | Analog Input | 1731 | R
| Crest Factor - Circuit 84 | 84 | 7387 |  | -3 | UINT16 | 13430 | 13431 | Analog Input | 1732 | R
| Crest Factor - Circuit 85 | 85 | 7388 |  | -3 | UINT16 | 13432 | 13433 | Analog Input | 1733 | R
| Crest Factor - Circuit 86 | 86 | 7389 |  | -3 | UINT16 | 13434 | 13435 | Analog Input | 1734 | R
| Crest Factor - Circuit 87 | 87 | 7390 |  | -3 | UINT16 | 13436 | 13437 | Analog Input | 1735 | R
| Crest Factor - Circuit 88 | 88 | 7391 |  | -3 | UINT16 | 13438 | 13439 | Analog Input | 1736 | R
| Crest Factor - Circuit 89 | 89 | 7392 |  | -3 | UINT16 | 13440 | 13441 | Analog Input | 1737 | R
| Crest Factor - Circuit 90 | 90 | 7393 |  | -3 | UINT16 | 13442 | 13443 | Analog Input | 1738 | R
| Crest Factor - Circuit 91 | 91 | 7394 |  | -3 | UINT16 | 13444 | 13445 | Analog Input | 1739 | R
| Crest Factor - Circuit 92 | 92 | 7395 |  | -3 | UINT16 | 13446 | 13447 | Analog Input | 1740 | R
| Crest Factor - Circuit 93 | 93 | 7396 |  | -3 | UINT16 | 13448 | 13449 | Analog Input | 1741 | R
| Crest Factor - Circuit 94 | 94 | 7397 |  | -3 | UINT16 | 13450 | 13451 | Analog Input | 1742 | R
| Crest Factor - Circuit 95 | 95 | 7398 |  | -3 | UINT16 | 13452 | 13453 | Analog Input | 1743 | R
| Crest Factor - Circuit 96 | 96 | 7399 |  | -3 | UINT16 | 13454 | 13455 | Analog Input | 1744 | R
| Breaker Utilization |  | 7400 | 7495 | -2 | UINT16 | 13456 | 13647 | Analog Input | 1745 - 1840 | R |  | Percent |  | Circuit Utilization = (Current / Breaker Size) * 100
| Breaker Utilization - Circuit 1 | 1 | 7400 |  | -2 | UINT16 | 13456 | 13457 | Analog Input | 1745 | R |  | Percent
| Breaker Utilization - Circuit 2 | 2 | 7401 |  | -2 | UINT16 | 13458 | 13459 | Analog Input | 1746 | R |  | Percent
| Breaker Utilization - Circuit 3 | 3 | 7402 |  | -2 | UINT16 | 13460 | 13461 | Analog Input | 1747 | R |  | Percent
| Breaker Utilization - Circuit 4 | 4 | 7403 |  | -2 | UINT16 | 13462 | 13463 | Analog Input | 1748 | R |  | Percent
| Breaker Utilization - Circuit 5 | 5 | 7404 |  | -2 | UINT16 | 13464 | 13465 | Analog Input | 1749 | R |  | Percent
| Breaker Utilization - Circuit 6 | 6 | 7405 |  | -2 | UINT16 | 13466 | 13467 | Analog Input | 1750 | R |  | Percent
| Breaker Utilization - Circuit 7 | 7 | 7406 |  | -2 | UINT16 | 13468 | 13469 | Analog Input | 1751 | R |  | Percent
| Breaker Utilization - Circuit 8 | 8 | 7407 |  | -2 | UINT16 | 13470 | 13471 | Analog Input | 1752 | R |  | Percent
| Breaker Utilization - Circuit 9 | 9 | 7408 |  | -2 | UINT16 | 13472 | 13473 | Analog Input | 1753 | R |  | Percent
| Breaker Utilization - Circuit 10 | 10 | 7409 |  | -2 | UINT16 | 13474 | 13475 | Analog Input | 1754 | R |  | Percent
| Breaker Utilization - Circuit 11 | 11 | 7410 |  | -2 | UINT16 | 13476 | 13477 | Analog Input | 1755 | R |  | Percent
| Breaker Utilization - Circuit 12 | 12 | 7411 |  | -2 | UINT16 | 13478 | 13479 | Analog Input | 1756 | R |  | Percent
| Breaker Utilization - Circuit 13 | 13 | 7412 |  | -2 | UINT16 | 13480 | 13481 | Analog Input | 1757 | R |  | Percent
| Breaker Utilization - Circuit 14 | 14 | 7413 |  | -2 | UINT16 | 13482 | 13483 | Analog Input | 1758 | R |  | Percent
| Breaker Utilization - Circuit 15 | 15 | 7414 |  | -2 | UINT16 | 13484 | 13485 | Analog Input | 1759 | R |  | Percent
| Breaker Utilization - Circuit 16 | 16 | 7415 |  | -2 | UINT16 | 13486 | 13487 | Analog Input | 1760 | R |  | Percent
| Breaker Utilization - Circuit 17 | 17 | 7416 |  | -2 | UINT16 | 13488 | 13489 | Analog Input | 1761 | R |  | Percent
| Breaker Utilization - Circuit 18 | 18 | 7417 |  | -2 | UINT16 | 13490 | 13491 | Analog Input | 1762 | R |  | Percent
| Breaker Utilization - Circuit 19 | 19 | 7418 |  | -2 | UINT16 | 13492 | 13493 | Analog Input | 1763 | R |  | Percent
| Breaker Utilization - Circuit 20 | 20 | 7419 |  | -2 | UINT16 | 13494 | 13495 | Analog Input | 1764 | R |  | Percent
| Breaker Utilization - Circuit 21 | 21 | 7420 |  | -2 | UINT16 | 13496 | 13497 | Analog Input | 1765 | R |  | Percent
| Breaker Utilization - Circuit 22 | 22 | 7421 |  | -2 | UINT16 | 13498 | 13499 | Analog Input | 1766 | R |  | Percent
| Breaker Utilization - Circuit 23 | 23 | 7422 |  | -2 | UINT16 | 13500 | 13501 | Analog Input | 1767 | R |  | Percent
| Breaker Utilization - Circuit 24 | 24 | 7423 |  | -2 | UINT16 | 13502 | 13503 | Analog Input | 1768 | R |  | Percent
| Breaker Utilization - Circuit 25 | 25 | 7424 |  | -2 | UINT16 | 13504 | 13505 | Analog Input | 1769 | R |  | Percent
| Breaker Utilization - Circuit 26 | 26 | 7425 |  | -2 | UINT16 | 13506 | 13507 | Analog Input | 1770 | R |  | Percent
| Breaker Utilization - Circuit 27 | 27 | 7426 |  | -2 | UINT16 | 13508 | 13509 | Analog Input | 1771 | R |  | Percent
| Breaker Utilization - Circuit 28 | 28 | 7427 |  | -2 | UINT16 | 13510 | 13511 | Analog Input | 1772 | R |  | Percent
| Breaker Utilization - Circuit 29 | 29 | 7428 |  | -2 | UINT16 | 13512 | 13513 | Analog Input | 1773 | R |  | Percent
| Breaker Utilization - Circuit 30 | 30 | 7429 |  | -2 | UINT16 | 13514 | 13515 | Analog Input | 1774 | R |  | Percent
| Breaker Utilization - Circuit 31 | 31 | 7430 |  | -2 | UINT16 | 13516 | 13517 | Analog Input | 1775 | R |  | Percent
| Breaker Utilization - Circuit 32 | 32 | 7431 |  | -2 | UINT16 | 13518 | 13519 | Analog Input | 1776 | R |  | Percent
| Breaker Utilization - Circuit 33 | 33 | 7432 |  | -2 | UINT16 | 13520 | 13521 | Analog Input | 1777 | R |  | Percent
| Breaker Utilization - Circuit 34 | 34 | 7433 |  | -2 | UINT16 | 13522 | 13523 | Analog Input | 1778 | R |  | Percent
| Breaker Utilization - Circuit 35 | 35 | 7434 |  | -2 | UINT16 | 13524 | 13525 | Analog Input | 1779 | R |  | Percent
| Breaker Utilization - Circuit 36 | 36 | 7435 |  | -2 | UINT16 | 13526 | 13527 | Analog Input | 1780 | R |  | Percent
| Breaker Utilization - Circuit 37 | 37 | 7436 |  | -2 | UINT16 | 13528 | 13529 | Analog Input | 1781 | R |  | Percent
| Breaker Utilization - Circuit 38 | 38 | 7437 |  | -2 | UINT16 | 13530 | 13531 | Analog Input | 1782 | R |  | Percent
| Breaker Utilization - Circuit 39 | 39 | 7438 |  | -2 | UINT16 | 13532 | 13533 | Analog Input | 1783 | R |  | Percent
| Breaker Utilization - Circuit 40 | 40 | 7439 |  | -2 | UINT16 | 13534 | 13535 | Analog Input | 1784 | R |  | Percent
| Breaker Utilization - Circuit 41 | 41 | 7440 |  | -2 | UINT16 | 13536 | 13537 | Analog Input | 1785 | R |  | Percent
| Breaker Utilization - Circuit 42 | 42 | 7441 |  | -2 | UINT16 | 13538 | 13539 | Analog Input | 1786 | R |  | Percent
| Breaker Utilization - Circuit 43 | 43 | 7442 |  | -2 | UINT16 | 13540 | 13541 | Analog Input | 1787 | R |  | Percent
| Breaker Utilization - Circuit 44 | 44 | 7443 |  | -2 | UINT16 | 13542 | 13543 | Analog Input | 1788 | R |  | Percent
| Breaker Utilization - Circuit 45 | 45 | 7444 |  | -2 | UINT16 | 13544 | 13545 | Analog Input | 1789 | R |  | Percent
| Breaker Utilization - Circuit 46 | 46 | 7445 |  | -2 | UINT16 | 13546 | 13547 | Analog Input | 1790 | R |  | Percent
| Breaker Utilization - Circuit 47 | 47 | 7446 |  | -2 | UINT16 | 13548 | 13549 | Analog Input | 1791 | R |  | Percent
| Breaker Utilization - Circuit 48 | 48 | 7447 |  | -2 | UINT16 | 13550 | 13551 | Analog Input | 1792 | R |  | Percent
| Breaker Utilization - Circuit 49 | 49 | 7448 |  | -2 | UINT16 | 13552 | 13553 | Analog Input | 1793 | R |  | Percent
| Breaker Utilization - Circuit 50 | 50 | 7449 |  | -2 | UINT16 | 13554 | 13555 | Analog Input | 1794 | R |  | Percent
| Breaker Utilization - Circuit 51 | 51 | 7450 |  | -2 | UINT16 | 13556 | 13557 | Analog Input | 1795 | R |  | Percent
| Breaker Utilization - Circuit 52 | 52 | 7451 |  | -2 | UINT16 | 13558 | 13559 | Analog Input | 1796 | R |  | Percent
| Breaker Utilization - Circuit 53 | 53 | 7452 |  | -2 | UINT16 | 13560 | 13561 | Analog Input | 1797 | R |  | Percent
| Breaker Utilization - Circuit 54 | 54 | 7453 |  | -2 | UINT16 | 13562 | 13563 | Analog Input | 1798 | R |  | Percent
| Breaker Utilization - Circuit 55 | 55 | 7454 |  | -2 | UINT16 | 13564 | 13565 | Analog Input | 1799 | R |  | Percent
| Breaker Utilization - Circuit 56 | 56 | 7455 |  | -2 | UINT16 | 13566 | 13567 | Analog Input | 1800 | R |  | Percent
| Breaker Utilization - Circuit 57 | 57 | 7456 |  | -2 | UINT16 | 13568 | 13569 | Analog Input | 1801 | R |  | Percent
| Breaker Utilization - Circuit 58 | 58 | 7457 |  | -2 | UINT16 | 13570 | 13571 | Analog Input | 1802 | R |  | Percent
| Breaker Utilization - Circuit 59 | 59 | 7458 |  | -2 | UINT16 | 13572 | 13573 | Analog Input | 1803 | R |  | Percent
| Breaker Utilization - Circuit 60 | 60 | 7459 |  | -2 | UINT16 | 13574 | 13575 | Analog Input | 1804 | R |  | Percent
| Breaker Utilization - Circuit 61 | 61 | 7460 |  | -2 | UINT16 | 13576 | 13577 | Analog Input | 1805 | R |  | Percent
| Breaker Utilization - Circuit 62 | 62 | 7461 |  | -2 | UINT16 | 13578 | 13579 | Analog Input | 1806 | R |  | Percent
| Breaker Utilization - Circuit 63 | 63 | 7462 |  | -2 | UINT16 | 13580 | 13581 | Analog Input | 1807 | R |  | Percent
| Breaker Utilization - Circuit 64 | 64 | 7463 |  | -2 | UINT16 | 13582 | 13583 | Analog Input | 1808 | R |  | Percent
| Breaker Utilization - Circuit 65 | 65 | 7464 |  | -2 | UINT16 | 13584 | 13585 | Analog Input | 1809 | R |  | Percent
| Breaker Utilization - Circuit 66 | 66 | 7465 |  | -2 | UINT16 | 13586 | 13587 | Analog Input | 1810 | R |  | Percent
| Breaker Utilization - Circuit 67 | 67 | 7466 |  | -2 | UINT16 | 13588 | 13589 | Analog Input | 1811 | R |  | Percent
| Breaker Utilization - Circuit 68 | 68 | 7467 |  | -2 | UINT16 | 13590 | 13591 | Analog Input | 1812 | R |  | Percent
| Breaker Utilization - Circuit 69 | 69 | 7468 |  | -2 | UINT16 | 13592 | 13593 | Analog Input | 1813 | R |  | Percent
| Breaker Utilization - Circuit 70 | 70 | 7469 |  | -2 | UINT16 | 13594 | 13595 | Analog Input | 1814 | R |  | Percent
| Breaker Utilization - Circuit 71 | 71 | 7470 |  | -2 | UINT16 | 13596 | 13597 | Analog Input | 1815 | R |  | Percent
| Breaker Utilization - Circuit 72 | 72 | 7471 |  | -2 | UINT16 | 13598 | 13599 | Analog Input | 1816 | R |  | Percent
| Breaker Utilization - Circuit 73 | 73 | 7472 |  | -2 | UINT16 | 13600 | 13601 | Analog Input | 1817 | R |  | Percent
| Breaker Utilization - Circuit 74 | 74 | 7473 |  | -2 | UINT16 | 13602 | 13603 | Analog Input | 1818 | R |  | Percent
| Breaker Utilization - Circuit 75 | 75 | 7474 |  | -2 | UINT16 | 13604 | 13605 | Analog Input | 1819 | R |  | Percent
| Breaker Utilization - Circuit 76 | 76 | 7475 |  | -2 | UINT16 | 13606 | 13607 | Analog Input | 1820 | R |  | Percent
| Breaker Utilization - Circuit 77 | 77 | 7476 |  | -2 | UINT16 | 13608 | 13609 | Analog Input | 1821 | R |  | Percent
| Breaker Utilization - Circuit 78 | 78 | 7477 |  | -2 | UINT16 | 13610 | 13611 | Analog Input | 1822 | R |  | Percent
| Breaker Utilization - Circuit 79 | 79 | 7478 |  | -2 | UINT16 | 13612 | 13613 | Analog Input | 1823 | R |  | Percent
| Breaker Utilization - Circuit 80 | 80 | 7479 |  | -2 | UINT16 | 13614 | 13615 | Analog Input | 1824 | R |  | Percent
| Breaker Utilization - Circuit 81 | 81 | 7480 |  | -2 | UINT16 | 13616 | 13617 | Analog Input | 1825 | R |  | Percent
| Breaker Utilization - Circuit 82 | 82 | 7481 |  | -2 | UINT16 | 13618 | 13619 | Analog Input | 1826 | R |  | Percent
| Breaker Utilization - Circuit 83 | 83 | 7482 |  | -2 | UINT16 | 13620 | 13621 | Analog Input | 1827 | R |  | Percent
| Breaker Utilization - Circuit 84 | 84 | 7483 |  | -2 | UINT16 | 13622 | 13623 | Analog Input | 1828 | R |  | Percent
| Breaker Utilization - Circuit 85 | 85 | 7484 |  | -2 | UINT16 | 13624 | 13625 | Analog Input | 1829 | R |  | Percent
| Breaker Utilization - Circuit 86 | 86 | 7485 |  | -2 | UINT16 | 13626 | 13627 | Analog Input | 1830 | R |  | Percent
| Breaker Utilization - Circuit 87 | 87 | 7486 |  | -2 | UINT16 | 13628 | 13629 | Analog Input | 1831 | R |  | Percent
| Breaker Utilization - Circuit 88 | 88 | 7487 |  | -2 | UINT16 | 13630 | 13631 | Analog Input | 1832 | R |  | Percent
| Breaker Utilization - Circuit 89 | 89 | 7488 |  | -2 | UINT16 | 13632 | 13633 | Analog Input | 1833 | R |  | Percent
| Breaker Utilization - Circuit 90 | 90 | 7489 |  | -2 | UINT16 | 13634 | 13635 | Analog Input | 1834 | R |  | Percent
| Breaker Utilization - Circuit 91 | 91 | 7490 |  | -2 | UINT16 | 13636 | 13637 | Analog Input | 1835 | R |  | Percent
| Breaker Utilization - Circuit 92 | 92 | 7491 |  | -2 | UINT16 | 13638 | 13639 | Analog Input | 1836 | R |  | Percent
| Breaker Utilization - Circuit 93 | 93 | 7492 |  | -2 | UINT16 | 13640 | 13641 | Analog Input | 1837 | R |  | Percent
| Breaker Utilization - Circuit 94 | 94 | 7493 |  | -2 | UINT16 | 13642 | 13643 | Analog Input | 1838 | R |  | Percent
| Breaker Utilization - Circuit 95 | 95 | 7494 |  | -2 | UINT16 | 13644 | 13645 | Analog Input | 1839 | R |  | Percent
| Breaker Utilization - Circuit 96 | 96 | 7495 |  | -2 | UINT16 | 13646 | 13647 | Analog Input | 1840 | R |  | Percent
True Meter | True Meter #1 | 1 | 15000 | 15276 |  |  | 15060 | 15485 | [6 empty] | Add 500 for next Circuit
Meter Configuration
| # of Circuits Assigned |  | 15000
| Assigned Circuits |  | 15001 | 15003 | [6 empty] | R | NV |  |  | Read Only Registers (Use Meter Configuration registers to configure)
| Assigned Circuit to True Meter Circuit 1 |  | 15001 | [7 empty] | R | NV
| Assigned Circuit to True Meter Circuit 2 |  | 15002 | [7 empty] | R | NV
| Assigned Circuit to True Meter Circuit 3 |  | 15003 | [7 empty] | R | NV
| CT Size |  | 15004 | 15006 | [6 empty] | R | NV | Amps |  | Read Only Registers (Use Meter Configuration registers to configure)
| CT Size - Assigned Circuit 1 |  | 15004 | [7 empty] | R | NV | Amps
| CT Size - Assigned Circuit 2 |  | 15005 | [7 empty] | R | NV | Amps
| CT Size - Assigned Circuit 3 |  | 15006 | [7 empty] | R | NV | Amps
| Breaker Size |  | 15007 | 15009 | [6 empty] | R | NV | Amps |  | Read Only Registers (Use Meter Configuration registers to configure)
| Breaker Size - Assigned Circuit 1 |  | 15007 | [7 empty] | R | NV | Amps
| Breaker Size - Assigned Circuit 2 |  | 15008 | [7 empty] | R | NV | Amps
| Breaker Size - Assigned Circuit 3 |  | 15009 | [7 empty] | R | NV | Amps
| Voltage Phase |  | 15010 | 15012 | [6 empty] | R | NV |  |  | Read Only Registers (Use Meter Configuration registers to configure)
| Voltage Phase - Assigned Circuit 1 |  | 15010 | [7 empty] | R | NV
| Voltage Phase - Assigned Circuit 2 |  | 15011 | [7 empty] | R | NV
| Voltage Phase - Assigned Circuit 3 |  | 15012 | [7 empty] | R | NV
| Reset/Command All Phases |  | 15013
| Reset/Command |  | 15014 | 15016
| Reset/Command - Assigned Channel 1 |  | 15014
| Reset/Command - Assigned Channel 2 |  | 15015
| Reset/Command - Assigned Channel 3 |  | 15016
| CT Type/Compensation |  | 15017 | 15019
| CT Type/Compensation - Assigned Channel 1 |  | 15017
| CT Type/Compensation - Assigned Channel 2 |  | 15018
| CT Type/Compensation - Assigned Channel 3 |  | 15019
| Meter Name - 40 Characters (20 Register) |  | 15020 | 15039
Voltage
| Frequency |  | 15040 |  |  |  | 15060 | 15061 |  |  | R |  | Hz
| Voltage LN |  | 15041 | 15044 |  |  | 15062 | 15069 |  |  | R |  | Volts
| Voltage LN - Average of Assigned Circuit |  | 15041 |  |  |  | 15062 | 15063 |  |  | R |  | Volts
| Voltage LN - Assigned Circuit 1 |  | 15042 |  |  |  | 15064 | 15065 |  |  | R |  | Volts
| Voltage LN - Assigned Circuit 2 |  | 15043 |  |  |  | 15066 | 15067 |  |  | R |  | Volts
| Voltage LN - Assigned Circuit 3 |  | 15044 |  |  |  | 15068 | 15069 |  |  | R |  | Volts
| Voltage LN THD |  | 15045 | 15048 |  |  | 15070 | 15077 |  |  | R |  | Volts
| Voltage LN THD - Average of Assigned Circuit |  | 15045 |  |  |  | 15070 | 15071 |  |  | R |  | Volts
| Voltage LN THD - Assigned Circuit 1 |  | 15046 |  |  |  | 15072 | 15073 |  |  | R |  | Volts
| Voltage LN THD - Assigned Circuit 2 |  | 15047 |  |  |  | 15074 | 15075 |  |  | R |  | Volts
| Voltage LN THD - Assigned Circuit 3 |  | 15048 |  |  |  | 15076 | 15077 |  |  | R |  | Volts
True Meter #1 Total/Average |  |  | 15100
| Energy Scale |  | 15100
| Power Scale |  | 15101
| Current Scale |  | 15102
| Voltage Scale |  | 15103
| Alarm Status |  | 15104
| kWh |  | 15105 | 15106 |  |  | 15300 | 15301 |  |  | R | NV | kWh
| kVARh |  | 15107 | 15108 |  |  | 15302 | 15303 |  |  | R | NV | kVARh
| kVAh |  | 15109 | 15110 |  |  | 15304 | 15305 |  |  | R | NV | kVAh
| kW |  | 15111 |  |  |  | 15306 | 15307 |  |  | R |  | kW
| kVAR |  | 15112 |  |  |  | 15308 | 15309 |  |  | R |  | kVAR
| kVA |  | 15113 |  |  |  | 15310 | 15311 |  |  | R |  | kVA
| Current |  | 15114 |  |  |  | 15312 | 15313 |  |  | R |  | Amps
| Power Factor Average |  | 15115 |  |  |  | 15314 | 15315 |  |  | R |  |  | 0 - 1.0 | Average Power Factor is not signed
| Neutral Current |  | 15116 |  |  |  | 15316 | 15317 |  |  |  |  | Amps
| Current THD Average |  | 15117 |  |  |  | 15318 | 15319 |  |  | R |  | Percent
| Max Current |  | 15118 |  |  |  | 15320 | 15321 |  |  | R |  | Amps
| Max kW |  | 15119 |  |  |  | 15322 | 15323 |  |  | R |  | kW
| Current Demand |  | 15120 |  |  |  | 15324 | 15325 |  |  | R |  | Amps
| kW Demand |  | 15121 |  |  |  | 15326 | 15327 |  |  | R |  | kW
| Max Current Demand |  | 15122 |  |  |  | 15328 | 15329 |  |  | R |  | Amps
| Max kW Demand |  | 15123 |  |  |  | 15330 | 15331 |  |  | R |  | kW
| KWH Snapshot |  | 15124 | 15125 |  |  | 15332 | 15333 |  |  | R |  | kWh
| Crest Factor |  | 15126 |  |  |  | 15334 | 15335 |  |  | R
True Meter #1 Circuit 1
| Energy Scale |  | 15150
| Power Scale |  | 15151
| Current Scale |  | 15152
| Voltage Scale |  | 15153
| Alarm Status |  | 15154
| kWh |  | 15155 | 15156 |  |  | 15350 | 15351 |  |  | R | NV | kWh
| kVARh |  | 15157 | 15158 |  |  | 15352 | 15353 |  |  | R | NV | kVARh
| kVAh |  | 15159 | 15160 |  |  | 15354 | 15355 |  |  | R | NV | kVAh
| kW |  | 15161 |  |  |  | 15356 | 15357 |  |  | R |  | kW
| kVAR |  | 15162 |  |  |  | 15358 | 15359 |  |  | R |  | kVAR
| kVA |  | 15163 |  |  |  | 15360 | 15361 |  |  | R |  | kVA
| Current |  | 15164 |  |  |  | 15362 | 15363 |  |  | R |  | Amps
| Power Factor |  | 15165 |  |  |  | 15364 | 15365 |  |  | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Current Angle |  | 15166 |  |  |  | 15366 | 15367 |  |  | R |  | Degrees
| Percent THD |  | 15167 |  |  |  | 15368 | 15369 |  |  | R |  | Percent
| Max Current |  | 15168 |  |  |  | 15370 | 15371 |  |  | R |  | Amps
| Max kW |  | 15169 |  |  |  | 15372 | 15373 |  |  | R |  | kW
| Current Demand |  | 15170 |  |  |  | 15374 | 15375 |  |  | R |  | Amps
| kW Demand |  | 15171 |  |  |  | 15376 | 15377 |  |  | R |  | kW
| Max Current Demand |  | 15172 |  |  |  | 15378 | 15379 |  |  | R |  | Amps
| Max kW Demand |  | 15173 |  |  |  | 15380 | 15381 |  |  | R |  | kW
| KWH Snapshot |  | 15174 | 15175 |  |  | 15382 | 15383 |  |  | R |  | kWh
| Crest Factor |  | 15176 |  |  |  | 15384 | 15385 |  |  | R
| Breaker Utilization |  | 15177 |  |  |  | 15386 | 15387 |  |  | R |  | Percent |  | (Current / Breaker Size) * 100
True Meter #1 Circuit 2
| Energy Scale |  | 15200
| Power Scale |  | 15201
| Current Scale |  | 15202
| Voltage Scale |  | 15203
| Alarm Status |  | 15204
| kWh |  | 15205 | 15206 |  |  | 15400 | 15401 |  |  | R | NV | kWh
| kVARh |  | 15207 | 15208 |  |  | 15402 | 15403 |  |  | R | NV | kVARh
| kVAh |  | 15209 | 15210 |  |  | 15404 | 15405 |  |  | R | NV | kVAh
| kW |  | 15211 |  |  |  | 15406 | 15407 |  |  | R |  | kW
| kVAR |  | 15212 |  |  |  | 15408 | 15409 |  |  | R |  | kVAR
| kVA |  | 15213 |  |  |  | 15410 | 15411 |  |  | R |  | kVA
| Current |  | 15214 |  |  |  | 15412 | 15413 |  |  | R |  | Amps
| Power Factor |  | 15215 |  |  |  | 15414 | 15415 |  |  | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Current Angle |  | 15216 |  |  |  | 15416 | 15417 |  |  | R |  | Degrees
| Percent THD |  | 15217 |  |  |  | 15418 | 15419 |  |  | R |  | Percent
| Max Current |  | 15218 |  |  |  | 15420 | 15421 |  |  | R |  | Amps
| Max kW |  | 15219 |  |  |  | 15422 | 15423 |  |  | R |  | kW
| Current Demand |  | 15220 |  |  |  | 15424 | 15425 |  |  | R |  | Amps
| kW Demand |  | 15221 |  |  |  | 15426 | 15427 |  |  | R |  | kW
| Max Current Demand |  | 15222 |  |  |  | 15428 | 15429 |  |  | R |  | Amps
| Max kW Demand |  | 15223 |  |  |  | 15430 | 15431 |  |  | R |  | kW
| KWH Snapshot |  | 15224 | 15225 |  |  | 15432 | 15433 |  |  | R |  | kWh
| Crest Factor |  | 15226 |  |  |  | 15434 | 15435 |  |  | R
| Breaker Utilization |  | 15227 |  |  |  | 15436 | 15437 |  |  | R |  | Percent |  | (Current / Breaker Size) * 100
True Meter #1 Circuit 3
| Energy Scale |  | 15250
| Power Scale |  | 15251
| Current Scale |  | 15252
| Voltage Scale |  | 15253
| Alarm Status |  | 15254
| kWh |  | 15255 | 15256 |  |  | 15450 | 15451 |  |  | R | NV | kWh
| kVARh |  | 15257 | 15258 |  |  | 15452 | 15453 |  |  | R | NV | kVARh
| kVAh |  | 15259 | 15260 |  |  | 15454 | 15455 |  |  | R | NV | kVAh
| kW |  | 15261 |  |  |  | 15456 | 15457 |  |  | R |  | kW
| kVAR |  | 15262 |  |  |  | 15458 | 15459 |  |  | R |  | kVAR
| kVA |  | 15263 |  |  |  | 15460 | 15461 |  |  | R |  | kVA
| Current |  | 15264 |  |  |  | 15462 | 15463 |  |  | R |  | Amps
| Power Factor |  | 15265 |  |  |  | 15464 | 15465 |  |  | R |  |  | -1.0 - 1.0 | Positive for Leading (Capacitive), Negative for Lagging (Inductive)
| Current Angle |  | 15266 |  |  |  | 15466 | 15467 |  |  | R |  | Degrees
| Percent THD |  | 15267 |  |  |  | 15468 | 15469 |  |  | R |  | Percent
| Max Current |  | 15268 |  |  |  | 15470 | 15471 |  |  | R |  | Amps
| Max kW |  | 15269 |  |  |  | 15472 | 15473 |  |  | R |  | kW
| Current Demand |  | 15270 |  |  |  | 15474 | 15475 |  |  | R |  | Amps
| kW Demand |  | 15271 |  |  |  | 15476 | 15477 |  |  | R |  | kW
| Max Current Demand |  | 15272 |  |  |  | 15478 | 15479 |  |  | R |  | Amps
| Max kW Demand |  | 15273 |  |  |  | 15480 | 15481 |  |  | R |  | kW
| KWH Snapshot |  | 15274 | 15275 |  |  | 15482 | 15483 |  |  | R |  | kWh
| Crest Factor |  | 15276 |  |  |  | 15484 | 15485 |  |  | R
| Breaker Utilization |  | 15277 |  |  |  | 15486 | 15487 |  |  | R |  | Percent |  | (Current / Breaker Size) * 100
| True Meter #2 | 2 | 15500 | 15999 | [10 empty] | True Meter #2 = True Meter #1 + 500
| True Meter #3 | 3 | 16000 | 16499 | [10 empty] | True Meter #3 = True Meter #1 + 1000
| True Meter #4 | 4 | 16500 | 16999 | [10 empty] | True Meter #4 = True Meter #1 + 1500
| True Meter #5 | 5 | 17000 | 17499 | [10 empty] | True Meter #5 = True Meter #1 + 2000
| True Meter #6 | 6 | 17500 | 17999 | [10 empty] | True Meter #6 = True Meter #1 + 2500
| True Meter #7 | 7 | 18000 | 18499 | [10 empty] | True Meter #7 = True Meter #1 + 3000
| True Meter #8 | 8 | 18500 | 18999 | [10 empty] | True Meter #8 = True Meter #1 + 3500
| True Meter #9 | 9 | 19000 | 19499 | [10 empty] | True Meter #9 = True Meter #1 + 4000
| True Meter #10 | 10 | 19500 | 19999 | [10 empty] | True Meter #10 = True Meter #1 + 4500
| True Meter #11 | 11 | 20000 | 20499 | [10 empty] | True Meter #11 = True Meter #1 + 5000
| True Meter #12 | 12 | 20500 | 20999 | [10 empty] | True Meter #12 = True Meter #1 + 5500
| True Meter #13 | 13 | 21000 | 21499 | [10 empty] | True Meter #13 = True Meter #1 + 6000
| True Meter #14 | 14 | 21500 | 21999 | [10 empty] | True Meter #14 = True Meter #1 + 6500
| True Meter #15 | 15 | 22000 | 22499 | [10 empty] | True Meter #15 = True Meter #1 + 7000
| True Meter #16 | 16 | 22500 | 22999 | [10 empty] | True Meter #16 = True Meter #1 + 7500
| True Meter #17 | 17 | 23000 | 23499 | [10 empty] | True Meter #17 = True Meter #1 + 8000
| True Meter #18 | 18 | 23500 | 23999 | [10 empty] | True Meter #18 = True Meter #1 + 8500
| True Meter #19 | 19 | 24000 | 24499 | [10 empty] | True Meter #19 = True Meter #1 + 9000
| True Meter #20 | 20 | 24500 | 24999 | [10 empty] | True Meter #20 = True Meter #1 + 9500
| True Meter #21 | 21 | 25000 | 25499 | [10 empty] | True Meter #21 = True Meter #1 + 10000
| True Meter #22 | 22 | 25500 | 25999 | [10 empty] | True Meter #22 = True Meter #1 + 10500
| True Meter #23 | 23 | 26000 | 26499 | [10 empty] | True Meter #23 = True Meter #1 + 11000
| True Meter #24 | 24 | 26500 | 26999 | [10 empty] | True Meter #24 = True Meter #1 + 11500
| True Meter #25 | 25 | 27000 | 27499 | [10 empty] | True Meter #25 = True Meter #1 + 12000
| True Meter #26 | 26 | 27500 | 27999 | [10 empty] | True Meter #26 = True Meter #1 + 12500
| True Meter #27 | 27 | 28000 | 28499 | [10 empty] | True Meter #27 = True Meter #1 + 13000
| True Meter #28 | 28 | 28500 | 28999 | [10 empty] | True Meter #28 = True Meter #1 + 13500
| True Meter #29 | 29 | 29000 | 29499 | [10 empty] | True Meter #29 = True Meter #1 + 14000
| True Meter #30 | 30 | 29500 | 29999 | [10 empty] | True Meter #30 = True Meter #1 + 14500
| True Meter #31 | 31 | 30000 | 30499 | [10 empty] | True Meter #31 = True Meter #1 + 15000
| True Meter #32 | 32 | 30500 | 30999 | [10 empty] | True Meter #32 = True Meter #1 + 15500
| True Meter #33 | 33 | 31000 | 31499 | [10 empty] | True Meter #33 = True Meter #1 + 16000
| True Meter #34 | 34 | 31500 | 31999 | [10 empty] | True Meter #34 = True Meter #1 + 16500
| True Meter #35 | 35 | 32000 | 32499 | [10 empty] | True Meter #35 = True Meter #1 + 17000
| True Meter #36 | 36 | 32500 | 32999 | [10 empty] | True Meter #36 = True Meter #1 + 17500
| True Meter #37 | 37 | 33000 | 33499 | [10 empty] | True Meter #37 = True Meter #1 + 18000
| True Meter #38 | 38 | 33500 | 33999 | [10 empty] | True Meter #38 = True Meter #1 + 18500
| True Meter #39 | 39 | 34000 | 34499 | [10 empty] | True Meter #39 = True Meter #1 + 19000
| True Meter #40 | 40 | 34500 | 34999 | [10 empty] | True Meter #40 = True Meter #1 + 19500
| True Meter #41 | 41 | 35000 | 35499 | [10 empty] | True Meter #41 = True Meter #1 + 20000
| True Meter #42 | 42 | 35500 | 35999 | [10 empty] | True Meter #42 = True Meter #1 + 20500
| True Meter #43 | 43 | 36000 | 36499 | [10 empty] | True Meter #43 = True Meter #1 + 21000
| True Meter #44 | 44 | 36500 | 36999 | [10 empty] | True Meter #44 = True Meter #1 + 21500
| True Meter #45 | 45 | 37000 | 37499 | [10 empty] | True Meter #45 = True Meter #1 + 22000
| True Meter #46 | 46 | 37500 | 37999 | [10 empty] | True Meter #46 = True Meter #1 + 22500
| True Meter #47 | 47 | 38000 | 38499 | [10 empty] | True Meter #47 = True Meter #1 + 23000
| True Meter #48 | 48 | 38500 | 38999 | [10 empty] | True Meter #48 = True Meter #1 + 23500
| True Meter #49 | 49 | 39000 | 39499 | [10 empty] | True Meter #49 = True Meter #1 + 24000
| True Meter #50 | 50 | 39500 | 39999 | [10 empty] | True Meter #50 = True Meter #1 + 24500
| True Meter #51 | 51 | 40000 | 40499 | [10 empty] | True Meter #51 = True Meter #1 + 25000
| True Meter #52 | 52 | 40500 | 40999 | [10 empty] | True Meter #52 = True Meter #1 + 25500
| True Meter #53 | 53 | 41000 | 41499 | [10 empty] | True Meter #53 = True Meter #1 + 26000
| True Meter #54 | 54 | 41500 | 41999 | [10 empty] | True Meter #54 = True Meter #1 + 26500
| True Meter #55 | 55 | 42000 | 42499 | [10 empty] | True Meter #55 = True Meter #1 + 27000
| True Meter #56 | 56 | 42500 | 42999 | [10 empty] | True Meter #56 = True Meter #1 + 27500
| True Meter #57 | 57 | 43000 | 43499 | [10 empty] | True Meter #57 = True Meter #1 + 28000
| True Meter #58 | 58 | 43500 | 43999 | [10 empty] | True Meter #58 = True Meter #1 + 28500
| True Meter #59 | 59 | 44000 | 44499 | [10 empty] | True Meter #59 = True Meter #1 + 29000
| True Meter #60 | 60 | 44500 | 44999 | [10 empty] | True Meter #60 = True Meter #1 + 29500
| True Meter #61 | 61 | 45000 | 45499 | [10 empty] | True Meter #61 = True Meter #1 + 30000
| True Meter #62 | 62 | 45500 | 45999 | [10 empty] | True Meter #62 = True Meter #1 + 30500
| True Meter #63 | 63 | 46000 | 46499 | [10 empty] | True Meter #63 = True Meter #1 + 31000
| True Meter #64 | 64 | 46500 | 46999 | [10 empty] | True Meter #64 = True Meter #1 + 31500
| True Meter #65 | 65 | 47000 | 47499 | [10 empty] | True Meter #65 = True Meter #1 + 32000
| True Meter #66 | 66 | 47500 | 47999 | [10 empty] | True Meter #66 = True Meter #1 + 32500
| True Meter #67 | 67 | 48000 | 48499 | [10 empty] | True Meter #67 = True Meter #1 + 33000
| True Meter #68 | 68 | 48500 | 48999 | [10 empty] | True Meter #68 = True Meter #1 + 33500
| True Meter #69 | 69 | 49000 | 49499 | [10 empty] | True Meter #69 = True Meter #1 + 34000
| True Meter #70 | 70 | 49500 | 49999 | [10 empty] | True Meter #70 = True Meter #1 + 34500
| True Meter #71 | 71 | 50000 | 50499 | [10 empty] | True Meter #71 = True Meter #1 + 35000
| True Meter #72 | 72 | 50500 | 50999 | [10 empty] | True Meter #72 = True Meter #1 + 35500
| True Meter #73 | 73 | 51000 | 51499 | [10 empty] | True Meter #73 = True Meter #1 + 36000
| True Meter #74 | 74 | 51500 | 51999 | [10 empty] | True Meter #74 = True Meter #1 + 36500
| True Meter #75 | 75 | 52000 | 52499 | [10 empty] | True Meter #75 = True Meter #1 + 37000
| True Meter #76 | 76 | 52500 | 52999 | [10 empty] | True Meter #76 = True Meter #1 + 37500
| True Meter #77 | 77 | 53000 | 53499 | [10 empty] | True Meter #77 = True Meter #1 + 38000
| True Meter #78 | 78 | 53500 | 53999 | [10 empty] | True Meter #78 = True Meter #1 + 38500
| True Meter #79 | 79 | 54000 | 54499 | [10 empty] | True Meter #79 = True Meter #1 + 39000
| True Meter #80 | 80 | 54500 | 54999 | [10 empty] | True Meter #80 = True Meter #1 + 39500
| True Meter #81 | 81 | 55000 | 55499 | [10 empty] | True Meter #81 = True Meter #1 + 40000
| True Meter #82 | 82 | 55500 | 55999 | [10 empty] | True Meter #82 = True Meter #1 + 40500
| True Meter #83 | 83 | 56000 | 56499 | [10 empty] | True Meter #83 = True Meter #1 + 41000
| True Meter #84 | 84 | 56500 | 56999 | [10 empty] | True Meter #84 = True Meter #1 + 41500
| True Meter #85 | 85 | 57000 | 57499 | [10 empty] | True Meter #85 = True Meter #1 + 42000
| True Meter #86 | 86 | 57500 | 57999 | [10 empty] | True Meter #86 = True Meter #1 + 42500
| True Meter #87 | 87 | 58000 | 58499 | [10 empty] | True Meter #87 = True Meter #1 + 43000
| True Meter #88 | 88 | 58500 | 58999 | [10 empty] | True Meter #88 = True Meter #1 + 43500
| True Meter #89 | 89 | 59000 | 59499 | [10 empty] | True Meter #89 = True Meter #1 + 44000
| True Meter #90 | 90 | 59500 | 59999 | [10 empty] | True Meter #90 = True Meter #1 + 44500
| True Meter #91 | 91 | 60000 | 60499 | [10 empty] | True Meter #91 = True Meter #1 + 45000
| True Meter #92 | 92 | 60500 | 60999 | [10 empty] | True Meter #92 = True Meter #1 + 45500
| True Meter #93 | 93 | 61000 | 61499 | [10 empty] | True Meter #93 = True Meter #1 + 46000
| True Meter #94 | 94 | 61500 | 61999 | [10 empty] | True Meter #94 = True Meter #1 + 46500
| True Meter #95 | 95 | 62000 | 62499 | [10 empty] | True Meter #95 = True Meter #1 + 47000
| True Meter #96 | 96 | 62500 | 62999 | [10 empty] | True Meter #96 = True Meter #1 + 47500

## Busway-Dynamic Map
|  |  | Modbus Registers | [5 empty] | Bacnet Objects
|  |  | Integer |  |  |  | Float
| Description | # | Start (MSW) | End (LSW) | Scale | Type | MSW | LSW | Object Type | Instance # | R/W | NV | Units | Range | Notes
Smart Port Information
| Smart Port Status |  | 0 | [11 empty] | 0 = Nothing Detected, 1 = Status OK, 2 = Offline, 3 = Invalid Device Detected
| Number of Tap-offs Connected to Smart Port |  | 1
| Total Number of Channels Connected to Smart Port |  | 2
| Tap-off #1 Product ID | 1 | 3 | [11 empty] | 0=Nothing Connected, 15=Busway 6CT, 16=Busway 3CT
| Tap-off #1 Serial Number | 1 | 4 | 5
| Tap-off #1 Revision | 1 | 6
| Tap-off #1 Number of Channels | 1 | 7
| Tap-off #1 Status | 1 | 8 | [11 empty] | 0 = Nothing Detected, 1 = Status OK, 2 = Offline, 3 = Invalid Device Detected
| Tap-off #1 Name (20 Registers) | 1 | 9 | 28
| Tap-off #2 Product ID | 2 | 29 | [11 empty] | 0=Nothing Connected, 15=Busway 6CT, 16=Busway 3CT
| Tap-off #2 Serial Number | 2 | 30 | 31
| Tap-off #2 Revision | 2 | 32
| Tap-off #2 Number of Channels | 2 | 33
| Tap-off #2 Status | 2 | 34 | [11 empty] | 0 = Nothing Detected, 1 = Status OK, 2 = Offline, 3 = Invalid Device Detected
| Tap-off #2 Name (20 Registers) | 2 | 35 | 54
| Tap-off #3 Product ID | 3 | 55 | [11 empty] | 0=Nothing Connected, 15=Busway 6CT, 16=Busway 3CT
| Tap-off #3 Serial Number | 3 | 56 | 57
| Tap-off #3 Revision | 3 | 58
| Tap-off #3 Number of Channels | 3 | 59
| Tap-off #3 Status | 3 | 60 | [11 empty] | 0 = Nothing Detected, 1 = Status OK, 2 = Offline, 3 = Invalid Device Detected
| Tap-off #3 Name (20 Registers) | 3 | 61 | 80
| Tap-off #4 Product ID | 4 | 81 | [11 empty] | 0=Nothing Connected, 15=Busway 6CT, 16=Busway 3CT
| Tap-off #4 Serial Number | 4 | 82 | 83
| Tap-off #4 Revision | 4 | 84
| Tap-off #4 Number of Channels | 4 | 85
| Tap-off #4 Status | 4 | 86 | [11 empty] | 0 = Nothing Detected, 1 = Status OK, 2 = Offline, 3 = Invalid Device Detected
| Tap-off #4 Name (20 Registers) | 4 | 87 | 106
| Tap-off #5 Product ID | 5 | 107 | [11 empty] | 0=Nothing Connected, 15=Busway 6CT, 16=Busway 3CT
| Tap-off #5 Serial Number | 5 | 108 | 109
| Tap-off #5 Revision | 5 | 110
| Tap-off #5 Number of Channels | 5 | 111
| Tap-off #5 Status | 5 | 112 | [11 empty] | 0 = Nothing Detected, 1 = Status OK, 2 = Offline, 3 = Invalid Device Detected
| Tap-off #5 Name (20 Registers) | 5 | 113 | 132
| Tap-off #6 Product ID | 6 | 133 | [11 empty] | 0=Nothing Connected, 15=Busway 6CT, 16=Busway 3CT
| Tap-off #6 Serial Number | 6 | 134 | 135
| Tap-off #6 Revision | 6 | 136
| Tap-off #6 Number of Channels | 6 | 137
| Tap-off #6 Status | 6 | 138 | [11 empty] | 0 = Nothing Detected, 1 = Status OK, 2 = Offline, 3 = Invalid Device Detected
| Tap-off #6 Name (20 Registers) | 6 | 139 | 158
| Tap-off #7 Product ID | 7 | 159 | [11 empty] | 0=Nothing Connected, 15=Busway 6CT, 16=Busway 3CT
| Tap-off #7 Serial Number | 7 | 160 | 161
| Tap-off #7 Revision | 7 | 162
| Tap-off #7 Number of Channels | 7 | 163
| Tap-off #7 Status | 7 | 164 | [11 empty] | 0 = Nothing Detected, 1 = Status OK, 2 = Offline, 3 = Invalid Device Detected
| Tap-off #7 Name (20 Registers) | 7 | 165 | 184
| Tap-off #8 Product ID | 8 | 185 | [11 empty] | 0=Nothing Connected, 15=Busway 6CT, 16=Busway 3CT
| Tap-off #8 Serial Number | 8 | 186 | 187
| Tap-off #8 Revision | 8 | 188
| Tap-off #8 Number of Channels | 8 | 189
| Tap-off #8 Status | 8 | 190 | [11 empty] | 0 = Nothing Detected, 1 = Status OK, 2 = Offline, 3 = Invalid Device Detected
| Tap-off #8 Name (20 Registers) | 8 | 191 | 210

## Change Log
Revision | Date | Changes | Firmware Revision | Notes:
A |  | Initial Release | 1.000 | Changes from previous version are highlighted with light gray shading
B | 2019-07-01 | Added Device Name (Reg 61-76) and changed register count for Brand Name (Reg 29-44) and Model Name (Reg 45-60)
Removed Voltage Presence registers (Reg 1307-1402)
|  | Added Alarm Status summary registers (Reg 1403-1498) |  | Yellow text indicates features which are not yet supported
Added Smart Port/Panel configuration registers (Reg 1800-1997)
Added Percent THD Average (Reg 4810/4918-4919) Moved L1, L2, L3 THD and L1, L2, L3 Angle (Reg 4810-4816/4918-4931)
Added Dynamic Smart Port Map (Reg 3000-3999)
Added Smart Port to Circuit Configuration (Reg 776-871)
Added CT Compensation Enabled (Reg 149)
C | 2019-07-22 | IP Address, Netmask and Default Gateway are Writable (Reg 126-131)
NTP, DNS and SMTP are not Writable (Reg 132-139)
RS485 Baud rate can be set using the pointmap (Reg 140-141)
Added Device Reboot to Reset/Commnad (Reg 192)
D | 2019-08-22 | Began Adding support for BACnet | 1.037
Added Units Column
Enabled Uptime (Reg 7-8)
Enabled Crest Factor Registers
Enabled CT Size, Breaker Size, Voltage Phase in True Meter (Read Only)
Added Circuit Utilzation to Single Phase pointmap (replaced temperature)
Added Utilization to True Meter Pointmap
E | 2019-10-08 | Added Smart Port Status Registers (Reg 1930-1933) | 1.039
Added Description to Alarm Status Register
F | 2019-10-24 | Updated Product ID list | 1.040
Added more information to Alarm and Status Registers